# 2022 RCM Limit Advice WEM Report Version 1.1 Public 15 July 2022

Western Power

363 Wellington Street

Perth WA 6000

GPO Box L921 Perth WA 6842

Electricity Networks Corporation

ABN 18 540 492 861

WEMLimitAdvice@westernpower.com.au

westernpower.com.au

ELECTRICITY INDUSTRY ACT 2004

ELECTRICITY INDUSTRY

(WHOLESALE ELECTRICITY MARKET)

REGULATIONS 2004

WHOLESALE ELECTRICITY MARKET RULES

Authorisation

|  | Title | Name | Date |
| --- | --- | --- | --- |
| Approver: | A/Transmission Grid Strategy & Planning Manager | Huuson Nguyen | 11 Nov 2022 |

Version Release History

| Version | Effective Date | Summary of Changes |
| --- | --- | --- |
| 1.0 | 15 Jul 2022 | 2022 RCM Limit Advice – original version |
| 1.1 | 11 Nov 2022 | Some minor changes to thermal ratings |

DISCLAIMER

Western Power provides this Limit Advice and associated information in good faith and in the performance of its functions conferred under rules 4.4B.3 and 4.4B. the Wholesale Electricity Market Rules. Western Power has used reasonable endeavours to ensure that this Limit Advice and information is complete, current and accurate at the time it is provided to AEMO. Western Power is not liable for any acts, errors or omissions, or for any results obtained by any party from the use of this information, generally and in accordance with its statutory immunity under section 126 of the Electricity Industry Act 2004 (WA).”

Contents

Abbreviations	1

1.	Purpose	1

2.	Provided information	1

2.1	Estimated SWIS configuration	1

2.2	Estimated proportion of the peak demand	1

2.3	RCM thermal network limit	2

2.4	Facilities subject to NCS or NCESS	2

# Abbreviations

The following table provides a list of abbreviations and acronyms used throughout this document. Defined terms are identified in this document by capitals.

| Term | Definition |
| --- | --- |
| MRN | Mason Rd North |  |
| NCESS | Non-Co-optimised Essential System Services |  |
| NCS | Network Control Services |  |
| RCM | Reserve Capacity Mechanism |  |
| SWIS | South West Interconnected System |  |
| WEM | Wholesale Electricity Market |  |

# Purpose

This Limit Advice is to provide AEMO with the requested information in accordance with Western Power’s obligation, as a Network Operator, specified in clauses 4.4B.3 and 4.4B.5 of the WEM Rules.

# Provided information

All the requested information are in the following sub sections or referenced attachments.

## Estimated SWIS configuration

The estimated configuration of the SWIS during summer 2025 peak, without the recently approved projects and the proposed connection points of the Facilities notified in AEMO’s Expression of Interest spreadsheet, is available from the SWIS PowerFactory Base Model Version 202110v1, uploaded to the “SWIS Powerfactory Model Upload” directory in AEMO’s portal on 22/11/2021.

The proposed connection points of the notified Facilities for the RCM constraint equation development purposes are provided under the “Substation for proposed connection” column of the “2022 RCM – EOI V0 published” spreadsheet uploaded to the “2022 Capacity Cycle” directory in AEMO’s portal on 23 Nov 2022.

The special protection/control schemes applicable to the RCM constraint equation development, but not limited to, are notified under the “Include in limit & constraint equation” column of the “Existing Special Protection Scheme Register (Ver 6C)” file uploaded to the “SWIS Special Protection Schemes” directory in AEMO’s portal on 8 Jul 2022.

## Estimated proportion of the peak demand

The estimated proportion of the SWIS peak demand during summer 2025 at each Electrical Location is in the “2022 RCM – peak demand and block loads V2 published” file uploaded to the “2022 Capacity Cycle” directory in AEMO’s portal on 23 Nov 2022. It includes a new load with an estimated peak demand > 10MW and with a forecast in service date between summer 2022 and sum 2025, details in the below table. There are no existing loads having a change in demand of more than 10MW between summer 2022 and summer 2025.

Table 2.1:	New load with estimated peak demand > 10MW

| # | Description | New estimated peak demand (MW) | Old estimated peak demand (MW) | New/Existing load | Substation | Forecast in service date |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Block load 24 | 29 | NA | New | MRN | 31 May 2023 |

## RCM thermal network limit

The following information has been included the “2022 RCM -thermal ratings V2 published” file uploaded to the “2022 Capacity Cycle” directory in AEMO’s portal on 23 Nov 2022:

Thermal ratings of all applicable lines and transformers assuming an ambient temperature of 41 degrees Celsius;

Transmission Network assets scheduled to be commissioned or retired. Note that none of them are associated with AEMO’s list of Facilities ceasing operation permanently; and

Proposed changes to the SWIS to facilitate the connection of new Facilities notified by in AEMO’s Expression of Interest spreadsheet.

## Facilities subject to NCS or NCESS

There are no facilities required to be in service during summer 2025 to provide NCS, NCESS or equivalent service.