# Limit Advice #1 Eastern Goldfields Transient Stability Import Limit Covering at least 3 EGF Statcoms in service and MU–NT 330kV line in/out Public 20 September 2022

Western Power

363 Wellington Street

Perth WA 6000

GPO Box L921 Perth WA 6842

Electricity Networks Corporation

ABN 18 540 492 861

WEMLimitAdvice@westernpower.com.au

westernpower.com.au

Authorisation

|  | Title | Name | Date |
| --- | --- | --- | --- |
| Approver: | Grid Vision Manager | Nathan Kirby | 20 September 2022 |

Version Release History

| Version | Effective Date | Summary of Changes |
| --- | --- | --- |
| 1.0 | 20 Sep 2022 | Original version |

DISCLAIMER

Western Power provides this Limit Advice and associated information in good faith and in the performance of its functions conferred under rules 1.33, 2.2C and 2.27A the Wholesale Electricity Market Rules. Western Power has used reasonable endeavours to ensure that this Limit Advice and information is complete, current and accurate at the time it is provided to AEMO. Western Power is not liable for any acts, errors or omissions, or for any results obtained by any party from the use of this information, generally and in accordance with its statutory immunity under section 126 of the Electricity Industry Act 2004 (WA).

Contents

1.	Purpose	1

2.	Scope	1

3.	Limit advice	2

3.1	Limit equation “W-LE1^WKT 220/132kV} EGF”	3

3.2	Network model & Network Reinforcement scheme (NRS) included	5

3.3	SCADA points availability	5

Acronyms and abbreviations

General

| APLD EGF ELPS IMC GT NRS RHS SCE | Accelerating Power Level Detector Eastern Goldfields EGF Load Permissive Scheme Independent Master Controller Gas turbine Network reinforcement scheme Right hand side Southern Cross Energy |
| --- | --- |

Substations and terminals

| BKF BLD CGT MDP MRS MU NT | Black Flag substation Boulder substation Collgar Terminal Merredin power station Merredin solar farm Muja Terminal Northern Terminal |
| --- | --- |
| PCY PKS SCE WKT | Piccadilly substation Parkeston substation Southern Cross Energy West Kalgoorlie Terminal |

Transmission lines

| BLD–PKS–PCY 81 CGT–YLN–WKT X1 MU–NT 91 | Boulder to Parkeston and Piccadilly 132kV line Collgar Terminal to Yilgarn and West Kalgoorlie Terminal 220kV line Muja to Northern Terminal line 330kV line |
| --- | --- |

# Purpose

This document is to provide AEMO with Limit Advice to avoid breaches to the below Technical Rules requirement:

Short term voltage stability (clause 2.2.9)

during MW import into the EGF load area.

This is a new limit advice.

# Scope

This Limit Advice is only valid for:

the system conditions indicated in Table 2.1; and

Table 2.1: Scenarios covered by this Limit Advice

| Equipment | Scenarios covered by this Limit Advice |  |
| --- | --- | --- |
| EGF Statcoms | At least 3 Statcoms in service |  |
| MU–NT 91 | In service | Out of service |

the WKT MW imports shown in Table 2.2.

Table 2.2: MW import to enable limit equation

| Number of EGF statcoms in service | WKT MW import |
| --- | --- |
| 5 | 103MW ≤ and ≤ 210MW |
| 4 | 74MW ≤ and ≤ 210MW |
| 3 | 59MW ≤ and ≤ 210MW |

The limit equation included in this Limit Advice will be disabled when either one of the above conditions is not met.

This Limit Advice includes only the existing generator facilities connected to EGF and East Country load areas as at June 2022, excluding any Non-Scheduled Facilities less than 5MW.

Constraint identification has been performed at a maximum of 210MW WKT import.  For WKT import > 210MW, new constraint identification needs to be carried out to determine whether additional limit equations are needed.

# Limit advice

Table 3.1 shows the limit equation included in this Limit Advice

Table 3.1 – Limit Equation and description of limits

| Equation name | Description of limit |
| --- | --- |
| W-LE1^WKT 220/132kV}EGF | This limit equation is required for EGF for the system conditions indicated in Table 2.1 and Table 2.2 to ensure the 132kV voltage within the EGF load area recovers to at least 0.9pu within 10 seconds after a 3-phase fault on the 132kV winding of the WKT 220/132kV T1 or T2 transformer. |

The limit equation is presented as:

WKT MW Import1 ≤ constant + A1.X1  + A2.X2 + A3.X3 + … + An.Xn

Where:

An is the coefficient and Xn is the variable.

## Limit equation “W-LE1^WKT 220/132kV} EGF”

- Table 3.2 presents the RHS variables and coefficients.

Table 3.2 – RHS variables and coefficients of limit equation “W-LE1^WKT 220/132kV} EGF”

| Variable | Coefficient |
| --- | --- |
| Constant | 177.77 |
| pnCGW | 0.0988 |
| qnCGW | 0.0452 |
| nCGW | 0.3680 |
| p-expSCE | -0.4015 |
| p-expPKS | -0.5806 |
| q-expPKS | 0.89889 |
| nPKS | 6.3569 |
| pnMDP | 0.1315 |
| nMDP | 1.6038 |
| pnMRS | 0.1787 |
| nMRS | 0.1072 |
| pELPS | 0.2295 |
| nWKTStatcom | 5.6558 |
| nBLDStatcom | 3.7716 |
| nPCYStatcom | 3.9923 |
| qUnavailEGFCap | -0.5919 |
| vMU220 | 276.27 |
| vWKT220 | -346.14 |
| Limit margin | -12.186 |

- Where:

| Variable | Description |
| --- | --- |
| pnCGW | The total MW sent out from Collgar wind farm |
| qnCGW | The total Mvar sent out from Collgar wind farm |
| nCGW | The total number of Collgar Statcoms online [=Absolute value of PI data (CGW WF1 STATCOM ONLINE + CGW WF2 STATCOM ONLINE)] |
| p-expSCE | The MW sent out from Southern Cross Energy (SCE) at BLD 132kV with a positive quantity being for the MW flow from WMS to BLD |
| p-expPKS | The MW sent out from Parkeston at PKS 132 kV with a positive quantity being for the MW flow from PKS to the PKS-BLD/PCY tee |
| q-expPKS | The Mvar sent out from Parkeston at PKS 132 kV with a positive quantity being for the Mvar flow from PKS to the PKS-BLD/PCY tee |
| nPKS | The total number of Parkeston generator units in service |
| pnMDP | The MW sent out from MDP |
| nMDP | The total number of MDP generator units online |
| pnMRS | The MW sent out from MRS |
| nMRS | The total number of MRS inverter units online |
| pELPS | The total MW of ELPS loads to be disconnected by APLD |
| nWKTStatcom | Status of WKT Statcoms in service (0=off, 1=in) |
| nBLDStatcom | - The total number of BLD Statcoms in service |
| nPCYStatcom | The total number of PCY Statcoms in service |
| qUnavailEGFCap | The total Mvar rating of any of the following EGF capacitor banks that are switched out and unavailable to be controlled by the IMC: BLDCAP62 BLDCAP63 BLDCAP64 BLDCAP65A (sharing the same CB with BLDCAP65B) BLDCAP65B PCYCAP31 PCYCAP33 PCYCAP35 PCYCAP36 BKFCAP61 BKFCAP62 BKFCAP63 WKT0T1_1 WKT0T1_2 WKT0T2_1 WKT0T2_2 WKTCAP63 |
| vMU220 | The actual MU 220kV bus voltage in pu |
| vWKT220 | The actual WKT 220kV bus voltage in pu |

## Network model & Network Reinforcement scheme (NRS) included

The SWIS PowerFactory “EGF LE – POST CAG82.pfd” file uploaded to AEMO’s portal was used to derive this limit equation.

The following NRS and control schemes were included:

- APLD protection (@ Stage 3 setting and operating time= 155 ms for disconnecting both SCE and PKS. When there are no PKS units in service, APLD will not disconnect PKS but some Parkeston loads will be shed by under voltage load shedding scheme. APLD also disconnects all ELPS loads within 390ms from the relay pickup point).

- 220 kV inter-trip: fault on any 220 kV line sections between Muja and MRT will disconnect MRS, MDP and all 220 kV line sections between the faulted section and CGT.

- Muja 220kV voltage control scheme to automatically maintain Muja 220kV voltage at the setpoints set out in the below table

| MW export to NGS from MU220kV | MU 220 kV voltage setpoint |
| --- | --- |
| < 90 MW | 1.26 pu |
| >= 90 MW | 1.45 pu |

- EGF Independent Master Controller (IMC). The controller maintains the output of WKT Statcom between -2 and 2 Mvar and the WKT 220 kV bus voltage between 0.98 and 1.05 pu by adjusting the following elements:

WKT 220/132 kV transformers tap position

WKT reactors

WKT shunt capacitors

Remaining EGF shunt capacitors (i.e. at BLD, PCY and BKF)

If WKT Statcom is out of service, IMC will maintain BLD Statcoms between -4 and 4 Mvar instead.

When WKT Statcom Mvar output is outside the limit and no more transformer tap to be moved nor reactive devices to be switched in/out, the IMC will send alarm, but the operation is still acceptable.

## SCADA points availability

No unavailable SCADA points have been used in deriving the above limit equation.

The MW import measured at WKT end of the CGT–YLN–WKT X1 line with a positive quantity being for the MW flow from YLN to WKT.

There is a total of 5 statcoms in EGF.

Protection clearance times for a three-phase fault on the 132kV winding of the WKT 220/132kV T1 or T2 transformer are 0.105 seconds for the 220 kV breaker and 0.130 seconds for the 132 kV breaker.

The coefficients for all the right-hand-side terms were reduced to 95% as specified in Technical Rules clause 2.3.8 (b).