## Authorisation
2024 RCM - Peak demand and block loads
Version # | Date | Summary of change
0 | 2024-06-10 | Latest version
1 | 2024-07-02 | Change demand at W and SF=0MW Add block load # 39B, 41, 42, 43
1.1 | 2024-07-18 | Update % of substation loads
1.2 | 2024-09-06 | update Block Load #40 & adjust % substation demands
Authorisation
| Date | Title | Name
Approver | 2024-09-06 | Principal Planning Engineer | Huuson Nguyen
EDM# | 68246928

## Proposed Electrical Location
Table 1 1. The estimated zone substation load (%) and Block loads (MW) are based on information from the applicable SWIS Base Model for the relevant reserve capacity cycle. 2. Connection points expected to export MW into the grid during the system coincident peak demand are excluded.
Capacity Year (3rd year of a Reserve Capacity Cycle) | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34
Estimated peak demand from WEM ESOO
Table 2 1. The demand at the following Electrical Locations are given as percentages, up to 2 decimal places. 2. Where an Electrical Location has one or more block loads, as specified in Table 3, the demand in Table 2 is the net demand at the Electrical Location, that is, the total load demand at the Electrical Location minus the total load demand of the block loads at the Electrical Location. 3. The estimated proportion of peak demand at an Electrical Connection is the net demand at that location divided by the sum of the demand at all Electrical Locations in the SWIS (=Western Power peak demand forecast for SWIS in summer) 4. Variation in estimated peak demand of the existing electrical connections and block loads is due to distribution load transfer, recent historical data, PV penetration, different load growth rate, etc. | bar: 2024-25
Electrical Location | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34
A - Arkana | 2024-25: 1.084%; 2025-26: 1.122%; 2026-27: 1.146%
ALB - Albany | 2024-25: 0.8206%; 2025-26: 0.7971%; 2026-27: 0.8279%
AMT - Amherst | 2024-25: 1.708%; 2025-26: 1.568%; 2026-27: 1.619%
APM - Australian Paper Mills | 2024-25: 0.5871%; 2025-26: 0.6139%; 2026-27: 0.6398%
BCH - Beechboro | 2024-25: 1.484%; 2025-26: 1.594%; 2026-27: 1.641%
BCT - Balcatta | 2024-25: 0.2959%; 2025-26: 0.2693%; 2026-27: 0.2918%
BEL - Belmont | 2024-25: 0.9478%; 2025-26: 0.838%; 2026-27: 0.8603%
BIB - Bibra Lake | 2024-25: 1.239%; 2025-26: 1.241%; 2026-27: 1.277%
BKF - Black Flag | 2024-25: 0.7998%; 2025-26: 0.8423%; 2026-27: 0.8819%
BLD - Boulder | 2024-25: 0.6264%; 2025-26: 0.4632%; 2026-27: 0.4993%
BNP - Beenup | 2024-25: 0.1479%; 2025-26: 0.14%; 2026-27: 0.1708%
BSN - Busselton | 2024-25: 0.957%; 2025-26: 1.336%; 2026-27: 0.8365%
BTN - Bridgetown | 2024-25: 0.5871%; 2025-26: 0.642%; 2026-27: 0.6852%
BTY - Bentley | 2024-25: 0.846%; 2025-26: 0.8725%; 2026-27: 0.9035%
BUH - Bunbury Harbour | 2024-25: 1.447%; 2025-26: 1.4%; 2026-27: 1.431%
BYF - Byford | 2024-25: 1.78%; 2025-26: 1.915%; 2026-27: 1.993%
CAP - Capel | 2024-25: 0.4739%; 2025-26: 0.4869%; 2026-27: 0.5144%
CAR - Carrabin | 2024-25: 0.006935%; 2025-26: 0.006463%; 2026-27: 0.03458%
CC - Cockburn Cement | 2024-25: 0.7559%; 2025-26: 1.049%; 2026-27: 1.079%
CK - Cook Street | 2024-25: 1.026%; 2025-26: 0.9435%; 2026-27: 0.4971%
CKN - Clarkson | 2024-25: 1.579%; 2025-26: 1.579%; 2026-27: 1.643%
CL - Clarence St | 2024-25: 0.6704%; 2025-26: 0.5967%; 2026-27: 0.6268%
CO - Collie | 2024-25: 0.289%; 2025-26: 0.3124%; 2026-27: 0.3415%
COL - Collier | 2024-25: 0.8992%; 2025-26: 0.9392%; 2026-27: 0.9684%
CPN - Chapman | 2024-25: 0.2728%; 2025-26: 0.2779%; 2026-27: 0.3069%
CTE - Cottesloe 132kV | 2024-25: 1.075%; 2025-26: 0.9672%; 2026-27: 0.9921%
CUN - Cunderdin | 2024-25: 0.1364%; 2025-26: 0.1228%; 2026-27: 0.1491%
CVE - Canning Vale | 2024-25: 1.16%; 2025-26: 1.068%; 2026-27: 1.089%
D - Darlington | 2024-25: 0.5016%; 2025-26: 0.4739%; 2026-27: 0.5036%
E - Edmund Street | 2024-25: 0.5178%; 2025-26: 0.4761%; 2026-27: 0.4971%
ENB - Eneabba | 2024-25: 0.1595%; 2025-26: 0.1486%; 2026-27: 0.1772%
FFD - Forrestfield | 2024-25: 0.6912%; 2025-26: 0.5859%; 2026-27: 0.5966%
G - Gosnells | 2024-25: 1.114%; 2025-26: 1.374%; 2026-27: 1.394%
GTN - Geraldton | 2024-25: 0.6519%; 2025-26: 0.6139%; 2026-27: 0.6506%
H - Hadfields | 2024-25: 1.07%; 2025-26: 1.103%; 2026-27: 1.12%
HAY - Hay Street | 2024-25: 1.068%; 2025-26: 1.215%; 2026-27: 0.6312%
HBK - Henley Brook | 2024-25: 1.436%; 2025-26: 1.736%; 2026-27: 1.848%
HZM - Hazelmere | 2024-25: 0.5733%; 2025-26: 0.5407%; 2026-27: 0.5793%
JDP - Joondalup | 2024-25: 1.114%; 2025-26: 1.135%; 2026-27: 1.167%
JTE - Joel Terrace 132kV | 2024-25: 1.258%; 2025-26: 1.183%; 2026-27: 1.21%
K - Kalamunda | 2024-25: 0.6981%; 2025-26: 0.7604%; 2026-27: 0.7846%
KAT - Katanning | 2024-25: 0.2543%; 2025-26: 0.2348%; 2026-27: 0.2615%
KDL - Kewdale | 2024-25: 0.5987%; 2025-26: 0.6118%; 2026-27: 0.6376%
KDN - Kondinin | 2024-25: 0.1641%; 2025-26: 0.1529%; 2026-27: 0.1794%
KEL - Kellerberrin | 2024-25: 0.06472%; 2025-26: 0.06032%; 2026-27: 0.08862%
KOJ - Kojonup | 2024-25: 0.05086%; 2025-26: 0.04524%; 2026-27: 0.07349%
LDE - Landsdale | 2024-25: 1.898%; 2025-26: 1.775%; 2026-27: 1.816%
MA - Manning Street | 2024-25: 0.7212%; 2025-26: 0.7303%; 2026-27: 0.7608%
MBR - Mount Barker | 2024-25: 0.1433%; 2025-26: 0.1422%; 2026-27: 0.1708%
MCE - Medical Centre 132kV | 2024-25: 1.052%; 2025-26: 0.9823%; 2026-27: 1.016%
MDN - Maddington | 2024-25: 0.4762%; 2025-26: 0.5235%; 2026-27: 0.549%
MDY - Munday | 2024-25: 0.497%; 2025-26: 0.4632%; 2026-27: 0.4907%
MED - Medina | 2024-25: 1.357%; 2025-26: 1.398%; 2026-27: 1.459%
MER - Merredin | 2024-25: 0.1896%; 2025-26: 0.1788%; 2026-27: 0.2075%
MH - Mandurah | 2024-25: 1.678%; 2025-26: 1.762%; 2026-27: 1.794%
MIL - Milligan Street | 2024-25: 1.359%; 2025-26: 1.416%; 2026-27: 0.262%
MJ - Midland Junction | 2024-25: 1.119%; 2025-26: 1.209%; 2026-27: 1.239%
MJP - Manjimup | 2024-25: 0.252%; 2025-26: 0.2887%; 2026-27: 0.3177%
MLG - Malaga | 2024-25: 0.8414%; 2025-26: 0.8294%; 2026-27: 0.3048%
MO - Morley | 2024-25: 1.153%; 2025-26: 1.217%; 2026-27: 1.249%
MOR - Moora | 2024-25: 0.2751%; 2025-26: 0.2844%; 2026-27: 0.1038%
MR - Margaret River | 2024-25: 0.2843%; 2025-26: 0.265%; 2026-27: 0.294%
MRR - Marriott Road | 2024-25: 1.345%; 2025-26: 1.445%; 2026-27: 0.006485%
MSR - Mason Road | 2024-25: 0.7651%; 2025-26: 0.6269%; 2026-27: 0.2378%
MSS - Meadow Springs | 2024-25: 1.644%; 2025-26: 1.863%; 2026-27: 1.926%
MUC - Muchea | 2024-25: 0.6218%; 2025-26: 0.5838%; 2026-27: 0.616%
MUL - Mullaloo | 2024-25: 1.119%; 2025-26: 0.9909%; 2026-27: 1.009%
MUR - Murdoch | 2024-25: 0.7605%; 2025-26: 0.7023%; 2026-27: 0.7284%
MYR - Myaree | 2024-25: 0.9894%; 2025-26: 0.9134%; 2026-27: 0.9403%
NB - North Beach | 2024-25: 1.331%; 2025-26: 1.303%; 2026-27: 1.347%
NGN - Narrogin | 2024-25: 0.3074%; 2025-26: 0.3081%; 2026-27: 0.3394%
NOR - Northam | 2024-25: 0.5224%; 2025-26: 0.5924%; 2026-27: 0.629%
NP - North Perth | 2024-25: 1.209%; 2025-26: 1.187%; 2026-27: 1.219%
OC - OConnor | 2024-25: 1.225%; 2025-26: 1.137%; 2026-27: 1.176%
OP - Osborne Park | 2024-25: 0.9663%; 2025-26: 0.8208%; 2026-27: 0.8387%
PBY - Padbury | 2024-25: 1.5%; 2025-26: 1.452%; 2026-27: 1.463%
PCY - Piccadilly St | 2024-25: 0.5756%; 2025-26: 0.5321%; 2026-27: 0.5533%
PIC - Picton | 2024-25: 0.92%; 2025-26: 0.6613%; 2026-27: 0.6809%
PNJ - Pinjarra | 2024-25: 0.4739%; 2025-26: 0.489%; 2026-27: 0.5339%
RAN - Rangeway | 2024-25: 0.5756%; 2025-26: 0.7023%; 2026-27: 0.7479%
RGN22 - Regans 22kV | 2024-25: 0.1318%; 2025-26: 0.1653%; 2026-27: 0.1967%
RGN33 - Regans 33kV | 2024-25: 0.1641%; 2025-26: 0.1739%; 2026-27: 0.2053%
RO - Rockingham | 2024-25: 1.348%; 2025-26: 1.094%; 2026-27: 1.096%
RTN - Riverton | 2024-25: 1.757%; 2025-26: 1.415%; 2026-27: 1.437%
RVE - Rivervale | 2024-25: 1.234%; 2025-26: 1.211%; 2026-27: 1.241%
SF - South Fremantle | bar: 2024-25 to 2026-27
SNR - Southern River | 2024-25: 1.919%; 2025-26: 2.034%; 2026-27: 2.123%
SPK - Shenton Park 132kV | 2024-25: 1.177%; 2025-26: 1.14%; 2026-27: 1.167%
SVY - Sawyers Valley 132kV | 2024-25: 0.5825%; 2025-26: 0.5838%; 2026-27: 0.4323%
SX - Southern Cross | 2024-25: 0.01156%; 2025-26: 0.03016%; 2026-27: 0.06052%
TS - Three Springs | 2024-25: 0.2127%; 2025-26: 0.1939%; 2026-27: 0.2248%
W - Wellington Street | bar: 2024-25 to 2026-27
WAG - Wagin | 2024-25: 0.1017%; 2025-26: 0.1056%; 2026-27: 0.134%
WAI - Waikiki | 2024-25: 1.852%; 2025-26: 1.822%; 2026-27: 1.891%
WD - Wembley Downs | 2024-25: 0.8114%; 2025-26: 0.7497%; 2026-27: 0.7825%
WE - Welshpool | 2024-25: 1.26%; 2025-26: 1.329%; 2026-27: 1.347%
WGA - Wangara | 2024-25: 0.3837%; 2025-26: 0.4007%; 2026-27: 0.4323%
WGP - Wagerup | 2024-25: 0.3976%; 2025-26: 0.3662%; 2026-27: 0.3977%
WKT11 - West Kalgoorlie 11 kV | 2024-25: 0.1503%; 2025-26: 0.1551%; 2026-27: 0.1837%
WKT33 - West Kalgoorlie 33 kV | 2024-25: 0.5109%; 2025-26: 0.5192%; 2026-27: 0.5512%
WLN - Willetton | 2024-25: 0.4531%; 2025-26: 0.6333%; 2026-27: 0.6679%
WNO - Wanneroo | 2024-25: 1.378%; 2025-26: 1.476%; 2026-27: 1.522%
WUN - Wundowie | 2024-25: 0.1942%; 2025-26: 0%; 2026-27: 0.2205%
Y - Yokine | 2024-25: 1.468%; 2025-26: 1.28%; 2026-27: 1.329%
YER - Yerbillon | 2024-25: 0.04854%; 2025-26: 0.04308%; 2026-27: 0.07133%
YLN - Yilgarn | 2024-25: 0.2497%; 2025-26: 0.2434%; 2026-27: 0.2767%
YP - Yanchep | 2024-25: 1.142%; 2025-26: 1.219%; 2026-27: 1.282%
Total | 2024-25: 84.77%; 2025-26: 84.61%; 2026-27: 82.64%
Table 3 1. The forecast demand of the following Block Loads are provided in MW, up to 2 decimal places, as measured at their respective Connection Points. | bar: 2024-25
Load | 2024-25: 2024-25 (MW); 2025-26: 2025-26 (MW); 2026-27: 2026-27 (MW)
ABD - Block Load 1 | 2024-25: 3.4; 2025-26: 3.4; 2026-27: 3.92
AFM - Block Load 2 | 2024-25: 4.2; 2025-26: 3.8; 2026-27: 2.3363
APJ - Block Load 3 | 2024-25: 15.2; 2025-26: 20.5; 2026-27: 26.38
BDE - Block Load 4 | 2024-25: 0.6; 2025-26: 0.6; 2026-27: 0.56974
BDP - Block Load 5 | 2024-25: 35.3; 2025-26: 41; 2026-27: 14.06
BEC - Block Load 6 | 2024-25: 9; 2025-26: 9.5; 2026-27: 0
BGM - Block Load 7 | 2024-25: 130.8; 2025-26: 130.1; 2026-27: 130.7371
BHK - Block Load 8 | 2024-25: 13.3; 2025-26: 3.7; 2026-27: 3.5597
BLV - Block Load 9 | 2024-25: 5.4; 2025-26: 5.4; 2026-27: 4.32
BNY - Block Load 10 | 2024-25: 9.5; 2025-26: 9.5; 2026-27: 6.719
BSI - Block Load 11 | 2024-25: 73; 2025-26: 72.4; 2026-27: 72.6186
CAR - Block Load 12 | 2024-25: 8.5; 2025-26: 8.1; 2026-27: 8.1
CBP - Block Load 13 | 2024-25: 9; 2025-26: 5.8; 2026-27: 7.72
CCL - Block Load 14 | 2024-25: 9.2; 2025-26: 10.6; 2026-27: 10.7498
CTB - Block Load 15 | 2024-25: 8.4; 2025-26: 8.2; 2026-27: 7.9
EDG - Block Load 16 | 2024-25: 7.1; 2025-26: 10; 2026-27: 11.48
FFD - Block Load 17 | 2024-25: 5; 2025-26: 5; 2026-27: 4
GGV - Block Load 18 | 2024-25: 17.2; 2025-26: 18.5; 2026-27: 21.1581
GNI - Block Load 19 | 2024-25: 13.2; 2025-26: 8.8; 2026-27: 8.8
KDP - Block Load 20 | 2024-25: 24.4; 2025-26: 21.5; 2026-27: 14.7292
KMC - Block Load 21 | 2024-25: 11.1; 2025-26: 9.4; 2026-27: 10.122
KMM - Block Load 22 | 2024-25: 9.1; 2025-26: 9.4; 2026-27: 7.7198
KRA - Block Load 23 | 2024-25: 78.7; 2025-26: 111; 2026-27: 69.6
MRN - Block Load 24 | 2024-25: 29; 2025-26: 27; 2026-27: 27
NOW - Block Load 25 | 2024-25: 7.5; 2025-26: 6.8; 2026-27: 4.7
NP - Block Load 26 | 2024-25: 8.1; 2025-26: 11.7; 2026-27: 4.7
PLD - Block Load 27 | 2024-25: 4; 2025-26: 6.2; 2026-27: 6.2
SUM - Block Load 28 | 2024-25: 8; 2025-26: 10.1; 2026-27: 8.0584
TLA - Block Load 29 | 2024-25: 16; 2025-26: 2.5; 2026-27: 4.41
TPP - Block Load 30 | 2024-25: 27.8; 2025-26: 21.8; 2026-27: 16.3036
WCL - Block Load 31 | 2024-25: 5.5; 2025-26: 4.3; 2026-27: 4.2027
WM - Block Load 32 | 2024-25: 31.3; 2025-26: 30.9; 2026-27: 15.9938
WSD - Block Load 33 | 2024-25: 5.9; 2025-26: 18.7; 2026-27: 2.1
AKW - Block Load 34 | 2024-25: 0; 2025-26: 2.7; 2026-27: 1.54
WAPL - Block Load 35 | 2024-25: 0; 2025-26: 4.4; 2026-27: 0
WHT - Block Load 36 | 2024-25: 10; 2025-26: 10; 2026-27: 8
SCE - Block Load 37 | 2024-25: 0; 2025-26: 0; 2026-27: 0
BTN - Block Load 38 | 2024-25: 15; 2025-26: 30; 2026-27: 36
MRR(523) - Block Load 39A | 2024-25: combined with other loads; 2026-27: 16.4
MRR(526) - Block Load 39B* | 2026-27: 7.56
MRR - Block Load 40 | 2026-27: 5
PKS - Block Load 41 | 2024-25: 0; 2025-26: 0; 2026-27: 0
YP - Block Load 42* | 2026-27: 27.12
BNL - Block Load 43* | 2026-27: 7.5
Sub Total | 2024-25: 668.7; 2025-26: 713.3; 2026-27: 650.0879
* Recently committed loads.

## DSOC - Potential New Facilities (hidden)
Potential New Facilities - indicative information
Project | DSOC (MW) | Forecast Energisation Date (Target)
Kwinana Waste to Energy Project | 38 | TBA
East Rockingham Resource Recovery Facility (Waste to Energy) | 28.6 | 2022-12-01
Hadouken - Collie Solar Farm | 9.9 | 12-18 months from Financial Close
South Energy Waroona solar | 213 | Q4 2024
South Energy Benger solar | 115 | Q4 2024
Byford Solar Farm (3 x 12MW Facilities + BESS) | 37.5 | Q4 2023
Three Springs Solar | 89 | 2024-12-23
Kwinana Battery Energy Storage System (KBESS) | 100 | 2022-08-01
Walpole Pumped Hydro | 1.5 | 2023-06-01
Sun Brilliance - Solar Farm, Cunderdin | 100 | Q1 2024
Moonies Hill Energy - Flat Rocks Wind Farm | 74 | Q4 2023
Tilt Renewables - Waddi Windfarm | 105 | TBD - Typically ~18 months from Financial Close
Lacour Energy - Kondinin Wind Farm | 120 | Estimated 24 months from Financial Close
Confidential - Not to be published

## SWIS_25-26_Forecast (hidden)
Name | In Folder | Grid | Zone | Active Power | Reactive Power | Load Demand % |  |  | MW | MVAR | Zone | Normal |  | Z/S contains both HV/LV Loads | Zone | (Multiple Items)
|  |  |  | MW | Mvar | 100% |  | Total_Load Demand | 5235.627 | 1060.2295
Auxiliary 1 Load | KWB-Kwinana Battery Storage System | KW - Kwinana Load Area | Customer Substations | 0.585 | 0.28333 |  |  | Generator Auxiliary Load | 90.3735 | 64.8389 | Row Labels | Sum of Active Power | Sum of Load Demand |  | Row Labels | Sum of Active Power | Sum of Load Demand
Auxiliary 2 Load | KWB-Kwinana Battery Storage System | KW - Kwinana Load Area | Customer Substations | 0.585 | 0.28333 |  |  | HV Customer | 685.7 | 157 | A - Arkana | 52.1 | 1.122% | #N/A | ABD - ALCOA Boddington | 3.4 | 0.07324%
Auxiliary 3 Load | KWB-Kwinana Battery Storage System | KW - Kwinana Load Area | Customer Substations | 0.585 | 0.28333 |  |  | Imbedded Generator Site_Load | 529.7 | 252 | ALB - Albany | 37 | 0.7971% | #N/A | AFM - Australian Fused Materials | 3.8 | 0.08186%
BWF_sub_load | BGA - Badgingarra Wind Farm | NC - North Country Load Area | Use On Works | 0 | 0 |  |  | Normal Substation LV | 3927.92 | 585.43 | AMT - Amherst | 72.8 | 1.568% | #N/A | AKW - ALCOA Kwinana | 63.9 | 0.05731%
DYN LOAD - BKF - PQ LOAD | SUB LOAD - BKF - 33.0 kV | LOAD MODELLING |  | 0 | 0 |  |  | Sub_Total Load Demand (excl. Imbedded) | 4703.9935 | 807.2689 | APM - Australian Paper Mills | 28.5 | 0.6139% | #N/A | APJ - ALCOA Pinjarra | 127.2 | 0.4423%
DYN LOAD - BLD - PQ LOAD | IMB LOAD - BLD - 33 kV | LOAD MODELLING |  | 0 | 0 |  |  | Total Required Generation @ BMO (excl. assumed net output from IMB Sites_observed historic data) | 4642.0739 |  | BCH - Beechboro | 74 | 1.594% | #N/A | AWG - Alcoa Wagerup | 82.1 | 0%
DYN LOAD - JAN - PQ LOAD | IMB LOAD - JAN - 66.0 kV | LOAD MODELLING |  | 0 | 0 | [5 empty] | BCT - Balcatta | 12.5 | 0.2693% | #N/A | BDE - Bandee | 0.6 | 0.01293%
DYN LOAD - KNS - STATIC LOAD | KNS - Kambalda Nickle Smelter | LOAD MODELLING |  | 0 | 0 | [5 empty] | BEL - Belmont | 38.9 | 0.838% | #N/A | BDP - Binningup Desalination Plant | 41 | 0.8832%
DYN LOAD - KRA HPGR VSD MOTORS GRP1 | KRA - Karara Mine | LOAD MODELLING |  | 0 | 0 | [5 empty] | BIB - Bibra Lake | 57.6 | 1.241% | #N/A | BEC - Beckenham | 9.5 | 0.2046%
DYN LOAD - KRA HPGR VSD MOTORS GRP2 | KRA - Karara Mine | LOAD MODELLING |  | 0 | 0 | [5 empty] | BKF - Black Flag | 39.1 | 0.8423% | #N/A | Bellevue - BLV | 5.4 | 0.1163%
DYN LOAD - KRA LOAD | KRA - Karara Mine | LOAD MODELLING |  | 0 | 0 | [5 empty] | BLD - Boulder | 21.5 | 0.4632% | #N/A | BGM - Boddington Gold Mine | 130.1 | 2.803%
DYN LOAD - KRA LOAD - AFTER LOAD SHED | KRA - Karara Mine | LOAD MODELLING |  | 0 | 0 | [5 empty] | BNP - Beenup | 6.5 | 0.14% | #N/A | BHK - Broken Hill Kwinana | 3.7 | 0.07971%
DYN LOAD - NKO North Load | WMK - Western Mining Kambalda | LOAD MODELLING |  | 0 | 0 | [5 empty] | BSN - Busselton | 62 | 1.336% | #N/A | BNY - Bounty | 9.5 | 0.2046%
DYN LOAD - WKT33 - PQ LOAD | SUB LOAD - WKT - 33.0 kV | LOAD MODELLING |  | 0 | 0 | [5 empty] | BTN - Bridgetown | 29.8 | 0.642% | #N/A | BPR - B.P. Refinery | 0 | 0%
DYN LOAD - WMK - STATIC LOAD | WMK - Western Mining Kambalda | LOAD MODELLING |  | 0 | 0 | [5 empty] | BTY - Bentley | 40.5 | 0.8725% | #N/A | BSI - Barrack Silicon Smelter | 72.4 | 1.56%
DYN LOAD - WMK - Township | WMK - Western Mining Kambalda | LOAD MODELLING |  | 0 | 0 | [5 empty] | BUH - Bunbury Harbour | 65 | 1.4% | 13 | BTN - Bridgetown | 30 | 0.6463%
DYN LOAD - YLN - PQ LOAD | SUB LOAD - YLN - 33.0 kV | LOAD MODELLING |  | 0 | 0 | [5 empty] | BYF - Byford | 88.9 | 1.915% | 18 | CAR - Carrabin | 8.1 | 0.1745%
GEN LOAD - APJ - G2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 1.4 | 1.05 | [5 empty] | CAP - Capel | 22.6 | 0.4869% | #N/A | CBP - CSBP | 5.8 | 0.1249%
GEN LOAD - APJ - G3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 1.4 | 1.05 | [5 empty] | CAR - Carrabin | 0.3 | 0.006463% | #N/A | CCL - Cockburn Cement Ltd | 10.6 | 0.2283%
GEN LOAD - APJ - G4 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 1.4 | 1.05 | [5 empty] | CC - Cockburn Cement | 48.7 | 1.049% | #N/A | CTB - Cataby | 8.2 | 0.1766%
GEN LOAD - APJ - G5 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 2.45 | 1.837 | [5 empty] | CK - Cook Street | 43.8 | 0.9435% | #N/A | EDG - Edgewater | 10 | 0.2154%
GEN LOAD - APJ - GT1 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 0.84 | 0.63 | [5 empty] | CKN - Clarkson | 73.3 | 1.579% | 32 | FFD - Forrestfield | 5 | 0.1077%
GEN LOAD - APJ - GT2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 3.78 | 2.835 | [5 empty] | CL - Clarence St | 27.7 | 0.5967% | #N/A | FIM - Fimiston | 46.4 | 0.01869%
GEN LOAD - AWG - G1 | AWG - Alcoa Wagerup | MU - Muja Load Area | Use On Works | 1.4 | 1.05 | [5 empty] | CO - Collie | 14.5 | 0.3124% | #N/A | GGV - Golden Grove | 18.5 | 0.3985%
GEN LOAD - AWG - G2 | AWG - Alcoa Wagerup | MU - Muja Load Area | Use On Works | 0.938 | 0.703 | [5 empty] | COL - Collier | 43.6 | 0.9392% | #N/A | GNI - Glen Iris | 8.8 | 0.1896%
GEN LOAD - AWG - G3 | AWG - Alcoa Wagerup | MU - Muja Load Area | Use On Works | 0.938 | 0.703 | [5 empty] | CPN - Chapman | 12.9 | 0.2779% | #N/A | JAN - Jan | 17.2 | 0%
GEN LOAD - AWG - G4 | AWG - Alcoa Wagerup | MU - Muja Load Area | Use On Works | 2.24 | 1.68 | [5 empty] | CTE - Cottesloe 132kV | 44.9 | 0.9672% | #N/A | KDP - Kwinana Desalination Plant | 21.5 | 0.4632%
GEN LOAD - AWG - GT1 | LWT - Landwehr Terminal | MU - Muja Load Area | Use On Works | 4.86 | 3.645 | [5 empty] | CUN - Cunderin | 5.7 | 0.1228% | #N/A | KMC - Kerr McGee Cataby | 9.4 | 0.2025%
GEN LOAD - AWG - GT2 | LWT - Landwehr Terminal | MU - Muja Load Area | Use On Works | 4.86 | 3.645 | [5 empty] | CVE - Canning Vale | 49.6 | 1.068% | #N/A | KMM - Kerr McGee Muchea | 9.4 | 0.2025%
GEN LOAD - BWP - G1 | BWP - Bluewaters Power Station | MU - Muja Load Area | Use On Works | 0 | 0 | [5 empty] | D - Darlington | 22 | 0.4739% | #N/A | KNS - Kambalda Nickle Smelter | 29.9 | 0%
GEN LOAD - BWP - G2 | BWP - Bluewaters Power Station | MU - Muja Load Area | Use On Works | 0 | 0 | [5 empty] | E - Edmund Street | 22.1 | 0.4761% | #N/A | KRA - Karara Mine | 111 | 2.391%
GEN LOAD - CKB - GT1 | CKB - Cockburn Power | KW - Kwinana Load Area | Use On Works | 4.1 | 3 | [5 empty] | ENB - Eneabba | 6.9 | 0.1486% | #N/A | LEF - Lefroy | 5.1 | 0%
GEN LOAD - CKB - SG1 | CKB - Cockburn Power | KW - Kwinana Load Area | Use On Works | 1.6 | 1.2 | [5 empty] | FFD - Forrestfield | 27.2 | 0.5859% | #N/A | MRN - Mason Road North | 27 | 0.5816%
GEN LOAD - CPS - G1 | CPS - Collie Power Station Terminal | MU - Muja Load Area | Use On Works | 22.4 | 16.8 | [5 empty] | G - Gosnells | 63.8 | 1.374% | #N/A | MSH - Marshall RD | 10 | 0.2154%
GEN LOAD - GNN - GT11 | GNN - Newgen Neerabup | NT - Northern Terminal Load Area | Use On Works | 0 | 0 | [5 empty] | GTN - Geraldton | 28.5 | 0.6139% | #N/A | NOW - Nowergup | 6.8 | 0.1465%
GEN LOAD - GNN - GT12 | GNN - Newgen Neerabup | NT - Northern Terminal Load Area | Use On Works | 0 | 0 | [5 empty] | H - Hadfields | 51.2 | 1.103% | 73 | NP - North Perth | 11.7 | 0.252%
GEN LOAD - KMK - GT1 | KMK - Kerr McGee Kwinana | KW - Kwinana Load Area | Use On Works | [7 empty] | HAY - Hay Street | 56.4 | 1.215% | #N/A | PLD - Parklands | 6.2 | 0.1336%
GEN LOAD - KMP - GT1 | KMP - Kemerton Power | BPS - Bunbury Load Area | Use On Works | 1.69 | 1.047 | [5 empty] | HBK - Henley Brook | 80.6 | 1.736% | #N/A | SUM - Summers Street | 10.1 | 0.2176%
GEN LOAD - KMP - GT2 | KMP - Kemerton Power | BPS - Bunbury Load Area | Use On Works | 1.69 | 1.047 | [5 empty] | HZM - Hazelmere | 25.1 | 0.5407% | #N/A | TLA - Tianqi Lithium Australia | 2.5 | 0.05386%
GEN LOAD - KPP - GT1 | KPP - Kwinana Power Partnership | KW - Kwinana Load Area | Use On Works | [7 empty] | JDP - Joondalup | 52.7 | 1.135% | #N/A | TPP - Tiwest Pigment Plant | 21.8 | 0.4696%
GEN LOAD - KPP - GT2 | KPP - Kwinana Power Partnership | KW - Kwinana Load Area | Use On Works | [7 empty] | JTE - Joel Terrace 132kV | 54.9 | 1.183% | #N/A | WAPL - Worsley Alumina Pty Ltd | 146.5 | 0.09471%
GEN LOAD - KPP - SG1 | KPP - Kwinana Power Partnership | KW - Kwinana Load Area | Use On Works | [7 empty] | K - Kalamunda | 35.3 | 0.7604% |  | WCL - Western Colleries Limited | 4.3 | 0.09263%
GEN LOAD - KPS - GT1 | KW - Kwinana | KW - Kwinana Load Area | Use On Works | [7 empty] | KAT - Katanning | 10.9 | 0.2348% |  | WM - Western Mining | 30.9 | 0.6657%
GEN LOAD - MDP - G1 | MDP - Merredin Power Station | EC - East Country Load Area | Use On Works | [7 empty] | KDL - Kewdale | 28.4 | 0.6118% |  | WMK - Western Mining Kambalda | 11.4 | 0%
GEN LOAD - MDP - G2 | MDP - Merredin Power Station | EC - East Country Load Area | Use On Works | [7 empty] | KDN - Kondinin | 7.1 | 0.1529% |  | WSD - Westralian Sands | 18.7 | 0.4028%
GEN LOAD - MGA - GT1 | MGA - Mungarra | NC - North Country Load Area | Use On Works | [7 empty] | KEL - Kellerberrin | 2.8 | 0.06032% |  | Grand Total | 1215.4 | 15.38%
GEN LOAD - MGA - GT3 | MGA - Mungarra | NC - North Country Load Area | Use On Works | [7 empty] | KOJ - Kojonup | 2.1 | 0.04524%
GEN LOAD - MPS - G7 | MPS - Muja Power Station | MU - Muja Load Area | Use On Works | 5 | 3.75 | [5 empty] | LDE - Landsdale | 82.4 | 1.775%
GEN LOAD - MPS - G8 | MPS - Muja Power Station | MU - Muja Load Area | Use On Works | 5 | 3.75 | [5 empty] | MA - Manning Street | 33.9 | 0.7303%
GEN LOAD - NGK - GT3 | KW - Kwinana | KW - Kwinana Load Area | Use On Works | 6.93 | 5.197 | [5 empty] | MBR - Mount Barker | 6.6 | 0.1422%
GEN LOAD - NGK - SG3 | KW - Kwinana | KW - Kwinana Load Area | Use On Works | 6.907 | 5.181 | [5 empty] | MCE - Medical Centre 132kV | 45.6 | 0.9823%
GEN LOAD - PJR - GT1 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MDN - Maddington | 24.3 | 0.5235%
GEN LOAD - PJR - GT10 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | 0.51 | 0.382 | [5 empty] | MDY - Munday | 21.5 | 0.4632%
GEN LOAD - PJR - GT11 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | 0.57 | 0.427 | [5 empty] | MED - Medina | 64.9 | 1.398%
GEN LOAD - PJR - GT2 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MER - Merredin | 8.3 | 0.1788%
GEN LOAD - PJR - GT3 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MH - Mandurah | 81.8 | 1.762%
GEN LOAD - PJR - GT4 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MIL - Milligan Street | 65.72 | 1.416%
GEN LOAD - PJR - GT5 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MJ - Midland Junction | 56.1 | 1.209%
GEN LOAD - PJR - GT7 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MJP - Manjimup | 13.4 | 0.2887%
GEN LOAD - PJR - GT9 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | 0.51 | 0.382 | [5 empty] | MLG - Malaga | 38.5 | 0.8294%
GEN LOAD - PRK - GT1 | PRK - Parkeston | EG - Eastern Goldfields Load Area | Use On Works | 0.2 | 0.15 | [5 empty] | MO - Morley | 56.5 | 1.217%
GEN LOAD - PRK - GT2 | PRK - Parkeston | EG - Eastern Goldfields Load Area | Use On Works | [7 empty] | MOR - Moora | 13.2 | 0.2844%
GEN LOAD - PRK - GT3 | PRK - Parkeston | EG - Eastern Goldfields Load Area | Use On Works | [7 empty] | MR - Margaret River | 12.3 | 0.265%
GEN LOAD - WKT - GT2 | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Use On Works | [7 empty] | MRR - Marriott Road | 67.1 | 1.445%
GEN LOAD - WKT - GT3 | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Use On Works | [7 empty] | MSR - Mason Road | 29.1 | 0.6269%
General Load | BLD - Boulder | EG - Eastern Goldfields Load Area | Other | [7 empty] | MSS - Meadow Springs | 86.5 | 1.863%
General Load | PCY - Piccadilly St | EG - Eastern Goldfields Load Area | Other | [7 empty] | MUC - Muchea | 27.1 | 0.5838%
General Load | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Other | [7 empty] | MUL - Mullaloo | 46 | 0.9909%
General Load(1) | BLD - Boulder | EG - Eastern Goldfields Load Area | Other | [7 empty] | MUR - Murdoch | 32.6 | 0.7023%
General Load(1) | PCY - Piccadilly St | EG - Eastern Goldfields Load Area | Other | [7 empty] | MYR - Myaree | 42.4 | 0.9134%
General Load(1) | LTH - Leath Road_Kwinana Waste Energy | KW - Kwinana Load Area | Use On Works | 4 | 1.3147 | [5 empty] | NB - North Beach | 60.5 | 1.303%
HV CUST - ABD | ABD - ALCOA Boddington | MU - Muja Load Area | HV Customer | 3.4 | 0.2 | 0.07324% |  |  |  |  | NGN - Narrogin | 14.3 | 0.3081%
HV CUST - AFM | AFM - Australian Fused Materials | KW - Kwinana Load Area | HV Customer | 3.8 | 1.7 | 0.08186% |  |  |  |  | NOR - Northam | 27.5 | 0.5924%
HV CUST - BDE | BDE - Bandee | EC - East Country Load Area | HV Customer | 0.6 | 0.3 | 0.01293% |  |  |  |  | NP - North Perth | 55.1 | 1.187%
HV CUST - BEC - PTA | BEC - Beckenham | CT - Cannington Terminal Load Area | HV Customer | 9.5 | 1.8 | 0.2046% |  |  |  |  | OC - OConnor | 52.8 | 1.137%
HV CUST - BGM | BGM - Boddington Gold Mine | MU - Muja Load Area | HV Customer | 130.1 | 26.7 | 2.803% |  |  |  |  | OP - Osborne Park | 38.1 | 0.8208%
HV CUST - BHK | BHK - Broken Hill Kwinana | KW - Kwinana Load Area | HV Customer | 3.7 | 0.5 | 0.07971% |  |  |  |  | PBY - Padbury | 67.4 | 1.452%
HV CUST - BLV - PTA | Bellevue - BLV | GLT - Guildford Terminal Load Area | HV Customer | 5.4 | 1.8 | 0.1163% |  |  |  |  | PCY - Piccadilly St | 24.7 | 0.5321%
HV CUST - BNY | BNY - Bounty | EC - East Country Load Area | HV Customer | 9.5 | 2.8 | 0.2046% |  |  |  |  | PIC - Picton | 30.7 | 0.6613%
HV CUST - BPR - 132.0 kV | BPR - B.P. Refinery | KW - Kwinana Load Area | HV Customer | 0 | 0 | 0% |  |  |  |  | PNJ - Pinjarra | 22.7 | 0.489%
HV CUST - BSI | BSI - Barrack Silicon Smelter | BPS - Bunbury Load Area | HV Customer | 72.4 | 16.1 | 1.56% |  |  |  |  | RAN - Rangeway | 32.6 | 0.7023%
HV CUST - BTN | BTN - Bridgetown | MU - Muja Load Area | HV Customer | 30 | 9.9 | 0.6463% |  |  |  |  | RGN - Regans | 15.8 | 0.3404%
HV CUST - CCL | CCL - Cockburn Cement Ltd | ST - Southern Terminal Load Area | HV Customer | 10.6 | 6.3 | 0.2283% |  |  |  |  | RO - Rockingham | 50.8 | 1.094%
HV CUST - CSBP LOAD SIMPLIFIED | CBP - CSBP | KW - Kwinana Load Area | HV Customer | 5.8 | 3.1 | 0.1249% |  |  |  |  | RTN - Riverton | 65.7 | 1.415%
HV CUST - EDG - PTA | EDG - Edgewater | NT - Northern Terminal Load Area | HV Customer | 10 | 6.6 | 0.2154% |  |  |  |  | RVE - Rivervale | 56.2 | 1.211%
HV CUST - EGM | CAR - Carrabin | EC - East Country Load Area | HV Customer | 8.1 | 3.3 | 0.1745% |  |  |  |  | SF - South Fremantle | 0 | 0%
HV CUST - GGV | GGV - Golden Grove | NC - North Country Load Area | HV Customer | 18.5 | 3.9 | 0.3985% |  |  |  |  | SNR - Southern River | 94.4 | 2.034%
HV CUST - IIuka Cataby Mine - 33.0 kV | CTB - Cataby | NC - North Country Load Area | HV Customer | 8.2 | 0.3 | 0.1766% |  |  |  |  | SPK - Shenton Park 132kV | 52.9 | 1.14%
HV CUST - KBP - 132.0 kV | MRN - Mason Road North | KW - Kwinana Load Area | HV Customer | 27 | 8.9 | 0.5816% |  |  |  |  | SVY - Sawyers Valley 132kV | 27.1 | 0.5838%
HV CUST - KDP | KDP - Kwinana Desalination Plant | KW - Kwinana Load Area | HV Customer | 21.5 | -1.5 | 0.4632% |  |  |  |  | SX - Southern Cross | 1.4 | 0.03016%
HV CUST - KMC | KMC - Kerr McGee Cataby | NC - North Country Load Area | HV Customer | 9.4 | 5.8 | 0.2025% |  |  |  |  | TS - Three Springs | 9 | 0.1939%
HV CUST - KMM | KMM - Kerr McGee Muchea | NT - Northern Terminal Load Area | HV Customer | 9.4 | 5.2 | 0.2025% |  |  |  |  | W - Wellington Street | 0 | 0%
HV CUST - KRA | KRA - Karara Mine | NC - North Country Load Area | HV Customer | 111 | 7 | 2.391% |  |  |  |  | WAG - Wagin | 4.9 | 0.1056%
HV CUST - LOAD - 132kV | BDP - Binningup Desalination Plant | BPS - Bunbury Load Area | HV Customer | 41 | 1.2 | 0.8832% |  |  |  |  | WAI - Waikiki | 84.6 | 1.822%
HV CUST - MSH - PTA | MSH - Marshall RD | NT - Northern Terminal Load Area | HV Customer | 10 | 3.3 | 0.2154% |  |  |  |  | WD - Wembley Downs | 34.8 | 0.7497%
HV CUST - MVE - PTA | FFD - Forrestfield | GLT - Guildford Terminal Load Area | HV Customer | 5 | 0 | 0.1077% |  |  |  |  | WE - Welshpool | 61.7 | 1.329%
HV CUST - NOW - PTA | NOW - Nowergup | NT - Northern Terminal Load Area | HV Customer | 6.8 | 2.4 | 0.1465% |  |  |  |  | WGA - Wangara | 18.6 | 0.4007%
HV CUST - SRD | NP - North Perth | EP - East Perth Load Area | HV Customer | 11.7 | 1.2 | 0.252% |  |  |  |  | WGP - Wagerup | 17 | 0.3662%
HV CUST - SUM - PTA | SUM - Summers Street | EP - East Perth Load Area | HV Customer | 10.1 | 3.9 | 0.2176% |  |  |  |  | WKT - West Kalgoorlie | 31.3 | 0.6743%
HV CUST - TLA - 6.6 kV | TLA - Tianqi Lithium Australia | KW - Kwinana Load Area | HV Customer | 2.5 | 0.1 | 0.05386% |  |  |  |  | WLN - Willetton | 29.4 | 0.6333%
HV CUST - TPP - 132.0 kV | TPP - Tiwest Pigment Plant | KW - Kwinana Load Area | HV Customer | 21.8 | 12.6 | 0.4696% |  |  |  |  | WNO - Wanneroo | 68.5 | 1.476%
HV CUST - WCL | WCL - Western Colleries Limited | MU - Muja Load Area | HV Customer | 4.3 | 1.5 | 0.09263% |  |  |  |  | WUN - Wundowie | 0 | 0%
HV CUST - WM | WM - Western Mining | KW - Kwinana Load Area | HV Customer | 30.9 | 14.5 | 0.6657% |  |  |  |  | Y - Yokine | 59.4 | 1.28%
HV CUST - WSD | WSD - Westralian Sands | BPS - Bunbury Load Area | HV Customer | 18.7 | 5.2 | 0.4028% |  |  |  |  | YER - Yerbillon | 2 | 0.04308%
IMB LOAD - AKW - 22.0 kV | AKW - ALCOA Kwinana | KW - Kwinana Load Area | Imbedded | 63.9 | 27.8 | 0.05731% | 2.6603 |  |  |  | YLN - Yilgarn | 11.3 | 0.2434%
IMB LOAD - APJ - 13.8 kV / 1 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 50.9 | 18.8 | 0.4423% | 20.5298 |  |  |  | YP - Yanchep | 56.6 | 1.219%
IMB LOAD - APJ - 13.8 kV / 2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 35.6 | 13.2 | [5 empty] | Grand Total | 3927.92 | 84.62%
IMB LOAD - APJ - 13.8 kV / 3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 35.6 | 13.2
IMB LOAD - APJ - 33.0 kV | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 5.1 | 1.9 | 0%
IMB LOAD - AWG - 22.0 kV | AWG - Alcoa Wagerup | MU - Muja Load Area | Imbedded | 82.1 | 31.8 | 0% | 0
IMB LOAD - FIM - 33.0 kV | FIM - Fimiston | EG - Eastern Goldfields Load Area | Imbedded | 46.4 | 29.7 | 0.01869% | 0.86744
IMB LOAD - JAN | JAN - Jan | EG - Eastern Goldfields Load Area | Imbedded | 17.2 | 1.4
IMB LOAD - KNS | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | Imbedded | 29.9 | 20.5 | 0% | 0
IMB LOAD - LEF | LEF - Lefroy | EG - Eastern Goldfields Load Area | Imbedded | 5.1 | 0.4
IMB LOAD - WAPL / 1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 24.9 | 15.5 | 0.09471% | 4.3964
IMB LOAD - WAPL / 2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 24.9 | 15.5
IMB LOAD - WAPL / 3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 24.9 | 15.5
IMB LOAD - WAPL / 4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 1.5 | 0.9
IMB LOAD - WAPL / 5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 65.9 | 41.1
IMB LOAD - WAPL / 6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 4.4 | 2.7
IMB LOAD - WMK | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | Imbedded | 11.4 | 2.1
KCGM - MOT4 - VSD | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
KCGM - MOT7 - VSD | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
KCGM - Sag Mill 1 - CCV | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
KCGM - Sag Mill 2 - CCV | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
KCGM - STATIC | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
Lumped Load_BATP | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.16524 | 0.080029
Lumped Load_Common1 | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.68076 | 0.32971
Lumped Load_Common2 | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.68076 | 0.32971
Lumped Load_CSP | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.14094 | 0.06826
Lumped Load_FGT | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.16632 | 0.080552
SUB LOAD - A - 22.0 kV | A - Arkana | NT - Northern Terminal Load Area | Normal | 52.1 | 8.6 | 1.122%
SUB LOAD - ALB - 22.0 kV | ALB - Albany | MU - Muja Load Area | Normal | 37 | 1.9 | 0.7971%
SUB LOAD - AMT - 22.0 kV | AMT - Amherst | SF - South Fremantle Load Area | Normal | 72.8 | 5.7 | 1.568%
SUB LOAD - APM - 22.0 kV | APM - Australian Paper Mills | SF - South Fremantle Load Area | Normal | 28.5 | 8.4 | 0.6139%
SUB LOAD - BCH - 22.0 kV | BCH - Beechboro | NT - Northern Terminal Load Area | Normal | 74 | 2.5 | 1.594%
SUB LOAD - BCT - 22.0 kV | BCT - Balcatta | NT - Northern Terminal Load Area | Normal | 12.5 | 2 | 0.2693%
SUB LOAD - BEL - 22.0 kV | BEL - Belmont | CT - Cannington Terminal Load Area | Normal | 38.9 | 9.6 | 0.838%
SUB LOAD - BIB - 22.0 kV | BIB - Bibra Lake | SF - South Fremantle Load Area | Normal | 57.6 | 4.9 | 1.241%
SUB LOAD - BKF - 33.0 kV | BKF - Black Flag | EG - Eastern Goldfields Load Area | Normal | 39.1 | 11.8 | 0.8423%
SUB LOAD - BLD - 33 kV | BLD - Boulder | EG - Eastern Goldfields Load Area | Normal | 21.5 | 8.4 | 0.4632%
SUB LOAD - BNP - 22.0 kV | BNP - Beenup | MU - Muja Load Area | Normal | 6.5 | 0.9 | 0.14%
SUB LOAD - BSN - 22.0 kV / 2 | BSN - Busselton | BPS - Bunbury Load Area | Normal | 37.2 | 1.2 | 0.8014%
SUB LOAD - BSN - T1 | BSN - Busselton | BPS - Bunbury Load Area | Normal | 12.4 | 0.4 | 0.2671%
SUB LOAD - BSN - T2 | BSN - Busselton | BPS - Bunbury Load Area | Normal | 12.4 | 0.4 | 0.2671%
SUB LOAD - BTN - 22.0 kV | BTN - Bridgetown | MU - Muja Load Area | Normal | 29.8 | 3.3 | 0.642%
SUB LOAD - BTY - 22.0 kV | BTY - Bentley | CT - Cannington Terminal Load Area | Normal | 40.5 | 8.7 | 0.8725%
SUB LOAD - BUH - 22.0 kV | BUH - Bunbury Harbour | BPS - Bunbury Load Area | Normal | 65 | 3.9 | 1.4%
SUB LOAD - BYF - 22.0 kV | BYF - Byford | ST - Southern Terminal Load Area | Normal | 88.9 | 9 | 1.915%
SUB LOAD - CAP - 22.0 kV | CAP - Capel | BPS - Bunbury Load Area | Normal | 22.6 | 5.5 | 0.4869%
SUB LOAD - CAR - 22.0 kV | CAR - Carrabin | EC - East Country Load Area | Normal | 0.3 | 0.1 | 0.006463%
SUB LOAD - CC - 22.0 kV | CC - Cockburn Cement | ST - Southern Terminal Load Area | Normal | 48.7 | 7.8 | 1.049%
SUB LOAD - CK - 11.0 kV / 1 | CK - Cook Street | EP - East Perth Load Area | Normal | 21.9 | 3.8 | 0.4718%
SUB LOAD - CK - 11.0 kV / 2 | CK - Cook Street | EP - East Perth Load Area | Normal | 21.9 | 3.8 | 0.4718%
SUB LOAD - CKN - 22.0 kV | CKN - Clarkson | NT - Northern Terminal Load Area | Normal | 73.3 | 8.8 | 1.579%
SUB LOAD - CL - 11.0 kV | CL - Clarence St | CT - Cannington Terminal Load Area | Normal | 27.7 | 6.3 | 0.5967%
SUB LOAD - CO - 22.0 kV | CO - Collie | MU - Muja Load Area | Normal | 14.5 | 2 | 0.3124%
SUB LOAD - COL - 11.0 kV | COL - Collier | CT - Cannington Terminal Load Area | Normal | 43.6 | 6.7 | 0.9392%
SUB LOAD - CPN - 11.0 kV | CPN - Chapman | NC - North Country Load Area | Normal | 12.9 | 2.6 | 0.2779%
SUB LOAD - CTE - 11.0 kV | CTE - Cottesloe 132kV | WT - Western Terminal Load Area | Normal | 44.9 | 11.8 | 0.9672%
SUB LOAD - CUN - 22.0 kV | CUN - Cunderin | EC - East Country Load Area | Normal | 5.7 | 0.6 | 0.1228%
SUB LOAD - CVE - 22.0 kV | CVE - Canning Vale | ST - Southern Terminal Load Area | Normal | 49.6 | 9.3 | 1.068%
SUB LOAD - D - 22.0 kV | D - Darlington | GLT - Guildford Terminal Load Area | Normal | 22 | 1.4 | 0.4739%
SUB LOAD - E - 11.0 kV | E - Edmund Street | SF - South Fremantle Load Area | Normal | 22.1 | 9.4 | 0.4761%
SUB LOAD - ENB - 33.0 kV | ENB - Eneabba | NC - North Country Load Area | Normal | 6.9 | 5.8 | 0.1486%
SUB LOAD - FFD - 22.0 kV | FFD - Forrestfield | GLT - Guildford Terminal Load Area | Normal | 27.2 | 8.3 | 0.5859%
SUB LOAD - G - 22.0 kV | G - Gosnells | ST - Southern Terminal Load Area | Normal | 63.8 | 8.8 | 1.374%
SUB LOAD - GNI - 132.0 kV / 1 - PTA | GNI - Glen Iris | ST - Southern Terminal Load Area | HV Customer | 4.4 | 0.5 | 0.09479%
SUB LOAD - GNI - 132.0 kV / 2 - PTA | GNI - Glen Iris | ST - Southern Terminal Load Area | HV Customer | 4.4 | 0.5 | 0.09479%
SUB LOAD - GTN - 33.0 kV | GTN - Geraldton | NC - North Country Load Area | Normal | 28.5 | 6.3 | 0.6139%
SUB LOAD - H - 22.0 kV | H - Hadfields | NT - Northern Terminal Load Area | Normal | 51.2 | 7.3 | 1.103%
SUB LOAD - HAY - 11.0 kV / 1 | HAY - Hay Street | EP - East Perth Load Area | Normal | 28.2 | 5.8 | 0.6075%
SUB LOAD - HAY - 11.0 kV / 2 | HAY - Hay Street | EP - East Perth Load Area | Normal | 28.2 | 5.8 | 0.6075%
SUB LOAD - HBK - 22.0 kV | HBK - Henley Brook | NT - Northern Terminal Load Area | Normal | 80.6 | 1.7 | 1.736%
SUB LOAD - HZM - 22.0 kV | HZM - Hazelmere | GLT - Guildford Terminal Load Area | Normal | 25.1 | 5.9 | 0.5407%
SUB LOAD - JDP - 22.0 kV | JDP - Joondalup | NT - Northern Terminal Load Area | Normal | 52.7 | 6.7 | 1.135%
SUB LOAD - JTE - 11.0 kV | JTE - Joel Terrace 132kV | EP - East Perth Load Area | Normal | 54.9 | 17.6 | 1.183%
SUB LOAD - K - 22.0 kV | K - Kalamunda | GLT - Guildford Terminal Load Area | Normal | 35.3 | 2.1 | 0.7604%
SUB LOAD - KAT - 22.0 kV | KAT - Katanning | MU - Muja Load Area | Normal | 10.9 | 3.3 | 0.2348%
SUB LOAD - KDL - 22.0 kV | KDL - Kewdale | CT - Cannington Terminal Load Area | Normal | 28.4 | 10.2 | 0.6118%
SUB LOAD - KDN - 33.0 kV | KDN - Kondinin | EC - East Country Load Area | Normal | 7.1 | 4.3 | 0.1529%
SUB LOAD - KEL - 22.0 kV | KEL - Kellerberrin | EC - East Country Load Area | Normal | 2.8 | 1.1 | 0.06032%
SUB LOAD - KOJ - 22.0 kV | KOJ - Kojonup | MU - Muja Load Area | Normal | 2.1 | 0.1 | 0.04524%
SUB LOAD - LDE - 22.0 kV | LDE - Landsdale | NT - Northern Terminal Load Area | Normal | 82.4 | 8.7 | 1.775%
SUB LOAD - MA - 11.0 kV | MA - Manning Street | NT - Northern Terminal Load Area | Normal | 33.9 | -2.4 | 0.7303%
SUB LOAD - MBR - 22.0 kV | MBR - Mount Barker | MU - Muja Load Area | Normal | 6.6 | -0.9 | 0.1422%
SUB LOAD - MCE | MCE - Medical Centre 132kV | WT - Western Terminal Load Area | Normal | 45.6 | 13.3 | 0.9823%
SUB LOAD - MDN - 22.0 kV | MDN - Maddington | ST - Southern Terminal Load Area | Normal | 24.3 | 5.3 | 0.5235%
SUB LOAD - MDY - 22.0 kV | MDY - Munday | GLT - Guildford Terminal Load Area | Normal | 21.5 | 5 | 0.4632%
SUB LOAD - MED - 22.0 kV | MED - Medina | KW - Kwinana Load Area | Normal | 64.9 | -1.4 | 1.398%
SUB LOAD - MER - 22.0 kV | MER - Merredin | EC - East Country Load Area | Normal | 8.3 | -3e-12 | 0.1788%
SUB LOAD - MH - 22.0 kV | MH - Mandurah | KW - Kwinana Load Area | Normal | 81.8 | 4.5 | 1.762%
SUB LOAD - MIL - 11.0 kV / 1 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 10.9533 | 2.505 | 0.236%
SUB LOAD - MIL - 11.0 kV / 2 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 10.9533 | 2.505 | 0.236%
SUB LOAD - MIL - 11.0 kV / 3 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 10.9533 | 2.505 | 0.236%
SUB LOAD - MIL - 11.0 kV / 4 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 10.9533 | 2.505 | 0.236%
SUB LOAD - MIL - 11.0 kV / 5 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 10.9533 | 2.505 | 0.236%
SUB LOAD - MIL - 11.0 kV / 6 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 10.9533 | 2.505 | 0.236%
SUB LOAD - MJ - 22.0 kV | MJ - Midland Junction | GLT - Guildford Terminal Load Area | Normal | 56.1 | 14 | 1.209%
SUB LOAD - MJP - 22.0 kV | MJP - Manjimup | MU - Muja Load Area | Normal | 13.4 | 1.1 | 0.2887%
SUB LOAD - MLG - 22.0 kV / 1 | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 12.7 | 3.6 | 0.2736%
SUB LOAD - MLG - 22.0 kV / 2 | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 12.7 | 3.6 | 0.2736%
SUB LOAD - MLG - 22.0 kV / 3 | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 13.1 | 3.7 | 0.2822%
SUB LOAD - MO - 11.0 kV | MO - Morley | NT - Northern Terminal Load Area | Normal | 56.5 | 15.6 | 1.217%
SUB LOAD - MOR - T1 | MOR - Moora | NC - North Country Load Area | Normal | 3.6 | 0.4 | 0.07755%
SUB LOAD - MOR - T3 | MOR - Moora | NC - North Country Load Area | Normal | 9.6 | 1 | 0.2068%
SUB LOAD - MR - 22.0 kV | MR - Margaret River | BPS - Bunbury Load Area | Normal | 12.3 | -2.2 | 0.265%
SUB LOAD - MRR - 22.0 kV | MRR - Marriott Road | BPS - Bunbury Load Area | Normal | 67.1 | 18 | 1.445%
SUB LOAD - MSR - 1 | MSR - Mason Road | KW - Kwinana Load Area | Normal | 9.6 | -1.5 | 0.2068%
SUB LOAD - MSR - 2 | MSR - Mason Road | KW - Kwinana Load Area | Normal | 9.9 | -1.5 | 0.2133%
SUB LOAD - MSR - 3 | MSR - Mason Road | KW - Kwinana Load Area | Normal | 9.6 | -1.5 | 0.2068%
SUB LOAD - MSS - 22.0 kV | MSS - Meadow Springs | KW - Kwinana Load Area | Normal | 86.5 | 3.3 | 1.863%
SUB LOAD - MUC - 22.0 kV | MUC - Muchea | NT - Northern Terminal Load Area | Normal | 27.1 | 2.8 | 0.5838%
SUB LOAD - MUL - 22.0 kV | MUL - Mullaloo | NT - Northern Terminal Load Area | Normal | 46 | 10 | 0.9909%
SUB LOAD - MUR - 22.0 kV | MUR - Murdoch | ST - Southern Terminal Load Area | Normal | 32.6 | -0.8 | 0.7023%
SUB LOAD - MYR - 22.0 kV | MYR - Myaree | SF - South Fremantle Load Area | Normal | 42.4 | 10 | 0.9134%
SUB LOAD - NB - 22.0 kV | NB - North Beach | NT - Northern Terminal Load Area | Normal | 60.5 | 4.4 | 1.303%
SUB LOAD - NGN - 22.0 kV | NGN - Narrogin | MU - Muja Load Area | Normal | 14.3 | 1 | 0.3081%
SUB LOAD - NOR - 22.0 kV | NOR - Northam | EC - East Country Load Area | Normal | 27.5 | -1 | 0.5924%
SUB LOAD - NP - 11.0 kV | NP - North Perth | EP - East Perth Load Area | Normal | 55.1 | 11.7 | 1.187%
SUB LOAD - OC - 22.0 kV | OC - OConnor | SF - South Fremantle Load Area | Normal | 52.8 | 10.4 | 1.137%
SUB LOAD - OP - 11.0 kV | OP - Osborne Park | NT - Northern Terminal Load Area | Normal | 38.1 | 11.5 | 0.8208%
SUB LOAD - PBY - 22.0 kV | PBY - Padbury | NT - Northern Terminal Load Area | Normal | 67.4 | 6.8 | 1.452%
SUB LOAD - PCY - 11.0 kV | PCY - Piccadilly St | EG - Eastern Goldfields Load Area | Normal | 24.7 | 5.3 | 0.5321%
SUB LOAD - PIC - 22.0 kV | PIC - Picton | BPS - Bunbury Load Area | Normal | 30.7 | 10.8 | 0.6613%
SUB LOAD - PLD - 22.0 kV - PTA | PLD - Parklands | KW - Kwinana Load Area | HV Customer | 6.2 | -0.6 | 0.1336%
SUB LOAD - PNJ - 22.0 kV | PNJ - Pinjarra | BPS - Bunbury Load Area | Normal | 22.7 | -2.1 | 0.489%
SUB LOAD - RAN - 11.0 kV | RAN - Rangeway | NC - North Country Load Area | Normal | 32.6 | 5.3 | 0.7023%
SUB LOAD - RGN - 22.0 kV | RGN - Regans | NC - North Country Load Area | Normal | 7.7 | 2.1 | 0.1659%
SUB LOAD - RGN - 33.0 kV | RGN - Regans | NC - North Country Load Area | Normal | 8.1 | 2.1 | 0.1745%
SUB LOAD - RO - 22.0 kV | RO - Rockingham | KW - Kwinana Load Area | Normal | 50.8 | 7.8 | 1.094%
SUB LOAD - RTN - 22.0 kV | RTN - Riverton | ST - Southern Terminal Load Area | Normal | 65.7 | 7 | 1.415%
SUB LOAD - RVE - 22.0 kV | RVE - Rivervale | CT - Cannington Terminal Load Area | Normal | 56.2 | 8.6 | 1.211%
SUB LOAD - SF - 22.0kV | SF - South Fremantle | SF - South Fremantle Load Area | Normal | 0 | 0 | 0%
SUB LOAD - SNR - 22.0 kV | SNR - Southern River | ST - Southern Terminal Load Area | Normal | 94.4 | -0.8 | 2.034%
SUB LOAD - SPK / 1.A | SPK - Shenton Park 132kV | WT - Western Terminal Load Area | Normal | 52.9 | 10.4 | 1.14%
SUB LOAD - SVY - 22.0 kV | SVY - Sawyers Valley 132kV | EC - East Country Load Area | Normal | 27.1 | 1.5 | 0.5838%
SUB LOAD - SX - 33.0 kV | SX - Southern Cross | EC - East Country Load Area | Normal | 1.4 | 1.5 | 0.03016%
SUB LOAD - TS - 33.0 kV | TS - Three Springs | NC - North Country Load Area | Normal | 9 | 5.3 | 0.1939%
SUB LOAD - W - 11.0 kV / 1 | W - Wellington Street | EP - East Perth Load Area | Normal | 0 | 0 | 0%
SUB LOAD - W - 11.0 kV / 2 | W - Wellington Street | EP - East Perth Load Area | Normal | 0 | 0 | 0%
SUB LOAD - WAG - 22.0 kV | WAG - Wagin | MU - Muja Load Area | Normal | 4.9 | 0.5 | 0.1056%
SUB LOAD - WAI - 22.0 kV | WAI - Waikiki | KW - Kwinana Load Area | Normal | 84.6 | 5.5 | 1.822%
SUB LOAD - WD - 6.6 kV | WD - Wembley Downs | WT - Western Terminal Load Area | Normal | 34.8 | 10.1 | 0.7497%
SUB LOAD - WE - 22.0 kV | WE - Welshpool | CT - Cannington Terminal Load Area | Normal | 61.7 | 10 | 1.329%
SUB LOAD - WGA - 22.0 kV | WGA - Wangara | NT - Northern Terminal Load Area | Normal | 18.6 | 1.9 | 0.4007%
SUB LOAD - WGP - 22.0 kV | WGP - Wagerup | MU - Muja Load Area | Normal | 17 | 5.5 | 0.3662%
SUB LOAD - WKT - 11 kV | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Normal | 7.2 | 0.1 | 0.1551%
SUB LOAD - WKT - 33.0 kV | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Normal | 24.1 | 10.1 | 0.5192%
SUB LOAD - WLN - 22.0 kV | WLN - Willetton | ST - Southern Terminal Load Area | Normal | 29.4 | 5.6 | 0.6333%
SUB LOAD - WNO - 22.0 kV | WNO - Wanneroo | NT - Northern Terminal Load Area | Normal | 68.5 | 14.4 | 1.476%
SUB LOAD - WUN - 22.0 kV | WUN - Wundowie | EC - East Country Load Area | Normal | 0 | 0 | 0%
SUB LOAD - Y - 11.0 kV | Y - Yokine | NT - Northern Terminal Load Area | Normal | 59.4 | 11 | 1.28%
SUB LOAD - YER - 6.6 kV | YER - Yerbillon | EC - East Country Load Area | Normal | 2 | 1 | 0.04308%
SUB LOAD - YLN - 33.0 kV | YLN - Yilgarn | EC - East Country Load Area | Normal | 11.3 | 2.8 | 0.2434%
SUB LOAD - YP - 22.0 kV | YP - Yanchep | NT - Northern Terminal Load Area | Normal | 56.6 | -2 | 1.219%
Substation Auxiliary Load | KWB-Kwinana Battery Storage System | KW - Kwinana Load Area | Customer Substations | 0.1785 | 0.11062
VSD_Common1 | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.32373 | 0.15679
VSD_Common2 | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.32373 | 0.15679
VSD_CSP | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.27108 | 0.13129
VSD_FGT | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.00792 | 0
Confidential - Not to be published
Confidential - Not to be published

## SWIS_25-26_IMB_GEN (hidden)
Name | In Folder | Grid | Out of Service | Pn | Pmax(act.) | Pmin(act.) | Qmax(act.) | Qmin(act.) | Act.Pow. | React.Pow. | Active Power | Reactive Power | Facility Code | Row Labels | Sum of Active Power
|  |  |  | MW | MW | MW | Mvar | Mvar | MW | Mvar | MW | Mvar |  | ALCOA_KWI | 62.5
GEN KBA GT | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | 0 | 46 | 46 | 10 | 28.1087 | -21.6209 | 46 | 7.1071 |  |  | STHRNCRS_EG | ALCOA_PNJ | 87
Gen_AKW_G1 | AKW - ALCOA Kwinana | KW - Kwinana Load Area | 0 | 65.002 | 68 | 25 | 36.1 | -34.8 | 60 | 0 |  |  | ALCOA_KWI | ALCOA_WGP | 93
Gen_APJ_G2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 19.9999 | 25 | 10 | 15.575 | -11.75 | 19 | 6.5737 |  |  | ALCOA_PNJ | PRK_AG | 94.7885
Gen_APJ_G3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 19.9999 | 25 | 10 | 15.575 | -11.75 | 19 | 0 |  |  | ALCOA_PNJ | STHRNCRS_EG | 70
Gen_APJ_G4 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 19.9999 | 25 | 10 | 15.575 | -11.75 | 19 | 0 |  |  | ALCOA_PNJ | WAPL_WORSLEY | 141.6108
Gen_APJ_G5 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 30 | 36 | 17 | 15 | -14.3 | 30 | 0 |  |  | ALCOA_PNJ | (blank) | 0
Gen_AWG_G1 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 25 | 30 | 12 | 18.75 | -14.3 | 25 | 6.3398 |  |  | ALCOA_WGP | Grand Total | 548.8992
Gen_AWG_G2 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 18 | 21 | 9 | 13.5 | -9.1 | 18 | 8.6958 |  |  | ALCOA_WGP
Gen_AWG_G3 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 18 | 21 | 9 | 13.5 | -9.1 | 18 | 8.6958 |  |  | ALCOA_WGP
Gen_AWG_G4 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 37.7 | 40 | 18 | 27.9 | -21.9 | 37.7 | 9.1241 |  |  | ALCOA_WGP
Gen_KNS_G1 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 1 | 10.72 | 11 | 5 | 9.385 | -5.5 | 9 | 3.5235 |  |  | STHRNCRS_EG
Gen_KNS_G3 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 1 | 11 | 12 | 5 | 8.8625 | -5.5 | 10 | 6 |  |  | STHRNCRS_EG
Gen_KNS_GT2 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 0 | 46 | 46 | 10 | 28.1087 | -21.6209 | 46 | 22.3 |  |  | STHRNCRS_EG
Gen_PRK_GT1 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | 40.0803 | -19.3161 | 32.1442 | 15.6924 |  |  | PRK_AG
Gen_PRK_GT2 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | 33.4279 | -19.517 | 32.1442 | 15.6924 |  |  | PRK_AG
Gen_PRK_GT3 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | 34.3333 | -19.6633 | 30.5 | 15.6924 |  |  | PRK_AG
Gen_WAPL_G1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 1 | 27.5 | 30 | 13 | 25.7699 | -19.3571 | 13 | 7.5703 |  |  | WAPL_WORSLEY
Gen_WAPL_G2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 1 | 27.5 | 30 | 13 | 20.8521 | -14.1614 | 27 | 7.5703 |  |  | WAPL_WORSLEY
Gen_WAPL_G3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 27.5 | 30 | 13 | 21.5041 | -14.8593 | 25.6108 | 7.5703 |  |  | WAPL_WORSLEY
Gen_WAPL_G4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 32 | 35 | 16 | 24 | -7.25 | 32 | 4.5166 |  |  | WAPL_WORSLEY
Gen_WAPL_G5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 57.84 | 61 | 27 | 49.3882 | -38.4321 | 57.84 | 0 |  |  | WAPL_WORSLEY
Gen_WAPL_G6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 57.84 | 61 | 27 | 49.3882 | -38.4321 | 57.84 | 0 |  |  | WAPL_WORSLEY
[10 empty] | Total Generation @ IMB_Generation | 0
Name | In Folder | Grid | Zone | Active Power | Reactive Power | Facility Code |  | Row Labels | Sum of Active Power
|  |  |  | MW | Mvar |  |  | ALCOA_KWI | 63.9
IMB LOAD - AKW - 22.0 kV | AKW - ALCOA Kwinana | KW - Kwinana Load Area | Imbedded | 63.9 | 27.8 | ALCOA_KWI |  | ALCOA_PNJ | 127.2
IMB LOAD - APJ - 13.8 kV / 1 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 50.9 | 18.8 | ALCOA_PNJ |  | ALCOA_WGP | 82.1
IMB LOAD - APJ - 13.8 kV / 2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 35.6 | 13.2 | ALCOA_PNJ |  | PRK_AG | 46.4
IMB LOAD - APJ - 13.8 kV / 3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 35.6 | 13.2 | ALCOA_PNJ |  | STHRNCRS_EG | 63.6
IMB LOAD - APJ - 33.0 kV | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 5.1 | 1.9 | ALCOA_PNJ |  | WAPL_WORSLEY | 146.5
IMB LOAD - AWG - 22.0 kV | AWG - Alcoa Wagerup | MU - Muja Load Area | Imbedded | 82.1 | 31.8 | ALCOA_WGP |  | (blank) | 0
IMB LOAD - FIM - 33.0 kV | FIM - Fimiston | EG - Eastern Goldfields Load Area | Imbedded | 46.4 | 29.7 | PRK_AG |  | Grand Total | 529.7
IMB LOAD - JAN | JAN - Jan | EG - Eastern Goldfields Load Area | Imbedded | 17.2 | 1.4 | STHRNCRS_EG
IMB LOAD - KNS | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | Imbedded | 29.9 | 20.5 | STHRNCRS_EG
IMB LOAD - LEF | LEF - Lefroy | EG - Eastern Goldfields Load Area | Imbedded | 5.1 | 0.4 | STHRNCRS_EG
IMB LOAD - WAPL / 1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 24.9 | 15.5 | WAPL_WORSLEY
IMB LOAD - WAPL / 2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 24.9 | 15.5 | WAPL_WORSLEY
IMB LOAD - WAPL / 3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 24.9 | 15.5 | WAPL_WORSLEY
IMB LOAD - WAPL / 4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 1.5 | 0.9 | WAPL_WORSLEY
IMB LOAD - WAPL / 5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 65.9 | 41.1 | WAPL_WORSLEY
IMB LOAD - WAPL / 6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 4.4 | 2.7 | WAPL_WORSLEY
IMB LOAD - WMK | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | Imbedded | 11.4 | 2.1 | STHRNCRS_EG
|  |  | Total Generation @ IMB_LOAD | 529.7
Facility Code | Total Net Value from IMB_GEN Sites Observed Std.dev_High End_MW @ SYS_MAX (+/-: GEN/LOAD) | MW (as Load) to be considered in RCM
ALCOA_KWI | -2.6603 | -2.6603
ALCOA_PNJ | -20.5298 | -20.5298
ALCOA_WGP | 5.2568 | 0
PRK_AG | -0.86744 | -0.86744
STHRNCRS_EG | 4.3783 | 0
WAPL_WORSLEY | -4.3964 | -4.3964
| Total MW (as Load) to be considered in RCM | -28.4539
Facility Code | Total Net Value from IMB_GEN Sites Observed Std.dev_High End_MW @ SYS_MAX (+/-: GEN/LOAD) | MW (as Load) to be considered in RCM
ALCOA_KWI | -1.4 | -1.4
ALCOA_PNJ | -40.2 | -40.2
ALCOA_WGP | 10.9 | 0
PRK_AG | 48.3885 | 0
STHRNCRS_EG | 6.4 | 0
WAPL_WORSLEY | -4.8892 | -4.8892
| Total MW (as Load) to be considered in RCM | -46.4892
Confidential - Not to be published

## SWIS_26-27_IMB_GEN (hidden)
Name | In Folder | Grid | Out of Service | Pn | Pmax(act.) | Pmin(act.) | Qmax(act.) | Qmin(act.) | Act.Pow. | React.Pow. | Active Power | Reactive Power | Facility Code | Row Labels | Sum of Active Power
|  |  |  | MW | MW | MW | Mvar | Mvar | MW | Mvar | MW | Mvar |  | ALCOA_KWI | 62.5 | 59
GEN KBA GT | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | 0 | 46 | 46 | 10 | 28.1087 | -21.6209 | 35 | -4.84 |  |  | STHRNCRS_EG | ALCOA_PNJ | 87 | 87
Gen_AKW_G1 | AKW - ALCOA Kwinana | KW - Kwinana Load Area | 0 | 65.002 | 68 | 25 | 36.1 | -34.8 | 59 | 26.67 |  |  | ALCOA_KWI | ALCOA_WGP | 93 | 93
Gen_APJ_G2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 19.9999 | 25 | 10 | 15.575 | -11.75 | 19 | 9.54 |  |  | ALCOA_PNJ | PRK_AG | 94.7885 | 38
Gen_APJ_G3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 19.9999 | 25 | 10 | 15.575 | -11.75 | 19 | 2.96 |  |  | ALCOA_PNJ | STHRNCRS_EG | 70 | 70
Gen_APJ_G4 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 19.9999 | 25 | 10 | 15.575 | -11.75 | 19 | 2.96 |  |  | ALCOA_PNJ | WAPL_WORSLEY | 141.6108 | 99.6
Gen_APJ_G5 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 30 | 36 | 17 | 15 | -14.3 | 30 | 5.39 |  |  | ALCOA_PNJ | (blank) | 0
Gen_AWG_G1 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 25 | 30 | 12 | 18.75 | -14.3 | 25 | 5.29 |  |  | ALCOA_WGP | Grand Total | 548.8992
Gen_AWG_G2 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 18 | 21 | 9 | 13.5 | -9.1 | 18 | 4.53 |  |  | ALCOA_WGP
Gen_AWG_G3 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 18 | 21 | 9 | 13.5 | -9.1 | 18 | 4.53 |  |  | ALCOA_WGP
Gen_AWG_G4 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 37.7 | 40 | 18 | 27.9 | -21.9 | 32 | 11.89 |  |  | ALCOA_WGP
Gen_KNS_G1 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 1 | 10.72 | 11 | 5 | 9.385 | -5.5 | 0 | 0 |  |  | STHRNCRS_EG
Gen_KNS_G3 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 1 | 11 | 12 | 5 | 8.8625 | -5.5 | 0 | 0 |  |  | STHRNCRS_EG
Gen_KNS_GT2 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 0 | 46 | 46 | 10 | 28.1087 | -21.6209 | 35 | 24.69 |  |  | STHRNCRS_EG
Gen_PRK_GT1 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | 40.0803 | -19.3161 | 38 | 11.84 |  |  | PRK_AG
Gen_PRK_GT2 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | 33.4279 | -19.517 | 0 | 0 |  |  | PRK_AG
Gen_PRK_GT3 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | 34.3333 | -19.6633 | 0 | 0 |  |  | PRK_AG
Gen_WAPL_G1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 1 | 27.5 | 30 | 13 | 25.7699 | -19.3571 | 0 | 0 |  |  | WAPL_WORSLEY
Gen_WAPL_G2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 1 | 27.5 | 30 | 13 | 20.8521 | -14.1614 | 0 | 0 |  |  | WAPL_WORSLEY
Gen_WAPL_G3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 27.5 | 30 | 13 | 21.5041 | -14.8593 | 25.6 | 18.59 |  |  | WAPL_WORSLEY
Gen_WAPL_G4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 32 | 35 | 16 | 24 | -7.25 | 32 | 4.88 |  |  | WAPL_WORSLEY
Gen_WAPL_G5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 57.84 | 61 | 27 | 49.3882 | -38.4321 | 42 | 27.15 |  |  | WAPL_WORSLEY
Gen_WAPL_G6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 57.84 | 61 | 27 | 49.3882 | -38.4321 | 42 | 27.15 |  |  | WAPL_WORSLEY
[10 empty] | Total Generation @ IMB_Generation | 0
Name | In Folder | Grid | Zone | Active Power | Reactive Power | Facility Code |  | Row Labels | Sum of Active Power
|  |  |  | MW | Mvar |  |  | ALCOA_KWI | 63.9 | 0
IMB LOAD - AKW - 22.0 kV | AKW - ALCOA Kwinana | KW - Kwinana Load Area | Imbedded | 0 | #REF! | ALCOA_KWI |  | ALCOA_PNJ | 127.2 | 107.5
IMB LOAD - APJ - 13.8 kV / 1 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 41 | #REF! | ALCOA_PNJ |  | ALCOA_WGP | 82.1 | 82.3
IMB LOAD - APJ - 13.8 kV / 2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 30.7 | #REF! | ALCOA_PNJ |  | PRK_AG | 46.4 | 46.4
IMB LOAD - APJ - 13.8 kV / 3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 30.7 | #REF! | ALCOA_PNJ |  | STHRNCRS_EG | 63.6 | 63.2 | 6.8
IMB LOAD - APJ - 33.0 kV | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 5.1 | #REF! | ALCOA_PNJ |  | WAPL_WORSLEY | 146.5 | 146.5
IMB LOAD - AWG - 22.0 kV | AWG - Alcoa Wagerup | MU - Muja Load Area | Imbedded | 82.3 | #REF! | ALCOA_WGP |  | (blank) | 0
IMB LOAD - FIM - 33.0 kV | FIM - Fimiston | EG - Eastern Goldfields Load Area | Imbedded | 46.4 | #REF! | PRK_AG |  | Grand Total | 529.7
IMB LOAD - JAN | JAN - Jan | EG - Eastern Goldfields Load Area | Imbedded | 17.2 | #REF! | STHRNCRS_EG
IMB LOAD - KNS | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | Imbedded | 29.9 | #REF! | STHRNCRS_EG
IMB LOAD - LEF | LEF - Lefroy | EG - Eastern Goldfields Load Area | Imbedded | 5.1 | #REF! | STHRNCRS_EG
IMB LOAD - WAPL / 1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 24.9 | #REF! | WAPL_WORSLEY
IMB LOAD - WAPL / 2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 24.9 | #REF! | WAPL_WORSLEY
IMB LOAD - WAPL / 3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 24.9 | #REF! | WAPL_WORSLEY
IMB LOAD - WAPL / 4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 1.5 | #REF! | WAPL_WORSLEY
IMB LOAD - WAPL / 5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 65.9 | #REF! | WAPL_WORSLEY
IMB LOAD - WAPL / 6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 4.4 | #REF! | WAPL_WORSLEY
IMB LOAD - WMK | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | Imbedded | 11 | #REF! | STHRNCRS_EG
|  |  | Total Generation @ IMB_LOAD | 445.9
Facility Code | Total Net Value from IMB_GEN Sites Observed Std.dev_High End_MW @ SYS_MAX (+/-: GEN/LOAD) | MW (as Load) to be considered in RCM
ALCOA_KWI | -2.6603 | -2.6603
ALCOA_PNJ | -20.5298 | -20.5298
ALCOA_WGP | 5.2568 | 0
PRK_AG | -0.86744 | -0.86744
STHRNCRS_EG | 4.3783 | 0
WAPL_WORSLEY | -4.3964 | -4.3964
| Total MW (as Load) to be considered in RCM | -28.4539
Facility Code | Total Net Value from IMB_GEN Sites Observed Std.dev_High End_MW @ SYS_MAX (+/-: GEN/LOAD) | MW (as Load) to be considered in RCM
ALCOA_KWI | 59 | 0
ALCOA_PNJ | -20.5 | -20.5
ALCOA_WGP | 10.7 | 0
PRK_AG | -8.4 | -8.4
STHRNCRS_EG | 6.8 | 0
WAPL_WORSLEY | -46.9 | -46.9
| Total MW (as Load) to be considered in RCM | -75.8
Confidential - Not to be published

## SWIS_24-25_Forecast (hidden)
Name | In Folder | Grid | Zone | Active Power | Reactive Power | Load Demand % |  |  | MW | MVAR | Zone | Normal |  | Z/S contains both HV/LV Loads | Zone | (Multiple Items)
|  |  |  | MW | Mvar | 100% |  | Total_Load Demand | 4921.3735 | 1034.0389
BWF_sub_load | BGA - Badgingarra Wind Farm | NC - North Country Load Area | Use On Works | 0 | 0 |  |  | Generator Auxiliary Load | 90.3735 | 64.8389 | Row Labels | Sum of Active Power | Sum of Load Demand |  | Row Labels | Sum of Active Power | Sum of Load Demand
DYN LOAD - BKF - PQ LOAD | SUB LOAD - BKF - 33.0 kV | LOAD MODELLING |  | 0 | 0 |  |  | HV Customer | 643.5 | 183.4 | A - Arkana | 46.9 | 1.084% | #N/A | ABD - ALCOA Boddington | 3.4 | 0.07859%
DYN LOAD - BLD - PQ LOAD | IMB LOAD - BLD - 33 kV | LOAD MODELLING |  | 0 | 0 |  |  | Imbedded Generator Site_Load | 520.2 | 251.3 | ALB - Albany | 35.5 | 0.8206% | #N/A | AFM - Australian Fused Materials | 4.2 | 0.09709%
DYN LOAD - JAN - PQ LOAD | IMB LOAD - JAN - 66.0 kV | LOAD MODELLING |  | 0 | 0 |  |  | Normal Substation LV | 3667.3 | 534.5 | AMT - Amherst | 73.9 | 1.708% | #N/A | AKW - ALCOA Kwinana | 58.2 | 0%
DYN LOAD - KNS - STATIC LOAD | KNS - Kambalda Nickle Smelter | LOAD MODELLING |  | 0 | 0 |  |  | Sub_Total Load Demand (excl. Imbedded) | 4401.1735 | 782.7389 | APM - Australian Paper Mills | 25.4 | 0.5871% | #N/A | APJ - ALCOA Pinjarra | 102.2 | 0.3514%
DYN LOAD - KRA HPGR VSD MOTORS GRP1 | KRA - Karara Mine | LOAD MODELLING |  | 0 | 0 |  |  | Total Required Generation @ BMO (excl. assumed net output from IMB Sites_observed historic data) | 4326 |  | BCH - Beechboro | 64.2 | 1.484% | #N/A | AWG - Alcoa Wagerup | 77.5 | 0%
DYN LOAD - KRA HPGR VSD MOTORS GRP2 | KRA - Karara Mine | LOAD MODELLING |  | 0 | 0 | [5 empty] | BCT - Balcatta | 12.8 | 0.2959% | #N/A | BDE - Bandee | 0.6 | 0.01387%
DYN LOAD - KRA LOAD | KRA - Karara Mine | LOAD MODELLING |  | 0 | 0 | [5 empty] | BEL - Belmont | 41 | 0.9478% | #N/A | BDP - Binningup Desalination Plant | 35.3 | 0.816%
DYN LOAD - KRA LOAD - AFTER LOAD SHED | KRA - Karara Mine | LOAD MODELLING |  | 0 | 0 | [5 empty] | BIB - Bibra Lake | 53.6 | 1.239% | #N/A | BEC - Beckenham | 9 | 0.208%
DYN LOAD - NKO North Load | WMK - Western Mining Kambalda | LOAD MODELLING |  | 0 | 0 | [5 empty] | BKF - Black Flag | 34.6 | 0.7998% | #N/A | BGM - Boddington Gold Mine | 130.8 | 3.024%
DYN LOAD - WKT33 - PQ LOAD | SUB LOAD - WKT - 33.0 kV | LOAD MODELLING |  | 0 | 0 | [5 empty] | BLD - Boulder | 27.1 | 0.6264% | #N/A | BHK - Broken Hill Kwinana | 13.3 | 0.3074%
DYN LOAD - WMK - STATIC LOAD | WMK - Western Mining Kambalda | LOAD MODELLING |  | 0 | 0 | [5 empty] | BNP - Beenup | 6.4 | 0.1479% | #N/A | BLV - Bellevue | 5.4 | 0.1248%
DYN LOAD - WMK - Township | WMK - Western Mining Kambalda | LOAD MODELLING |  | 0 | 0 | [5 empty] | BSN - Busselton | 41.4 | 0.957% | #N/A | BNY - Bounty | 9.5 | 0.2196%
DYN LOAD - YLN - PQ LOAD | SUB LOAD - YLN - 33.0 kV | LOAD MODELLING |  | 0 | 0 | [5 empty] | BTN - Bridgetown | 25.4 | 0.5871% | #N/A | BPR - B.P. Refinery | 0 | 0%
GEN LOAD - APJ - G2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 1.4 | 1.05 | [5 empty] | BTY - Bentley | 36.6 | 0.846% | #N/A | BSI - Barrack Silicon Smelter | 73 | 1.687%
GEN LOAD - APJ - G3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 1.4 | 1.05 | [5 empty] | BUH - Bunbury Harbour | 62.6 | 1.447% | 13 | BTN - Bridgetown | 15 | 0.3467%
GEN LOAD - APJ - G4 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 1.4 | 1.05 | [5 empty] | BYF - Byford | 77 | 1.78% | 18 | CAR - Carrabin | 8.5 | 0.1965%
GEN LOAD - APJ - G5 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 2.45 | 1.837 | [5 empty] | CAP - Capel | 20.5 | 0.4739% | #N/A | CBP - CSBP | 9 | 0.208%
GEN LOAD - APJ - GT1 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 0.84 | 0.63 | [5 empty] | CAR - Carrabin | 0.3 | 0.006935% | #N/A | CCL - Cockburn Cement Ltd | 9.2 | 0.2127%
GEN LOAD - APJ - GT2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Use On Works | 3.78 | 2.835 | [5 empty] | CC - Cockburn Cement | 32.7 | 0.7559% | #N/A | CTB - Cataby | 8.4 | 0.1942%
GEN LOAD - AWG - G1 | AWG - Alcoa Wagerup | MU - Muja Load Area | Use On Works | 1.4 | 1.05 | [5 empty] | CK - Cook Street | 44.4 | 1.026% | #N/A | EDG - Edgewater | 7.1 | 0.1641%
GEN LOAD - AWG - G2 | AWG - Alcoa Wagerup | MU - Muja Load Area | Use On Works | 0.938 | 0.703 | [5 empty] | CKN - Clarkson | 68.3 | 1.579% | 32 | FFD - Forrestfield | 5 | 0.1156%
GEN LOAD - AWG - G3 | AWG - Alcoa Wagerup | MU - Muja Load Area | Use On Works | 0.938 | 0.703 | [5 empty] | CL - Clarence St | 29 | 0.6704% | #N/A | FIM - Fimiston | 53.8 | 0%
GEN LOAD - AWG - G4 | AWG - Alcoa Wagerup | MU - Muja Load Area | Use On Works | 2.24 | 1.68 | [5 empty] | CO - Collie | 12.5 | 0.289% | #N/A | GGV - Golden Grove | 17.2 | 0.3976%
GEN LOAD - AWG - GT1 | LWT - Landwehr Terminal | MU - Muja Load Area | Use On Works | 4.86 | 3.645 | [5 empty] | COL - Collier | 38.9 | 0.8992% | #N/A | GNI - Glen Iris | 13.2 | 0.3051%
GEN LOAD - AWG - GT2 | LWT - Landwehr Terminal | MU - Muja Load Area | Use On Works | 4.86 | 3.645 | [5 empty] | CPN - Chapman | 11.8 | 0.2728% | #N/A | JAN - Jan | 17.2 | 0%
GEN LOAD - BWP - G1 | BWP - Bluewaters Power Station | MU - Muja Load Area | Use On Works | 0 | 0 | [5 empty] | CTE - Cottesloe 132kV | 46.5 | 1.075% | #N/A | KDP - Kwinana Desalination Plant | 24.4 | 0.564%
GEN LOAD - BWP - G2 | BWP - Bluewaters Power Station | MU - Muja Load Area | Use On Works | 0 | 0 | [5 empty] | CUN - Cunderin | 5.9 | 0.1364% | #N/A | KMC - Kerr McGee Cataby | 11.1 | 0.2566%
GEN LOAD - CKB - GT1 | CKB - Cockburn Power | KW - Kwinana Load Area | Use On Works | 4.1 | 3 | [5 empty] | CVE - Canning Vale | 50.2 | 1.16% | #N/A | KMM - Kerr McGee Muchea | 9.1 | 0.2104%
GEN LOAD - CKB - SG1 | CKB - Cockburn Power | KW - Kwinana Load Area | Use On Works | 1.6 | 1.2 | [5 empty] | D - Darlington | 21.7 | 0.5016% | #N/A | KNS - Kambalda Nickle Smelter | 29.5 | 0%
GEN LOAD - CPS - G1 | CPS - Collie Power Station Terminal | MU - Muja Load Area | Use On Works | 22.4 | 16.8 | [5 empty] | E - Edmund Street | 22.4 | 0.5178% | #N/A | KRA - Karara Mine | 78.7 | 1.819%
GEN LOAD - GNN - GT11 | GNN - Newgen Neerabup | NT - Northern Terminal Load Area | Use On Works | 0 | 0 | [5 empty] | ENB - Eneabba | 6.9 | 0.1595% | #N/A | LEF - Lefroy | 5.1 | 0%
GEN LOAD - GNN - GT12 | GNN - Newgen Neerabup | NT - Northern Terminal Load Area | Use On Works | 0 | 0 | [5 empty] | FFD - Forrestfield | 29.9 | 0.6912% | #N/A | MRN - Mason Road North | 29 | 0.6704%
GEN LOAD - KMK - GT1 | KMK - Kerr McGee Kwinana | KW - Kwinana Load Area | Use On Works | [7 empty] | G - Gosnells | 48.2 | 1.114% | #N/A | NOW - Nowergup | 7.5 | 0.1734%
GEN LOAD - KMP - GT1 | KMP - Kemerton Power | BPS - Bunbury Load Area | Use On Works | 1.69 | 1.047 | [5 empty] | GTN - Geraldton | 28.2 | 0.6519% | 73 | NP - North Perth | 8.1 | 0.1872%
GEN LOAD - KMP - GT2 | KMP - Kemerton Power | BPS - Bunbury Load Area | Use On Works | 1.69 | 1.047 | [5 empty] | H - Hadfields | 46.3 | 1.07% | #N/A | PLD - Parklands | 4 | 0.09246%
GEN LOAD - KPP - GT1 | KPP - Kwinana Power Partnership | KW - Kwinana Load Area | Use On Works | 0 | 0 | [5 empty] | HAY - Hay Street | 46.2 | 1.068% | #N/A | SUM - Summers Street | 8 | 0.1849%
GEN LOAD - KPP - GT2 | KPP - Kwinana Power Partnership | KW - Kwinana Load Area | Use On Works | 0 | 0 | [5 empty] | HBK - Henley Brook | 62.1 | 1.436% | #N/A | TLA - Tianqi Lithium Australia | 16 | 0.3699%
GEN LOAD - KPP - SG1 | KPP - Kwinana Power Partnership | KW - Kwinana Load Area | Use On Works | 0 | 0 | [5 empty] | HZM - Hazelmere | 24.8 | 0.5733% | #N/A | TPP - Tiwest Pigment Plant | 27.8 | 0.6426%
GEN LOAD - KPS - GT1 | KW - Kwinana | KW - Kwinana Load Area | Use On Works | [7 empty] | JDP - Joondalup | 48.2 | 1.114% | #N/A | WAPL - Worsley Alumina Pty Ltd | 158.9 | 0%
GEN LOAD - MDP - G1 | MDP - Merredin Power Station | EC - East Country Load Area | Use On Works | [7 empty] | JTE - Joel Terrace 132kV | 54.4 | 1.258% | #N/A | WCL - Western Colleries Limited | 5.5 | 0.1271%
GEN LOAD - MDP - G2 | MDP - Merredin Power Station | EC - East Country Load Area | Use On Works | [7 empty] | K - Kalamunda | 30.2 | 0.6981% |  | WM - Western Mining | 31.3 | 0.7235%
GEN LOAD - MGA - GT1 | MGA - Mungarra | NC - North Country Load Area | Use On Works | [7 empty] | KAT - Katanning | 11 | 0.2543% |  | WMK - Western Mining Kambalda | 17.8 | 0%
GEN LOAD - MGA - GT3 | MGA - Mungarra | NC - North Country Load Area | Use On Works | [7 empty] | KDL - Kewdale | 25.9 | 0.5987% |  | WSD - Westralian Sands | 5.9 | 0.1364%
GEN LOAD - MPS - G7 | MPS - Muja Power Station | MU - Muja Load Area | Use On Works | 5 | 3.75 | [5 empty] | KDN - Kondinin | 7.1 | 0.1641% |  | Grand Total | 1163.7 | 15.23%
GEN LOAD - MPS - G8 | MPS - Muja Power Station | MU - Muja Load Area | Use On Works | 5 | 3.75 | [5 empty] | KEL - Kellerberrin | 2.8 | 0.06472%
GEN LOAD - NGK - GT3 | KW - Kwinana | KW - Kwinana Load Area | Use On Works | 6.93 | 5.197 | [5 empty] | KOJ - Kojonup | 2.2 | 0.05086%
GEN LOAD - NGK - SG3 | KW - Kwinana | KW - Kwinana Load Area | Use On Works | 6.907 | 5.181 | [5 empty] | LDE - Landsdale | 82.1 | 1.898%
GEN LOAD - PJR - GT1 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MA - Manning Street | 31.2 | 0.7212%
GEN LOAD - PJR - GT10 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | 0.51 | 0.382 | [5 empty] | MBR - Mount Barker | 6.2 | 0.1433%
GEN LOAD - PJR - GT11 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | 0.57 | 0.427 | [5 empty] | MCE - Medical Centre 132kV | 45.5 | 1.052%
GEN LOAD - PJR - GT2 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MDN - Maddington | 20.6 | 0.4762%
GEN LOAD - PJR - GT3 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MDY - Munday | 21.5 | 0.497%
GEN LOAD - PJR - GT4 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MED - Medina | 58.7 | 1.357%
GEN LOAD - PJR - GT5 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MER - Merredin | 8.2 | 0.1896%
GEN LOAD - PJR - GT7 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | [7 empty] | MH - Mandurah | 72.6 | 1.678%
GEN LOAD - PJR - GT9 | PJR - Pinjar Power Station | NT - Northern Terminal Load Area | Use On Works | 0.51 | 0.382 | [5 empty] | MIL - Milligan Street | 58.8 | 1.359%
GEN LOAD - PRK - GT1 | PRK - Parkeston | EG - Eastern Goldfields Load Area | Use On Works | 0.2 | 0.15 | [5 empty] | MJ - Midland Junction | 48.4 | 1.119%
GEN LOAD - PRK - GT2 | PRK - Parkeston | EG - Eastern Goldfields Load Area | Use On Works | [7 empty] | MJP - Manjimup | 10.9 | 0.252%
GEN LOAD - PRK - GT3 | PRK - Parkeston | EG - Eastern Goldfields Load Area | Use On Works | [7 empty] | MLG - Malaga | 36.4 | 0.8414%
GEN LOAD - WKT - GT2 | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Use On Works | [7 empty] | MO - Morley | 49.9 | 1.153%
GEN LOAD - WKT - GT3 | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Use On Works | [7 empty] | MOR - Moora | 11.9 | 0.2751%
General Load | BLD - Boulder | EG - Eastern Goldfields Load Area | Other | [7 empty] | MR - Margaret River | 12.3 | 0.2843%
General Load | PCY - Piccadilly St | EG - Eastern Goldfields Load Area | Other | [7 empty] | MRR - Marriott Road | 58.2 | 1.345%
General Load | WKT - West Kalgoorlie | EG - Eastern Goldfields Load Area | Other | [7 empty] | MSR - Mason Road | 33.1 | 0.7651%
General Load(1) | LTH - Leath Road_Kwinana Waste Energy | KW - Kwinana Load Area | Use On Works | 4 | 1.3147 | [5 empty] | MSS - Meadow Springs | 71.1 | 1.644%
General Load(1) | BLD - Boulder | EG - Eastern Goldfields Load Area | Other | [7 empty] | MUC - Muchea | 26.9 | 0.6218%
General Load(1) | PCY - Piccadilly St | EG - Eastern Goldfields Load Area | Other | [7 empty] | MUL - Mullaloo | 48.4 | 1.119%
HV CUST - ABD | ABD - ALCOA Boddington | MU - Muja Load Area | HV Customer | 3.4 | 0.3 | 0.07859% |  |  |  |  | MUR - Murdoch | 32.9 | 0.7605%
HV CUST - AFM | AFM - Australian Fused Materials | KW - Kwinana Load Area | HV Customer | 4.2 | 0.2 | 0.09709% |  |  |  |  | MYR - Myaree | 42.8 | 0.9894%
HV CUST - BDE | BDE - Bandee | EC - East Country Load Area | HV Customer | 0.6 | 0 | 0.01387% |  |  |  |  | NB - North Beach | 57.6 | 1.331%
HV CUST - BEC - PTA | BEC - Beckenham | CT - Cannington Terminal Load Area | HV Customer | 9 | 1.8 | 0.208% |  |  |  |  | NGN - Narrogin | 13.3 | 0.3074%
HV CUST - BGM | BGM - Boddington Gold Mine | MU - Muja Load Area | HV Customer | 130.8 | 24.7 | 3.024% |  |  |  |  | NOR - Northam | 22.6 | 0.5224%
HV CUST - BHK | BHK - Broken Hill Kwinana | KW - Kwinana Load Area | HV Customer | 13.3 | -2e-12 | 0.3074% |  |  |  |  | NP - North Perth | 52.3 | 1.209%
HV CUST - BLV - PTA | BLV - Bellevue | GLT - Guildford Terminal Load Area | HV Customer | 5.4 | 1.8 | 0.1248% |  |  |  |  | OC - OConnor | 53 | 1.225%
HV CUST - BNY | BNY - Bounty | EC - East Country Load Area | HV Customer | 9.5 | 1.8 | 0.2196% |  |  |  |  | OP - Osborne Park | 41.8 | 0.9663%
HV CUST - BPR - 132.0 kV | BPR - B.P. Refinery | KW - Kwinana Load Area | HV Customer | 0 | 0 | 0% |  |  |  |  | PBY - Padbury | 64.9 | 1.5%
HV CUST - BSI | BSI - Barrack Silicon Smelter | BPS - Bunbury Load Area | HV Customer | 73 | 9.5 | 1.687% |  |  |  |  | PCY - Piccadilly St | 24.9 | 0.5756%
HV CUST - BTN | BTN - Bridgetown | MU - Muja Load Area | HV Customer | 15 | 9.9 | 0.3467% |  |  |  |  | PIC - Picton | 39.8 | 0.92%
HV CUST - CCL | CCL - Cockburn Cement Ltd | ST - Southern Terminal Load Area | HV Customer | 9.2 | 1.3 | 0.2127% |  |  |  |  | PNJ - Pinjarra | 20.5 | 0.4739%
HV CUST - CSBP LOAD SIMPLIFIED | CBP - CSBP | KW - Kwinana Load Area | HV Customer | 9 | 3.5 | 0.208% |  |  |  |  | RAN - Rangeway | 24.9 | 0.5756%
HV CUST - EDG - PTA | EDG - Edgewater | NT - Northern Terminal Load Area | HV Customer | 7.1 | 8.4 | 0.1641% |  |  |  |  | RGN22 - Regans 22 kV | 5.7 | 0.1318%
HV CUST - EGM | CAR - Carrabin | EC - East Country Load Area | HV Customer | 8.5 | 4.8 | 0.1965% |  |  |  |  | RGN33 - Regans 33 kV | 7.1 | 0.1641%
HV CUST - GGV | GGV - Golden Grove | NC - North Country Load Area | HV Customer | 17.2 | 4 | 0.3976% |  |  |  |  | RO - Rockingham | 58.3 | 1.348%
HV CUST - IIuka Cataby Mine - 33.0 kV | CTB - Cataby | NC - North Country Load Area | HV Customer | 8.4 | -2.2 | 0.1942% |  |  |  |  | RTN - Riverton | 76 | 1.757%
HV CUST - KBP - 132.0 kV | MRN - Mason Road North | KW - Kwinana Load Area | HV Customer | 29 | 8.9 | 0.6704% |  |  |  |  | RVE - Rivervale | 53.4 | 1.234%
HV CUST - KDP | KDP - Kwinana Desalination Plant | KW - Kwinana Load Area | HV Customer | 24.4 | 0.8 | 0.564% |  |  |  |  | SF - South Fremantle | 0 | 0%
HV CUST - KMC | KMC - Kerr McGee Cataby | NC - North Country Load Area | HV Customer | 11.1 | 9.6 | 0.2566% |  |  |  |  | SNR - Southern River | 83 | 1.919%
HV CUST - KMM | KMM - Kerr McGee Muchea | NT - Northern Terminal Load Area | HV Customer | 9.1 | 4.6 | 0.2104% |  |  |  |  | SPK - Shenton Park 132kV | 50.9 | 1.177%
HV CUST - KRA | KRA - Karara Mine | NC - North Country Load Area | HV Customer | 78.7 | 34.9 | 1.819% |  |  |  |  | SVY - Sawyers Valley 132kV | 25.2 | 0.5825%
HV CUST - LOAD - 132kV | BDP - Binningup Desalination Plant | BPS - Bunbury Load Area | HV Customer | 35.3 | 0.3 | 0.816% |  |  |  |  | SX - Southern Cross | 0.5 | 0.01156%
HV CUST - MVE - PTA | FFD - Forrestfield | GLT - Guildford Terminal Load Area | HV Customer | 5 | 0 | 0.1156% |  |  |  |  | TS - Three Springs | 9.2 | 0.2127%
HV CUST - NOW - PTA | NOW - Nowergup | NT - Northern Terminal Load Area | HV Customer | 7.5 | 2.5 | 0.1734% |  |  |  |  | W - Wellington Street | 0 | 0%
HV CUST - SRD | NP - North Perth | EP - East Perth Load Area | HV Customer | 8.1 | 1.8 | 0.1872% |  |  |  |  | WAG - Wagin | 4.4 | 0.1017%
HV CUST - SUM - PTA | SUM - Summers Street | EP - East Perth Load Area | HV Customer | 8 | -0.7 | 0.1849% |  |  |  |  | WAI - Waikiki | 80.1 | 1.852%
HV CUST - TLA - 6.6 kV | TLA - Tianqi Lithium Australia | KW - Kwinana Load Area | HV Customer | 16 | 5.3 | 0.3699% |  |  |  |  | WD - Wembley Downs | 35.1 | 0.8114%
HV CUST - TPP - 132.0 kV | TPP - Tiwest Pigment Plant | KW - Kwinana Load Area | HV Customer | 27.8 | 24.6 | 0.6426% |  |  |  |  | WE - Welshpool | 54.5 | 1.26%
HV CUST - WCL | WCL - Western Colleries Limited | MU - Muja Load Area | HV Customer | 5.5 | 2.2 | 0.1271% |  |  |  |  | WGA - Wangara | 16.6 | 0.3837%
HV CUST - WM | WM - Western Mining | KW - Kwinana Load Area | HV Customer | 31.3 | 14.4 | 0.7235% |  |  |  |  | WGP - Wagerup | 17.2 | 0.3976%
HV CUST - WSD | WSD - Westralian Sands | BPS - Bunbury Load Area | HV Customer | 5.9 | 3.1 | 0.1364% | 0 |  |  |  | WKT11 - West Kalgoorlie 11 kV | 6.5 | 0.1503%
IMB LOAD - AKW - 22.0 kV | AKW - ALCOA Kwinana | KW - Kwinana Load Area | Imbedded | 58.2 | 24.7 | 0% | 15.2 |  |  |  | WKT33 - West Kalgoorlie 33 kV | 22.1 | 0.5109%
IMB LOAD - APJ - 13.8 kV / 1 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 40.9 | 14.8 | 0.3514% |  |  |  |  | WLN - Willetton | 19.6 | 0.4531%
IMB LOAD - APJ - 13.8 kV / 2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 28.6 | 10.4 | [5 empty] | WNO - Wanneroo | 59.6 | 1.378%
IMB LOAD - APJ - 13.8 kV / 3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 28.6 | 10.4 | [5 empty] | WUN - Wundowie | 8.4 | 0.1942%
IMB LOAD - APJ - 33.0 kV | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 4.1 | 1.5 |  | 0 |  |  |  | Y - Yokine | 63.5 | 1.468%
IMB LOAD - AWG - 22.0 kV | AWG - Alcoa Wagerup | MU - Muja Load Area | Imbedded | 77.5 | 31.7 | 0% | 0 |  |  |  | YER - Yerbillon | 2.1 | 0.04854%
IMB LOAD - FIM - 33.0 kV | FIM - Fimiston | EG - Eastern Goldfields Load Area | Imbedded | 53.8 | 37.7 | 0% |  |  |  |  | YLN - Yilgarn | 10.8 | 0.2497%
IMB LOAD - JAN | JAN - Jan | EG - Eastern Goldfields Load Area | Imbedded | 17.2 | 1.4 |  | 0 |  |  |  | YP - Yanchep | 49.4 | 1.142%
IMB LOAD - KNS | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | Imbedded | 29.5 | 24.9 | 0% |  |  |  |  | Grand Total | 3667.3 | 84.77%
IMB LOAD - LEF | LEF - Lefroy | EG - Eastern Goldfields Load Area | Imbedded | 5.1 | 0.4 |  | 0
IMB LOAD - WAPL / 1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 27 | 15.9 | 0%
IMB LOAD - WAPL / 2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 27 | 15.9
IMB LOAD - WAPL / 3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 27 | 15.9
IMB LOAD - WAPL / 4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 1.6 | 0.9
IMB LOAD - WAPL / 5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 71.5 | 42
IMB LOAD - WAPL / 6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 4.8 | 2.8
IMB LOAD - WMK | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | Imbedded | 17.8 | 0
KCGM - MOT4 - VSD | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
KCGM - MOT7 - VSD | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
KCGM - STATIC | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
KCGM - Sag Mill 1 - CCV | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
KCGM - Sag Mill 2 - CCV | KCGM - Kalgoorlie Consolidated Mine Site | LOAD MODELLING |  | 0 | 0
Lumped Load_BATP | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.16524 | 0.080029
Lumped Load_CSP | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.14094 | 0.06826
Lumped Load_Common1 | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.68076 | 0.32971
Lumped Load_Common2 | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.68076 | 0.32971
Lumped Load_FGT | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.16632 | 0.080552
SUB LOAD - A - 22.0 kV | A - Arkana | NT - Northern Terminal Load Area | Normal | 46.9 | 10.9 | 1.084%
SUB LOAD - ALB - 22.0 kV | ALB - Albany | MU - Muja Load Area | Normal | 35.5 | 2.1 | 0.8206%
SUB LOAD - AMT - 22.0 kV | AMT - Amherst | SF - South Fremantle Load Area | Normal | 73.9 | 7.3 | 1.708%
SUB LOAD - APM - 22.0 kV | APM - Australian Paper Mills | SF - South Fremantle Load Area | Normal | 25.4 | 4.6 | 0.5871%
SUB LOAD - BCH - 22.0 kV | BCH - Beechboro | NT - Northern Terminal Load Area | Normal | 64.2 | 1.5 | 1.484%
SUB LOAD - BCT - 22.0 kV | BCT - Balcatta | NT - Northern Terminal Load Area | Normal | 12.8 | 2.5 | 0.2959%
SUB LOAD - BEL - 22.0 kV | BEL - Belmont | CT - Cannington Terminal Load Area | Normal | 41 | 8.6 | 0.9478%
SUB LOAD - BIB - 22.0 kV | BIB - Bibra Lake | SF - South Fremantle Load Area | Normal | 53.6 | 5.7 | 1.239%
SUB LOAD - BKF - 33.0 kV | BKF - Black Flag | EG - Eastern Goldfields Load Area | Normal | 34.6 | 13.6 | 0.7998%
SUB LOAD - BLD - 33 kV | BLD - Boulder | EG - Eastern Goldfields Load Area | Normal | 27.1 | 5.7 | 0.6264%
SUB LOAD - BNP - 22.0 kV | BNP - Beenup | MU - Muja Load Area | Normal | 6.4 | 0.5 | 0.1479%
SUB LOAD - BSN - 22.0 kV / 2 | BSN - Busselton | BPS - Bunbury Load Area | Normal | 24.8 | -0.1 | 0.5733%
SUB LOAD - BSN - T1 | BSN - Busselton | BPS - Bunbury Load Area | Normal | 8.3 | 0 | 0.1919%
SUB LOAD - BSN - T2 | BSN - Busselton | BPS - Bunbury Load Area | Normal | 8.3 | 0 | 0.1919%
SUB LOAD - BTN - 22.0 kV | BTN - Bridgetown | MU - Muja Load Area | Normal | 25.4 | 0.1 | 0.5871%
SUB LOAD - BTY - 22.0 kV | BTY - Bentley | CT - Cannington Terminal Load Area | Normal | 36.6 | 5.8 | 0.846%
SUB LOAD - BUH - 22.0 kV | BUH - Bunbury Harbour | BPS - Bunbury Load Area | Normal | 62.6 | 6.7 | 1.447%
SUB LOAD - BYF - 22.0 kV | BYF - Byford | ST - Southern Terminal Load Area | Normal | 77 | 5.3 | 1.78%
SUB LOAD - CAP - 22.0 kV | CAP - Capel | BPS - Bunbury Load Area | Normal | 20.5 | 6.8 | 0.4739%
SUB LOAD - CAR - 22.0 kV | CAR - Carrabin | EC - East Country Load Area | Normal | 0.3 | 0.1 | 0.006935%
SUB LOAD - CC - 22.0 kV | CC - Cockburn Cement | ST - Southern Terminal Load Area | Normal | 32.7 | 3.8 | 0.7559%
SUB LOAD - CK - 11.0 kV / 1 | CK - Cook Street | EP - East Perth Load Area | Normal | 22.2 | 4.6 | 0.5132%
SUB LOAD - CK - 11.0 kV / 2 | CK - Cook Street | EP - East Perth Load Area | Normal | 22.2 | 4.6 | 0.5132%
SUB LOAD - CKN - 22.0 kV | CKN - Clarkson | NT - Northern Terminal Load Area | Normal | 68.3 | 9.4 | 1.579%
SUB LOAD - CL - 11.0 kV | CL - Clarence St | CT - Cannington Terminal Load Area | Normal | 29 | 7.1 | 0.6704%
SUB LOAD - CO - 22.0 kV | CO - Collie | MU - Muja Load Area | Normal | 12.5 | 3.7 | 0.289%
SUB LOAD - COL - 11.0 kV | COL - Collier | CT - Cannington Terminal Load Area | Normal | 38.9 | 7.3 | 0.8992%
SUB LOAD - CPN - 11.0 kV | CPN - Chapman | NC - North Country Load Area | Normal | 11.8 | 1.7 | 0.2728%
SUB LOAD - CTE - 11.0 kV | CTE - Cottesloe 132kV | WT - Western Terminal Load Area | Normal | 46.5 | 8.4 | 1.075%
SUB LOAD - CUN - 22.0 kV | CUN - Cunderin | EC - East Country Load Area | Normal | 5.9 | 0.3 | 0.1364%
SUB LOAD - CVE - 22.0 kV | CVE - Canning Vale | ST - Southern Terminal Load Area | Normal | 50.2 | 8.6 | 1.16%
SUB LOAD - D - 22.0 kV | D - Darlington | GLT - Guildford Terminal Load Area | Normal | 21.7 | 1.2 | 0.5016%
SUB LOAD - E - 11.0 kV | E - Edmund Street | SF - South Fremantle Load Area | Normal | 22.4 | 6.3 | 0.5178%
SUB LOAD - ENB - 33.0 kV | ENB - Eneabba | NC - North Country Load Area | Normal | 6.9 | 4.1 | 0.1595%
SUB LOAD - FFD - 22.0 kV | FFD - Forrestfield | GLT - Guildford Terminal Load Area | Normal | 29.9 | 7.9 | 0.6912%
SUB LOAD - G - 22.0 kV | G - Gosnells | ST - Southern Terminal Load Area | Normal | 48.2 | 6.4 | 1.114%
SUB LOAD - GNI - 132.0 kV / 1 - PTA | GNI - Glen Iris | ST - Southern Terminal Load Area | HV Customer | 6.6 | 0.6 | 0.1526%
SUB LOAD - GNI - 132.0 kV / 2 - PTA | GNI - Glen Iris | ST - Southern Terminal Load Area | HV Customer | 6.6 | 0.6 | 0.1526%
SUB LOAD - GTN - 33.0 kV | GTN - Geraldton | NC - North Country Load Area | Normal | 28.2 | 2.4 | 0.6519%
SUB LOAD - H - 22.0 kV | H - Hadfields | NT - Northern Terminal Load Area | Normal | 46.3 | 6.5 | 1.07%
SUB LOAD - HAY - 11.0 kV / 1 | HAY - Hay Street | EP - East Perth Load Area | Normal | 23.1 | 4.3 | 0.534%
SUB LOAD - HAY - 11.0 kV / 2 | HAY - Hay Street | EP - East Perth Load Area | Normal | 23.1 | 4.3 | 0.534%
SUB LOAD - HBK - 22.0 kV | HBK - Henley Brook | NT - Northern Terminal Load Area | Normal | 62.1 | 1.7 | 1.436%
SUB LOAD - HZM - 22.0 kV | HZM - Hazelmere | GLT - Guildford Terminal Load Area | Normal | 24.8 | 5.2 | 0.5733%
SUB LOAD - JDP - 22.0 kV | JDP - Joondalup | NT - Northern Terminal Load Area | Normal | 48.2 | 6.7 | 1.114%
SUB LOAD - JTE - 11.0 kV | JTE - Joel Terrace 132kV | EP - East Perth Load Area | Normal | 54.4 | 9.2 | 1.258%
SUB LOAD - K - 22.0 kV | K - Kalamunda | GLT - Guildford Terminal Load Area | Normal | 30.2 | 5.9 | 0.6981%
SUB LOAD - KAT - 22.0 kV | KAT - Katanning | MU - Muja Load Area | Normal | 11 | 4.3 | 0.2543%
SUB LOAD - KDL - 22.0 kV | KDL - Kewdale | CT - Cannington Terminal Load Area | Normal | 25.9 | 7.8 | 0.5987%
SUB LOAD - KDN - 33.0 kV | KDN - Kondinin | EC - East Country Load Area | Normal | 7.1 | 4.2 | 0.1641%
SUB LOAD - KEL - 22.0 kV | KEL - Kellerberrin | EC - East Country Load Area | Normal | 2.8 | 0.2 | 0.06472%
SUB LOAD - KOJ - 22.0 kV | KOJ - Kojonup | MU - Muja Load Area | Normal | 2.2 | 0.1 | 0.05086%
SUB LOAD - LDE - 22.0 kV | LDE - Landsdale | NT - Northern Terminal Load Area | Normal | 82.1 | 8.6 | 1.898%
SUB LOAD - MA - 11.0 kV | MA - Manning Street | NT - Northern Terminal Load Area | Normal | 31.2 | -3.1 | 0.7212%
SUB LOAD - MBR - 22.0 kV | MBR - Mount Barker | MU - Muja Load Area | Normal | 6.2 | -0.8 | 0.1433%
SUB LOAD - MCE | MCE - Medical Centre 132kV | WT - Western Terminal Load Area | Normal | 45.5 | 11.2 | 1.052%
SUB LOAD - MDN - 22.0 kV | MDN - Maddington | ST - Southern Terminal Load Area | Normal | 20.6 | 4.6 | 0.4762%
SUB LOAD - MDY - 22.0 kV | MDY - Munday | GLT - Guildford Terminal Load Area | Normal | 21.5 | 5.3 | 0.497%
SUB LOAD - MED - 22.0 kV | MED - Medina | KW - Kwinana Load Area | Normal | 58.7 | 1.4 | 1.357%
SUB LOAD - MER - 22.0 kV | MER - Merredin | EC - East Country Load Area | Normal | 8.2 | 0.8 | 0.1896%
SUB LOAD - MH - 22.0 kV | MH - Mandurah | KW - Kwinana Load Area | Normal | 72.6 | 11.8 | 1.678%
SUB LOAD - MIL - 11.0 kV / 1 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 9.8 | 2.3 | 0.2265%
SUB LOAD - MIL - 11.0 kV / 2 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 9.8 | 7 | 0.2265%
SUB LOAD - MIL - 11.0 kV / 3 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 9.8 | 7 | 0.2265%
SUB LOAD - MIL - 11.0 kV / 4 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 9.8 | 2.3 | 0.2265%
SUB LOAD - MIL - 11.0 kV / 5 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 9.8 | 2.3 | 0.2265%
SUB LOAD - MIL - 11.0 kV / 6 | MIL - Milligan Street | EP - East Perth Load Area | Normal | 9.8 | 2.3 | 0.2265%
SUB LOAD - MJ - 22.0 kV | MJ - Midland Junction | GLT - Guildford Terminal Load Area | Normal | 48.4 | 8.3 | 1.119%
SUB LOAD - MJP - 22.0 kV | MJP - Manjimup | MU - Muja Load Area | Normal | 10.9 | 1 | 0.252%
SUB LOAD - MLG - 22.0 kV / 1 | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 12 | 3.7 | 0.2774%
SUB LOAD - MLG - 22.0 kV / 2 | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 12 | 3.7 | 0.2774%
SUB LOAD - MLG - 22.0 kV / 3 | MLG - Malaga | NT - Northern Terminal Load Area | Normal | 12.4 | 3.8 | 0.2866%
SUB LOAD - MO - 11.0 kV | MO - Morley | NT - Northern Terminal Load Area | Normal | 49.9 | 10.2 | 1.153%
SUB LOAD - MOR - T1 | MOR - Moora | NC - North Country Load Area | Normal | 3.2 | 0.7 | 0.07397%
SUB LOAD - MOR - T3 | MOR - Moora | NC - North Country Load Area | Normal | 8.7 | 1.8 | 0.2011%
SUB LOAD - MR - 22.0 kV | MR - Margaret River | BPS - Bunbury Load Area | Normal | 12.3 | -2.9 | 0.2843%
SUB LOAD - MRR - 22.0 kV | MRR - Marriott Road | BPS - Bunbury Load Area | Normal | 58.2 | 34.9 | 1.345%
SUB LOAD - MSR - 1 | MSR - Mason Road | KW - Kwinana Load Area | Normal | 10.9 | -9.2 | 0.252%
SUB LOAD - MSR - 2 | MSR - Mason Road | KW - Kwinana Load Area | Normal | 11.3 | -9.4 | 0.2612%
SUB LOAD - MSR - 3 | MSR - Mason Road | KW - Kwinana Load Area | Normal | 10.9 | -9.2 | 0.252%
SUB LOAD - MSS - 22.0 kV | MSS - Meadow Springs | KW - Kwinana Load Area | Normal | 71.1 | 3 | 1.644%
SUB LOAD - MUC - 22.0 kV | MUC - Muchea | NT - Northern Terminal Load Area | Normal | 26.9 | 2.2 | 0.6218%
SUB LOAD - MUL - 22.0 kV | MUL - Mullaloo | NT - Northern Terminal Load Area | Normal | 48.4 | 7 | 1.119%
SUB LOAD - MUR - 22.0 kV | MUR - Murdoch | ST - Southern Terminal Load Area | Normal | 32.9 | 4.7 | 0.7605%
SUB LOAD - MYR - 22.0 kV | MYR - Myaree | SF - South Fremantle Load Area | Normal | 42.8 | 12.6 | 0.9894%
SUB LOAD - NB - 22.0 kV | NB - North Beach | NT - Northern Terminal Load Area | Normal | 57.6 | 5.7 | 1.331%
SUB LOAD - NGN - 22.0 kV | NGN - Narrogin | MU - Muja Load Area | Normal | 13.3 | 2 | 0.3074%
SUB LOAD - NOR - 22.0 kV | NOR - Northam | EC - East Country Load Area | Normal | 22.6 | -1 | 0.5224%
SUB LOAD - NP - 11.0 kV | NP - North Perth | EP - East Perth Load Area | Normal | 52.3 | 6.9 | 1.209%
SUB LOAD - OC - 22.0 kV | OC - OConnor | SF - South Fremantle Load Area | Normal | 53 | 10 | 1.225%
SUB LOAD - OP - 11.0 kV | OP - Osborne Park | NT - Northern Terminal Load Area | Normal | 41.8 | 16.3 | 0.9663%
SUB LOAD - PBY - 22.0 kV | PBY - Padbury | NT - Northern Terminal Load Area | Normal | 64.9 | 5.6 | 1.5%
SUB LOAD - PCY - 11.0 kV | PCY - Piccadilly St | EG - Eastern Goldfields Load Area | Normal | 24.9 | 4.7 | 0.5756%
SUB LOAD - PIC - 22.0 kV | PIC - Picton | BPS - Bunbury Load Area | Normal | 39.8 | 7.7 | 0.92%
SUB LOAD - PLD - 22.0 kV - PTA | PLD - Parklands | KW - Kwinana Load Area | HV Customer | 4 | 0.1 | 0.09246%
SUB LOAD - PNJ - 22.0 kV | PNJ - Pinjarra | BPS - Bunbury Load Area | Normal | 20.5 | -2.7 | 0.4739%
SUB LOAD - RAN - 11.0 kV | RAN - Rangeway | NC - North Country Load Area | Normal | 24.9 | 4.3 | 0.5756%
SUB LOAD - RGN - 22.0 kV | RGN22 - Regans 22 kV | NC - North Country Load Area | Normal | 5.7 | 0.8 | 0.1318%
SUB LOAD - RGN - 33.0 kV | RGN33 - Regans 33 kV | NC - North Country Load Area | Normal | 7.1 | 2 | 0.1641%
SUB LOAD - RO - 22.0 kV | RO - Rockingham | KW - Kwinana Load Area | Normal | 58.3 | 14.6 | 1.348%
SUB LOAD - RTN - 22.0 kV | RTN - Riverton | ST - Southern Terminal Load Area | Normal | 76 | 7.2 | 1.757%
SUB LOAD - RVE - 22.0 kV | RVE - Rivervale | CT - Cannington Terminal Load Area | Normal | 53.4 | 6.8 | 1.234%
SUB LOAD - SF - 22.0kV | SF - South Fremantle | SF - South Fremantle Load Area | Normal | 0 | 0 | 0%
SUB LOAD - SNR - 22.0 kV | SNR - Southern River | ST - Southern Terminal Load Area | Normal | 83 | 1.1 | 1.919%
SUB LOAD - SPK / 1.A | SPK - Shenton Park 132kV | WT - Western Terminal Load Area | Normal | 50.9 | 11.3 | 1.177%
SUB LOAD - SVY - 22.0 kV | SVY - Sawyers Valley 132kV | EC - East Country Load Area | Normal | 25.2 | 1.4 | 0.5825%
SUB LOAD - SX - 33.0 kV | SX - Southern Cross | EC - East Country Load Area | Normal | 0.5 | 1.5 | 0.01156%
SUB LOAD - TS - 33.0 kV | TS - Three Springs | NC - North Country Load Area | Normal | 9.2 | 3.8 | 0.2127%
SUB LOAD - W - 11.0 kV / 1 | W - Wellington Street | EP - East Perth Load Area | Normal | 0 | 0 | 0%
SUB LOAD - W - 11.0 kV / 2 | W - Wellington Street | EP - East Perth Load Area | Normal | 0 | 0 | 0%
SUB LOAD - WAG - 22.0 kV | WAG - Wagin | MU - Muja Load Area | Normal | 4.4 | 0.2 | 0.1017%
SUB LOAD - WAI - 22.0 kV | WAI - Waikiki | KW - Kwinana Load Area | Normal | 80.1 | 2.6 | 1.852%
SUB LOAD - WD - 6.6 kV | WD - Wembley Downs | WT - Western Terminal Load Area | Normal | 35.1 | 8.2 | 0.8114%
SUB LOAD - WE - 22.0 kV | WE - Welshpool | CT - Cannington Terminal Load Area | Normal | 54.5 | 7.9 | 1.26%
SUB LOAD - WGA - 22.0 kV | WGA - Wangara | NT - Northern Terminal Load Area | Normal | 16.6 | 1.6 | 0.3837%
SUB LOAD - WGP - 22.0 kV | WGP - Wagerup | MU - Muja Load Area | Normal | 17.2 | 4.7 | 0.3976%
SUB LOAD - WKT - 11 kV | WKT11 - West Kalgoorlie 11 kV | EG - Eastern Goldfields Load Area | Normal | 6.5 | 0.4 | 0.1503%
SUB LOAD - WKT - 33.0 kV | WKT33 - West Kalgoorlie 33 kV | EG - Eastern Goldfields Load Area | Normal | 22.1 | 15.2 | 0.5109%
SUB LOAD - WLN - 22.0 kV | WLN - Willetton | ST - Southern Terminal Load Area | Normal | 19.6 | 2.2 | 0.4531%
SUB LOAD - WNO - 22.0 kV | WNO - Wanneroo | NT - Northern Terminal Load Area | Normal | 59.6 | 7.7 | 1.378%
SUB LOAD - WUN - 22.0 kV | WUN - Wundowie | EC - East Country Load Area | Normal | 8.4 | -2e-12 | 0.1942%
SUB LOAD - Y - 11.0 kV | Y - Yokine | NT - Northern Terminal Load Area | Normal | 63.5 | 10.2 | 1.468%
SUB LOAD - YER - 6.6 kV | YER - Yerbillon | EC - East Country Load Area | Normal | 2.1 | 0.1 | 0.04854%
SUB LOAD - YLN - 33.0 kV | YLN - Yilgarn | EC - East Country Load Area | Normal | 10.8 | 0.9 | 0.2497%
SUB LOAD - YP - 22.0 kV | YP - Yanchep | NT - Northern Terminal Load Area | Normal | 49.4 | -3.2 | 1.142%
VSD_CSP | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.27108 | 0.13129
VSD_Common1 | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.32373 | 0.15679
VSD_Common2 | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.32373 | 0.15679
VSD_FGT | OFE - Office Road Substation | KW - Kwinana Load Area | Use On Works | 0.00792 | 0
Confidential - Not to be published

## SWIS_24-25_IMB_GEN (hidden)
Name | In Folder | Grid | Out of Service | Pn | Pmax(act.) | Pmin(act.) | Qmax(act.) | Qmin(act.) | Act.Pow. | React.Pow. | Active Power | Reactive Power | Facility Code | Row Labels | Sum of Active Power
|  |  |  | MW | MW | MW | Mvar | Mvar | MW | Mvar | MW | Mvar |  | ALCOA_KWI | 60
GEN KBA GT | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | 0 | 46 | 46 | 10 | 28.1087 | -21.6209 | 46 | 7.1071 | 46 | -2.7904 | STHRNCRS_EG | ALCOA_PNJ | 87
Gen_AKW_G1 | AKW - ALCOA Kwinana | KW - Kwinana Load Area | 0 | 65.002 | 68 | 25 | 36.1 | -34.8 | 60 | 0 | 60 | 24.3121 | ALCOA_KWI | ALCOA_WGP | 98.7
Gen_APJ_G2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 19.9999 | 25 | 10 | 15.575 | -11.75 | 19 | 6.5737 | 19 | 5.2563 | ALCOA_PNJ | PRK_AG | 64.2886
Gen_APJ_G3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 19.9999 | 25 | 10 | 15.575 | -11.75 | 19 | 0 | 19 | -1.3174 | ALCOA_PNJ | STHRNCRS_EG | 92
Gen_APJ_G4 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 19.9999 | 25 | 10 | 15.575 | -11.75 | 19 | 0 | 19 | -1.3174 | ALCOA_PNJ | WAPL_WORSLEY | 173.2958
Gen_APJ_G5 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | 0 | 30 | 36 | 17 | 15 | -14.3 | 30 | 0 | 30 | -2.3982 | ALCOA_PNJ | (blank) | 0
Gen_AWG_G1 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 25 | 30 | 12 | 18.75 | -14.3 | 25 | 6.3398 | 25 | 10.2603 | ALCOA_WGP | Grand Total | 575.2844
Gen_AWG_G2 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 18 | 21 | 9 | 13.5 | -9.1 | 18 | 8.6958 | 18 | 9.1488 | ALCOA_WGP
Gen_AWG_G3 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 18 | 21 | 9 | 13.5 | -9.1 | 18 | 8.6958 | 18 | 9.1488 | ALCOA_WGP
Gen_AWG_G4 | AWG - Alcoa Wagerup | MU - Muja Load Area | 0 | 37.7 | 40 | 18 | 27.9 | -21.9 | 37.7 | 9.1241 | 37.7 | 22.7327 | ALCOA_WGP
Gen_KNS_G1 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 1 | 10.72 | 11 | 5 | 9.385 | -5.5 | 9 | 3.5235 |  |  | STHRNCRS_EG
Gen_KNS_G3 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 1 | 11 | 12 | 5 | 8.8625 | -5.5 | 10 | 6 |  |  | STHRNCRS_EG
Gen_KNS_GT2 | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | 0 | 46 | 46 | 10 | 28.1087 | -21.6209 | 46 | 22.3 | 46 | 5.2261 | STHRNCRS_EG
Gen_PRK_GT1 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | 40.0803 | -19.3161 | 32.1443 | 15.6924 | 32.1443 | 12.2706 | PRK_AG
Gen_PRK_GT2 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 0 | 44.6 | 38 | 7 | 33.4279 | -19.517 | 32.1443 | 15.6924 | 32.1443 | 2.3937 | PRK_AG
Gen_PRK_GT3 | PRK - Parkeston | EG - Eastern Goldfields Load Area | 1 | 44.6 | 38 | 7 | 34.3333 | -19.6633 | 30.5 | 15.6924 |  |  | PRK_AG
Gen_WAPL_G1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 1 | 27.5 | 30 | 13 | 25.7699 | -19.3571 | 13 | 7.5703 |  |  | WAPL_WORSLEY
Gen_WAPL_G2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 1 | 27.5 | 30 | 13 | 20.8521 | -14.1614 | 27 | 7.5703 |  |  | WAPL_WORSLEY
Gen_WAPL_G3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 27.5 | 30 | 13 | 21.5017 | -14.8568 | 25.6158 | 7.5703 | 25.6158 | 21.5017 | WAPL_WORSLEY
Gen_WAPL_G4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 32 | 35 | 16 | 24 | -7.25 | 32 | 4.5166 | 32 | 14.8602 | WAPL_WORSLEY
Gen_WAPL_G5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 57.84 | 61 | 27 | 49.3882 | -38.4321 | 57.84 | 0 | 57.84 | 33.3403 | WAPL_WORSLEY
Gen_WAPL_G6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | 0 | 57.84 | 61 | 27 | 49.3882 | -38.4321 | 57.84 | 0 | 57.84 | 33.3403 | WAPL_WORSLEY
[10 empty] | Total Generation @ IMB_Generation | 575.2844
Name | In Folder | Grid | Zone | Active Power | Reactive Power | Facility Code |  | Row Labels | Sum of Active Power
|  |  |  | MW | Mvar |  |  | ALCOA_KWI | 58.2
IMB LOAD - AKW - 22.0 kV | AKW - ALCOA Kwinana | KW - Kwinana Load Area | Imbedded | 58.2 | 24.7 | ALCOA_KWI |  | ALCOA_PNJ | 102.2
IMB LOAD - APJ - 13.8 kV / 1 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 40.9 | 14.8 | ALCOA_PNJ |  | ALCOA_WGP | 77.5
IMB LOAD - APJ - 13.8 kV / 2 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 28.6 | 10.4 | ALCOA_PNJ |  | PRK_AG | 53.8
IMB LOAD - APJ - 13.8 kV / 3 | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 28.6 | 10.4 | ALCOA_PNJ |  | STHRNCRS_EG | 69.6
IMB LOAD - APJ - 33.0 kV | APJ - ALCOA Pinjarra | BPS - Bunbury Load Area | Imbedded | 4.1 | 1.5 | ALCOA_PNJ |  | WAPL_WORSLEY | 158.9
IMB LOAD - AWG - 22.0 kV | AWG - Alcoa Wagerup | MU - Muja Load Area | Imbedded | 77.5 | 31.7 | ALCOA_WGP |  | (blank) | 0
IMB LOAD - FIM - 33.0 kV | FIM - Fimiston | EG - Eastern Goldfields Load Area | Imbedded | 53.8 | 37.7 | PRK_AG |  | Grand Total | 520.2
IMB LOAD - JAN | JAN - Jan | EG - Eastern Goldfields Load Area | Imbedded | 17.2 | 1.4 | STHRNCRS_EG
IMB LOAD - KNS | KNS - Kambalda Nickle Smelter | EG - Eastern Goldfields Load Area | Imbedded | 29.5 | 24.9 | STHRNCRS_EG
IMB LOAD - LEF | LEF - Lefroy | EG - Eastern Goldfields Load Area | Imbedded | 5.1 | 0.4 | STHRNCRS_EG
IMB LOAD - WAPL / 1 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 27 | 15.9 | WAPL_WORSLEY
IMB LOAD - WAPL / 2 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 27 | 15.9 | WAPL_WORSLEY
IMB LOAD - WAPL / 3 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 27 | 15.9 | WAPL_WORSLEY
IMB LOAD - WAPL / 4 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 1.6 | 0.9 | WAPL_WORSLEY
IMB LOAD - WAPL / 5 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 71.5 | 42 | WAPL_WORSLEY
IMB LOAD - WAPL / 6 | WAPL - Worsley Alumina Pty Ltd | MU - Muja Load Area | Imbedded | 4.8 | 2.8 | WAPL_WORSLEY
IMB LOAD - WMK | WMK - Western Mining Kambalda | EG - Eastern Goldfields Load Area | Imbedded | 17.8 | 0 | STHRNCRS_EG
|  |  | Total Generation @ IMB_LOAD | 520.2
Facility Code | Total Net Value from IMB_GEN Sites Observed Std.dev_High End_MW @ SYS_MAX (+/-: GEN/LOAD) | MW (as Load) to be considered in RCM
ALCOA_KWI | 1.8 | 0
ALCOA_PNJ | -15.2 | -15.2
ALCOA_WGP | 21.2 | 0
PRK_AG | 10.4886 | 0
STHRNCRS_EG | 22.4 | 0
WAPL_WORSLEY | 14.3958 | 0
| Total MW (as Load) to be considered in RCM | -15.2
Facility Code | Total Net Value from IMB_GEN Sites Observed mean MW @ SYS_MAX (+/-: GEN/LOAD) | MW (as Load) to be considered in RCM
ALCOA_KWI | -1.6342 | -1.6342
ALCOA_PNJ | -32.6421 | -32.6421
ALCOA_WGP | 9.1488 | 0
PRK_AG | -13.1786 | -13.1786
STHRNCRS_EG | 14.1612 | 0
WAPL_WORSLEY | -0.37063 | -0.37063
| Total MW (as Load) to be considered in RCM | -47.8255
Confidential - Not to be published