# 2024 RCM Limit Advice WEM Report Version 1.4 Public 20 September 2024

Western Power

363 Wellington Street

Perth WA 6000

GPO Box L921 Perth WA 6842

Electricity Networks Corporation

ABN 18 540 492 861

WEMLimitAdvice@westernpower.com.au

westernpower.com.au

ELECTRICITY INDUSTRY ACT 2004

ELECTRICITY INDUSTRY

(WHOLESALE ELECTRICITY MARKET)

REGULATIONS 2004

WHOLESALE ELECTRICITY MARKET RULES

Authorisation

|  | Title | Name | Date |
| --- | --- | --- | --- |
| Approver: | Transmission Grid Strategy & Planning Manager | Daniel Cassidy | 20/9/2024 |

Version Release History

| Version | Effective Date | Summary of Changes |
| --- | --- | --- |
| 0 | 11/6/2024 | 2024 RCM Limit Advice – original version |
| 1 | 3/7/24 | Update block loads and respond to updated 2024 RCM EOI info received on 8 Jul 24 |
| 1.1 | 8/8/24 | Uprate MH-PNJ, KEM-PIC/PNJ/BSN & PIC-MRR 132kV lines. New scheme to decouple NOR-CSN-MRT from 220kV system |
| 1.2 | 13/8/24 | Update MU 220kV inter-trip scheme |
| 1.3 | 6/9/24 | Update Block Load #40 |
| 1.4 | 20/9/24 | Add MUL-PBY 81 control scheme. Uprate PNJ-BSN/KEM/PIC 81 and PNJ-CT/MSS 81 |

DISCLAIMER

Western Power provides this Limit Advice and associated information in good faith and in the performance of its functions conferred under rules 4.4B.3 and 4.4B. the Wholesale Electricity Market Rules. Western Power has used reasonable endeavours to ensure that this Limit Advice and information is complete, current and accurate at the time it is provided to AEMO. Western Power is not liable for any acts, errors or omissions, or for any results obtained by any party from the use of this information, generally and in accordance with its statutory immunity under section 126 of the Electricity Industry Act 2004 (WA).”

Contents

Abbreviations	iv

1.	Purpose	1

2.	Provided Information	1

2.1	Estimated SWIS Configuration	1

2.2	Estimated proportion of the peak demand	1

2.3	RCM thermal network limit	2

2.4	RCM non-thermal network limit	2

2.5	Normally open points (NOP) in summer 2027	2

2.6	Facilities subject to NCS or NCESS	3

# Abbreviations

The following table provides a list of abbreviations and acronyms used throughout this document. Defined terms are identified in this document by capitals.

| Term | Definition |
| --- | --- |
| NCESS | Non-Co-optimised Essential System Services |  |
| NCS | Network Control Services |  |
| RCM | Reserve Capacity Mechanism |  |
| SWIS | South West Interconnected System |  |
| WEM | Wholesale Electricity Market |  |

# Purpose

This Limit Advice is to provide AEMO with the requested information in accordance with Western Power’s obligation, as a Network Operator, specified in clauses 4.4B.3 and 4.4B.5 of the WEM Rules.

# Provided Information

All the requested information is in the following sub sections or referenced attachments. The required explanation for changes in the information submitted for this and previous Reserve Capacity Cycles is included in the applicable uploaded files.

## Estimated SWIS Configuration

The estimated configuration of the SWIS during summer 2027 peak, without the recently approved projects and the proposed connection points of the Facilities to be included by AEMO in the 2024 RCM model, is available from the SWIS Base Model 2023V1_4 RCM 2024(22072024), uploaded to the “2024 Capacity Cycle” folder in AEMO’s sharepoint.

The proposed connection points of the Facilities to be included by AEMO in the 2024 RCM model are provided under the “Substation for proposed connection” row in the “4.4B.2.a-EOI details” worksheet of the “2024 RCM – EOI V0 published” spreadsheet uploaded to the “2024 Capacity Cycle” folder in AEMO’s sharepoint.

The special protection/control schemes, including the operation manual intervention processes mentioned in the 2023 RCM Limit Advice, applicable to the RCM constraint equation development, but not limited to, are notified under the “Include in limit & constraint equation” column of the “Existing Special Protection Scheme Register V7.4” file uploaded to the “SWIS Special Protection Schemes” folder in AEMO’s sharepoint.

## Estimated proportion of the peak demand

The estimated proportion of the SWIS peak demand during summer 2027 at each Electrical Location is in the “2024 RCM – peak demand and block loads V1.2 published” file uploaded to the “2024 Capacity Cycle” folder in AEMO’s sharepoint.

Table 2.1 shows information of:

one new load with an estimated peak demand > 10MW; and

existing loads having a change in the estimated peak demand of more than 10MW between summer 2026 and summer 2027.

Table 2.1:	New and existing block loads with estimated peak demand variation > 10MW

| # | Description | Estimated peak demand in 2024 RCM (MW) | Estimated peak demand in 2023 RCM (MW) | New/Existing load | Substation | Forecast in service date |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Block Load 23 | 69.6 | 111 | Existing | KRA (Karara) | N/A |
| 2 | Block Load 32 | 15.0 | 30.9 | Existing | TLA (Tianqi Lithium Australia) | N/A |
| 3 | Block Load 33 | 2.10 | 18.7 | Existing | WSD (Westralian Sands) | N/A |
| 4 | Block Load 42* | 27.1 | - | New | YP (Yanchep) | Jun 2025 |
| 5 | Block Load 43* | 7.5 | - | New | BNL (Bunning Lake) | Jun 2025 |

* denotes recently committed projects.

## RCM thermal network limit

The following information has been included the “2024 RCM thermal ratings V3 published” file uploaded to the “2024 Capacity Cycle” folder in AEMO’s sharepoint:

Thermal ratings of all applicable lines and transformers assuming an ambient temperature of 41 degrees Celsius;

Transmission Network assets scheduled to be commissioned or retired; and

Proposed changes to the SWIS to facilitate the connection of new Facilities notified by in AEMO’s Expression of Interest spreadsheet.

- Note as per the 2023 RCM thermal ratings, the 2024 RCM thermal ratings of overhead lines in the “2024 RCM -thermal ratings V2 published” file are based on the solar irradiance of 300 W/m2.

## RCM non-thermal network limit

If the limit equation “W-LE1^WKT 220/132kV} EGF” in the Limit Advice #1 results in no solution for AEMO’s 2023 NAQ model, it can be excluded as there are other means to manage the transfer when this limit equation is violated in the NAQ model.

## Normally open points (NOP) in summer 2027

Table 2.2 lists out the expected NOP under N-0 system during summer 2027.

Table 2.2: Expected NOP in summer 2027

| # | NOP |
| --- | --- |
| 1 | BEL end of BEL-EP-NT 81 line |
| 2 | PIC end of PIC-PNJ-BSN-KEM 81 line |
| 3 | NGN & NGS ends of NGN-NGS-WAG 71 line |
| 4 | KEL end of CUN-KEL |
| 5 | SX end of YLN-SX |
| 6 | 132kV end of KW BTT1 330/132kV transformer |
| 7 | MIL end of HAY-MIL 81 cable |
| 8 | MLA bus section 804 at MLA 132kV busbar |
| 9 | NT A and B 132kV bus sections non-paralleled by opening the 132kV bus couplers during high fault level periods |
| 11 | 22kV isolator 505.4 at WGP 22kV bus |

In addition to the above NOP, the NBT T2 transformer can be taken out of service daily when required.

## Facilities subject to NCS or NCESS

There are no facilities required to be in service during summer 2027 to provide NCS, NCESS or equivalent service to Western Power.