## Disclaimer
Disclaimer
This transmission outlook workbook contains data provided by or collected from third parties, and conclusions, opinions, assumptions or forecasts that are based on that data. AEMO has made every effort to ensure the quality of the information in this workbook but cannot guarantee that the information and assumptions in it are accurate, complete or appropriate for your circumstances. This workbook does not include all of the information that an investor, participant or potential participant in the electricity or gas market might require, and does not amount to a recommendation of any investment. Anyone proposing to use the information in this workbook should independently verify and check its accuracy, completeness and suitability for purpose, and obtain independent and specific advice from appropriate experts. This dataset or the information in it may be subsequently updated or amended. This work does not constitute legal or business advice, and should not be relied on as a substitute for obtaining detailed legal advice about the National Electricity Law, the National Electricity Rules, or any other applicable laws, procedures or policies. Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants involved in the preparation of this document:
• | make no representation or warranty, express or implied, as to the currency, accuracy, reliability or completeness of the information in this workbook; and
• | are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information or other matters contained in or derived from this publication, or any omissions from it, or in respect of a person’s use of the information in this workbook.

## NSW
New South Wales - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependent on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
QNI Minor | Uprate Liddell–Tamworth 330 kV line Uprate Liddell–Muswellbrook–Tamworth 330 kV line | Increase transfer between Queensland and New South Wales | ✓ | ✓ | ✓ | ✓ | ✓ | 150 (NSW to QLD) 165-215 (QLD to NSW) | Committed
Install 330 kV capacitor banks at Armidale, Dumaresq and Tamworth
Install dynamic reactive plant at Tamworth and Dumaresq
QNI Medium | Single circuit 500 kV from a new substation in NSW Central-West Orana REZ to Boggabri to West of Dumaresq to Bulli Creek to Western Downs (first circuit strung on a double circuit tower). | Increase transfer between Queensland and New South Wales; Increased renewable generation in North West NSW and Darling Downs REZs. (QNI Option 2E - Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 832 (NSW to QLD) 760 (QLD to NSW) 2,000 (Hosting capacity) (Note 1) | 1,481-2,750
New 330 kV single circuit line from Boggabri to Tamworth or future Uralla substation.
New 330 kV single circuit line from West Dumaresq to Dumaresq.
Establishing new 500/330 kV substations at Boggabri site and a new site West of Dumaresq (West Dumaresq).
One 550/330kV 1,500 MVA transformer at Boggabri.
One 500/330 kV 1,500 MVA transformer at west of Dumaresq.
One 500/330 kV 1,500 MVA transformer at Bulli Creek.
One 500/275 kV 1,000 MVA transformer at Western Downs.
New static and dynamic compensation at Boggabri, West Dumaresq, Sapphire, Bulli Creek, and/or Western Downs.
QNI Large | A second 500 kV circuit from a new substation in NSW Central-West Orana REZ to Boggabri to West of Dumaresq to Bulli Creek to Western Downs (second circuit strung on a double circuit tower). | Increase transfer between Queensland and New South Wales; Increased renewable generation in North West NSW and Darling Downs REZs. (QNI Option 3E - Input and Assumptions workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 1,540 (NSW to QLD) 1,370 (QLD to NSW) 2,000 (Hosting capacity) (Note 2) | 802-1,489
Second 500/275 kV 1,000 MVA transformer at Western Downs.
Power flow controllers on Boggabri–Tamworth and West Dumaresq–Dumaresq 330 kV lines (or 330 kV lines between Armidale-Tamworth-Liddell).
Additional static and dynamic compensation at Boggabri, West Dumaresq, Sapphire, Bulli Creek, and/or Western Downs.
VNI minor upgrade | Installation of a new 500/330 kV 1,000 MVA transformer at South Morang | Increase export from VIC to NSW. (VNI Option 1 - Input and Assumptions workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 170 (VIC to NSW) | 74-137
Uprate the South Morang-Dederang 330 kV lines and series capacitor;
Install modular power flow controllers on both the Upper Tumut–Canberra 330 kV line and the Upper Tumut-Yass 330 kV line.
Humelink | Establish a new 500/330 kV substation in the Snowy Area (Maragle) Cut-in Lower Tumut–Upper Tumut 330 kV line into Maragle 3x500/330 1,500 MVA transformers | Increased renewable generation in Southern NSW Tablelands and Wagga Wagga REZs / Snowy 2.0 | ✓ | ✓ | ✓ | ✓ | ✓ | 2,230 - 2,570 1,000 (Hosting capacity) (Note 3) | 1,470-2,730
1x500 kV line between Maragle and Bannaby 1x500 kV line between Wagga and Bannaby 1x500 kV line between Maragle and Wagga Wagga
Establish 500 kV substation at Wagga Wagga 2x500/330 kV 1500 MVA transformers at Wagga Wagga
VNI West | VNI Option 6: 2x500 kV lines from north of Ballarat to Shepparton to Wagga Wagga; 2x500/220 kV 1000 MVA transformers at Shepparton. Power flow controllers on Murray–Lower Tumut, Murray–Upper Tumut and Wodonga–Jindera 330 kV lines. Additional reactive plant at a new terminal station at north of Ballarat, Shepparton, and Wagga Wagga. | Increase transfers between Victoria and New South Wales; Increased renewable generation in Western Victoria and Central North Victoria. (VNI Option 6 - Input and Assumptions workbook) | ✓ | ✓ | ✓ | X | X | 1,930 (VIC to NSW) 1,800 (NSW to VIC) 3,000 (Hosting capacity) (Note 4) | 1,211-2,249
| VNI Option 7 (an alternative to VNI Option 6): 2x500 kV lines from north of Ballarat to Bendigo to Kerang to Dinawan to Wagga Wagga; 2x500/220 kV 1000 MVA transformers at Bendigo. 2x500/220 kV 1000 MVA transformers at Kerang 2x500/330 kV 1500 MVA transformers at Dinawan Power flow controllers on Murray–Lower Tumut, Murray–Upper Tumut and Wodonga–Jindera 330 kV lines. Additional reactive plant at Bendigo, Kerang, Dinawan and Wagga Wagga. | Increase transfers between Victoria and New South Wales; Increased renewable generation in Murray, Western Victoria and South West New South Wales REZs. (VNI Option 7 - Input and Assumptions workbook) | ✓ | ✓ | ✓ | X | X | 1,930 (VIC to NSW) 1,800 (NSW to VIC) 4,000 (Hosting capacity) (Note 5) | 1,687-3,133
Project EnergyConnect | A new 275 kV double circuit line between Robertstown and Bundey | Increase transfers between South Australia and New South Wales. Increased renewable generation in Riverland, South West NSW and Murray River (EnergyConnect - Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 800 (NSW to SA) 800 (SA to NSW) 1,780 (Hosting capacity) (Note 6) | 1,393-2,587
A new Bundey–Buronga–Dinawan–Wagga Wagga 330 kV double circuit line.
A new double circuit 220 kV line between Buronga and Red Cliffs to replace the existing 220 kV single circuit line.
New 3 x 275/330 kV transformers at Bundey.
New 330 kV phase shift transformers at Buronga.
New 330/220 kV transformers at Buronga.
New 330 kV substations at Bundey and Dinawan.
Augmentation of existing substations at Robertstown, Buronga, Wagga Wagga and Red Cliffs.
Turn in the existing Robertstown–Para 275 kV line into Tungkillo.
Static and dynamic reactive plant at Bundey, Buronga, and Dinawan substations.
A special protection scheme to detect and manage loss of either interconnection of Victoria – South Australia or New South Wales – South Australia.
Northern West NSW | Two 500/330 kV 1,500 MVA transformers at Boggabri | Increase in generation in North West NSW | ✓ | ✓ | ✓ | ✓ | x | (Note 7) | 70-140
| One 500/300 kV transformers at West of Dumaresq |  | ✓ | ✓ | ✓ | ✓ | x
| Establish a new Uralla 500/330 kV substation | Increase in generation in New England | ✓ | ✓ | ✓ | ✓ | x | 5,000-6,000 (Hosting capacity) | 940-1,750
| Turn both Armidale–Tamworth 330 kV lines 85 and 86 into Uralla |  | ✓ | ✓ | ✓ | ✓ | x
| Uprate Armidale–Uralla–Tamworth 330 kV lines |  | ✓ | ✓ | ✓ | ✓ | x
| A new double circuit Uralla–Bayswater 500 kV line |  | ✓ | ✓ | ✓ | ✓ | x
| Two 500/330 kV 1,500 MVA Uralla transformers |  | ✓ | ✓ | ✓ | ✓ | x
| One 500/330 kV 1,500 MVA Bayswater transformer | Increased in renewable generation in North West NSW and New England | ✓ | ✓ | ✓ | ✓ | x
| A new Walcha 500/330 kV Substation, turn Bayswater–Uralla into Walcha (dependent on connection interest in the area). | Increased in renewable generation in New England | ✓ | ✓ | ✓ | ✓ | x
| Two 500/330 kV 1,500 MVA Walcha transformers |  | ✓ | ✓ | ✓ | ✓ | x
| A new single circuit Uralla–Boggabri 500 kV line | Increased in renewable generation in North West NSW and New England | ✓ | ✓ | ✓ | ✓ | x
| Additional reactive support |  | ✓ | ✓ | ✓ | ✓ | x
Central NSW | A 500 kV (or 330kV) loop which traverses the Central-West Orana REZ (Note 8) | Increased in renewable generation in Central-West Orana REZ | ✓ | ✓ (Note 9) | ✓ | ✓ | ✓ | 3000 (Hosting capacity) | 450-850
| Uprating of a number of 330 kV overload lines between Marulan and Liddell. | Coal retirement within NSW (timing is indicative). The sequence of works and the timing is highly influenced load distribution, battery storage locations, and potential line upratings within Sydney/Wollongong/Newcastle load centre | ✓ | ✓ | ✓ | ✓ | ✓ | 5,000-6,000 (Hosting capacity) | NA
| Two 500 kV lines from Bannaby to South Creek (closer to Sydney West). |  | ✓ | ✓ | ✓ | ✓ | ✓
| A new 500/330 kV substation at South Creek. |  | ✓ | ✓ | ✓ | ✓ | ✓
| Tap both Eraring–Kemps Creek 500 kV lines at South Creek. |  | ✓ | ✓ | ✓ | ✓ | ✓
| Two 500/330 kV 1,500 MVA transformers at South Creek. |  | ✓ | ✓ | ✓ | ✓ | ✓
| One 500/330 kV 1,500 MVA transformer at Bannaby. |  | ✓ | ✓ | ✓ | ✓ | ✓
| A new 330 kV transmission line from South Creek to Sydney West (8 km). |  | ✓ | ✓ | ✓ | ✓ | ✓
| Tap Sydney West–Bayswater 330 kV line at South Creek. |  | ✓ | ✓ | ✓ | ✓ | ✓
| Tap Sydney West–Regentville 330 kV line at South Creek. |  | ✓ | ✓ | ✓ | ✓ | ✓
| Third Mt Piper–Wallerawang 330 kV line. |  | ✓ | ✓ | ✓ | ✓ | ✓
| Third Bayswater–Liddell 330 kV line. |  | ✓ | ✓ | ✓ | ✓ | ✓
| Two 500 kV lines from Bayswater to Eraring. |  | ✓ | ✓ | ✓ | ✓ | ✓
Note 1 | Increase in transfer is in addition to QNI Minor. Network capacity for additional generation is ~1,000 MW in Queensland and ~1,000 MW in New South Wales
Note 2 | Increase in transfer is in addition to QNI Minor and QNI Medium. Network capacity for additional generation additional to QNI 2E ~1,000 MW in Queensland and ~1,000 MW in New South Wales
Note 3 | Increase in REZ by 1,000 MW within the Wagga Wagga REZ. Increase for Snowy 2.0 of 2,040 MW
Note 4 | Network capacity for additional generation ~3,000 MW in Victoria
Note 5 | Network capacity for additional generation ~4,000 MW of which ~1,000 MW is in NSW within South West NSW
Note 6 | Project EnergyConnect allows for additional generation of 1,780 MW - Including Riverland, Murray River and South West NSW REZs.
Note 7 | This augmentation, together with QNI Medium and Large and the line Uralla - Boggabri 500 kV line allows for 3,000 MW of generation in North West New South Wales
Note 8 | Augmentation details for Central-West Orana is to be developed as part of the RIT-T.
Note 9 | In the Step change scenario, additional transmission network will be required from 2036.
Hosting capacity | Hosting capacity is the approximate amount of additional generation (MW) that can be transported from a REZ to the load centre considering network limitations.

## QLD
Queensland - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependent on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
QNI Minor | Uprate Liddell–Tamworth 330 kV line Uprate Liddell–Muswellbrook–Tamworth 330 kV line | Increase transfer between Queensland and New South Wales | ✓ | ✓ | ✓ | ✓ | ✓ | 150 (NSW to QLD) 165-215 (QLD to NSW) | Committed
Install 330 kV capacitor banks at Armidale, Dumaresq and Tamworth
Install dynamic reactive plant at Tamworth and Dumaresq
QNI Medium | Single circuit 500 kV from a new substation in NSW Central-West Orana REZ to Boggabri to West of Dumaresq to Bulli Creek to Western Downs (first circuit strung on a double circuit tower). | Increase transfer between Queensland and New South Wales; Increased renewable generation in North West NSW and Darling Downs REZs. (QNI Option 2E - Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 832 (NSW to QLD) 760 (QLD to NSW) 2,000 (Hosting capacity) (Note 1) | 1,481-2,750
New 330 kV single circuit line from Boggabri to Tamworth or future Uralla substation.
New 330 kV single circuit line from West Dumaresq to Dumaresq.
Establishing new 500/330 kV substations at Boggabri site and a new site West of Dumaresq (West Dumaresq).
One 550/330kV 1,500 MVA transformer at Boggabri.
One 500/330 kV 1,500 MVA transformer at west of Dumaresq.
One 500/330 kV 1,500 MVA transformer at Bulli Creek.
One 500/275 kV 1,000 MVA transformer at Western Downs.
New static and dynamic compensation at Boggabri, West Dumaresq, Sapphire, Bulli Creek, and/or Western Downs.
QNI Large | A second 500 kV circuit from a new substation in NSW Central-West Orana REZ to Boggabri to West of Dumaresq to Bulli Creek to Western Downs (second circuit strung on a double circuit tower). | Increase transfer between Queensland and New South Wales; Increased renewable generation in North West NSW and Darling Downs REZs. (QNI Option 3E - Input and Assumptions workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 1540 (NSW to QLD) 1,370 (QLD to NSW) 2,000 (Hosting capacity) (Note 2) | 802-1,489
Second 500/275 kV 1,000 MVA transformer at Western Downs.
Power flow controllers on Boggabri–Tamworth and West Dumaresq–Dumaresq 330 kV lines (or 330 kV lines between Armidale–Tamworth–Liddell).
Additional static and dynamic compensation at Boggabri, West Dumaresq, Sapphire, Bulli Creek, and/or Western Downs.
Far North Queensland | Rebuild the Ross–Chalumbin 275 kV double-circuit line at a higher capacity. (Note 3) | Increased in wind generation in Far North Queensland Assets renewal - timing could be brought forward and capacity increased | ✓ | ✓ | ✓ | ✓ | x | 1,300-1,800 (Hosting capacity) | 400-740
| Build an additional single-circuit Ross–Chalumbin 275 kV line | Increased in wind generation in Far North Queensland | ✓ | x | ✓ | ✓ | x |  | 280-530
| Increase rating on lower rated Ross–Strathmore 275 kV line |  | ✓ | ✓ | ✓ | ✓ | x |  | 10-15
| Build a new double-circuit Ross-Chalumbin 275 kV line |  | x | ✓ | x | x | x |  | 400-740
| Build an additional single-circuit Ross–Strathmore–Nebo 275 kV line |  | x | ✓ | x | x | x |  | 350-670
| A new single-circuit from Chalumbin–Walkamin–Lakeland |  | • | • | • | • | x |  | 300-570
| A new Chalumbin–Millstream 275 kV double/single-circuit line, turn Chalumbin–Woree 275 kV line into Millstream |  | • | • | • | • | x |  | 90-160
North Queensland | Build Nebo-Bouldercombe 275 kV line | Increase in generation in Far North Queensland and Isaac | x | ✓ | ✓ | ✓ | x | 700-800 (Hosting capacity) | 320-600
Gladstone Grid section | A new double-circuit Calvale-Larcom Creek 275 kV line | Retirement of Gladstone generation and increased renewable generation in Northern QLD | ✓ | ✓ | ✓ | ✓ | ✓ | 700-800 (Hosting capacity) | 300-560
| An additional 275/132 kV transformer at Calliope River (third) |  | ✓ | ✓ | ✓ | ✓ | ✓
| Rebuild the Bouldercombe–Calliope River 275 kV line as Bouldercombe–Larcom Creek–Calliope River 275 kV line with high thermal capacity | Asset renewal, Gladstone retirement and increase in high VRE in Northern QLD Timing could be brought forward with retirement of Gladstone generation. | ✓ | ✓ | ✓ | ✓ | ✓
| Build an additional single-circuit Bouldercombe–Calliope River 275 kV line | Increased renewable generation in Northern QLD | ✓ | ✓ | ✓ | ✓ | x | 1,000 (Hosting capacity) | 130-240
Central to Southern Queensland | A new double-circuit Calvale–Wandoan South 275 kV line | Increased in renewable generation in Central and Northern Queensland | ✓ | ✓ | ✓ | ✓ | x | 900 (Central to Southern QLD) | 300-560
Note 1 | Increase in transfer is in addition to QNI minor. Network capacity for additional generation is ~1,000 MW in Queensland and ~1,000 MW in New South Wales.
Note 2 | Increase in transfer is in addition to QNI minor and QNI medium. Network capacity for additional generation additional to QNI 2E ~1,000 MW in Queensland and ~1,000 MW in New South Wales.
Note 3 | In some scenarios, this is timed with the asset replacement around mid to late 2030s
Hosting capacity | Hosting capacity is the approximate amount of additional generation (MW) that can be transported from a REZ to the load centre considering network limitations.

## SA
South Australia - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependent on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
Project EnergyConnect | A new 275 kV double circuit line between Robertstown and Bundey | Increase transfers between South Australia and New South Wales. Increased renewable generation in Riverland, South West NSW and Murray River (EnergyConnect - Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | ✓ | 800 (NSW to SA) / 800 (SA to NSW) (Note 1) 1,780 (Hosting capacity) (Note 2) | 1,393-2,587
A new Bundey–Buronga–Dinawan–Wagga Wagga 330 kV double circuit line.
A new double circuit 220 kV line between Buronga and Red Cliffs to replace the existing 220 kV single circuit line.
New 3 x 275/330 kV transformers at Bundey.
New 330 kV phase shift transformers at Buronga†.
New 330/220 kV transformers at Buronga†.
New 330 kV substations at Bundey and Dinawan.
Augmentation of existing substations at Robertstown, Buronga, Wagga Wagga and Red Cliffs.
Turn in the existing Robertstown–Para 275 kV line into Tungkillo.
Static and dynamic reactive plant at Bundey, Buronga, and Dinawan substations.
A special protection scheme to detect and manage loss of either interconnection of Victoria – South Australia or New South Wales – South Australia.
Mid North SA | Rebuild of Davenport–Brinkworth–Templers West–Para 275 kV line | Increased renewable generation. Timing is also influenced by the retirement of gas generation within South Australia | ✓ | ✓ | ✓ | x | x | 1000 (Hosting capacity) | 420-770
South East SA | String vacant circuit between Tailem Bend and Tungkillo Install reactive compensation. Where necessary manage generation with control schemes such as runback schemes (Note 3) | Increased renewable generation with South East South Australia | ✓ | ✓ | ✓ | ✓ | x | 400-600 (Hosting capacity) (Note 4) | 20-80
Eyre Peninsula | A double circuit Cultana–Yadnarie 275 kV line energised at 132 kV A double circuit Yadnarie–Port Lincoln 132 kV line | Pending approval by AER - End of life replacements and improved reliability of supply. | ✓ | ✓ | ✓ | ✓ | ✓ | 470 (Hosting capacity) | 240 (Note 5)
Note 1 | For more information on Project EnergyConnect interconnector limits, including combined limits, refer to the 2020 Input and Assumptions workbook.
Note 2 | Project EnergyConnect allows for additional generation of 1,780 MW - Including Riverland, Murray River and South West NSW REZs.
Note 3 | Additional transmission infrastructure may be required depending on the location of generation within this REZ
Note 4 | Control schemes such as runback schemes can further increase capacity.
Note 5 | Cost estimates aligned with Eyre Peninsula Electricity Supply Options PACR.
Hosting capacity | Hosting capacity is the approximate amount of additional generation (MW) that can be transported from a REZ to the load centre considering network limitations.

## TAS
Tasmania - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependent on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
Marinus Link | 1x750 MW HVDC interconnectors between Burnie area in Tasmania and Latrobe Valley in Victoria | Marinus Link 1x750 MW (VIC-TAS option 3 in Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | x | 750 (TAS to VIC) 500-750 (VIC to TAS) 540 (Hosting capacity) (Note 1) | 1,292-2,399
A new 220 kV switching station in the Burnie area adjacent to the converter station.
A new double-circuit 220 kV transmission line from Burnie to Sheffield.
A 220 kV double circuit line from Sheffield to Palmerston.
A 500 kV connection asset for connection of the converter station in the Hazelwood area to the Hazelwood 500 kV terminal station.
| 2x750 MW HVDC interconnectors between Burnie area in Tasmania and Latrobe Valley in Victoria | Marinus Link 2x750 MW (VIC-TAS option 4 in Input and Assumptions Workbook) | ✓ | ✓ | X | ✓ | X | 1,500 (TAS to VIC) 1,250-1,500 (VIC to TAS) 1,140 (Hosting capacity) (Note 2) | 2,209-4,102
A new 220 kV switching station in the Burnie area adjacent to the converter station.
A new double-circuit 220 kV transmission line from Burnie to Sheffield.
A new 220 kV double circuit line from Hampshire to Burnie.
A new 220 kV double circuit line from Hampshire to Staverton.
220 kV switching station at Staverton.
Cut-in two Sheffield-Mersey Forth double circuit 220 kV lines at Staverton.
A 220 kV double circuit line from Sheffield to Palmerston.
A 500 kV connection asset for connection of the converter station in the Hazelwood area to the Hazelwood 500 kV terminal station.
Note 1 | Network capacity for additional generation is ~540 MW.
Note 2 | Network capacity for additional generation within REZs in Tasmania is ~1,140 MW.
Hosting capacity | Hosting capacity is the approximate amount of additional generation (MW) that can be transported from a REZ to the load centre considering network limitations.

## VIC
Victoria - Projected transmission network requirements |  |  |  | 2020-2030 |  | ✓ | Required
|  |  |  | 2030-2035 |  | X | Not required
|  |  |  | 2035-2042 |  | • | May be required dependent on location of resource
Transmission Upgrade / Zone | Network Augmentation | Driver for augmentation | Central | Step | Fast | High DER | Slow | Additional Capacity (MW) | Indicative cost ($ million)
VNI minor upgrade | Installation of a new 500/330 kV 1,000 MVA transformer at South Morang | Increase export from VIC to NSW. (VNI Option 1 - Input and Assumptions workbook)) | ✓ | ✓ | ✓ | ✓ | ✓ | 170 (VIC to NSW) | 74-137
Uprate the South Morang-Dederang 330 kV lines and series capacitor;
Install modular power flow controllers on both the Upper Tumut-Canberra 300 kV line and the Upper Tumut-Yass 330 kV line.
VNI West | VNI Option 6: 2x500 kV lines from north of Ballarat to Shepparton to Wagga Wagga; 2x500/220 kV 1000 MVA transformers at Shepparton. Power flow controllers on Murray–Lower Tumut, Murray–Upper Tumut and Wodonga–Jindera 330 kV lines. Additional reactive plant at a new terminal station at north of Ballarat, Shepparton, and Wagga Wagga. | Increase transfers between Victoria and New South Wales; Increased renewable generation in Western Victoria and Central North Victoria. (VNI Option 6 - Input and Assumptions workbook) | ✓ | ✓ | ✓ | X | X | 1,930 (VIC to NSW) 1,800 (NSW to VIC) 3,000 (Hosting capacity) (Note 1) | 1,211-2,249
| VNI Option 7 (an alternative to VNI Option 6): 2x500 kV lines from north of Ballarat to Bendigo to Kerang to Dinawan to Wagga Wagga; 2x500/220 kV 1000 MVA transformers at Bendigo. 2x500/220 kV 1000 MVA transformers at Kerang 2x500/330 kV 1500 MVA transformers at Dinawan Power flow controllers on Murray–Lower Tumut, Murray–Upper Tumut and Wodonga–Jindera 330 kV lines. Additional reactive plant at Bendigo, Kerang, Dinawan and Wagga Wagga. | Increase transfers between Victoria and New South Wales; Increased renewable generation in Murray, Western Victoria and South West New South Wales REZs. (VNI Option 7 - Input and Assumptions workbook) | ✓ | ✓ | ✓ | X | X | 1,930 (VIC to NSW) 1,800 (NSW to VIC) 4,000 (Hosting capacity) (Note 2) | 1,687-3,133
Marinus Link | 1x750 MW HVDC interconnectors between Burnie area in Tasmania and Latrobe Valley in Victoria | Marinus Link 1x750 MW (VIC-TAS option 3 in Input and Assumptions Workbook) | ✓ | ✓ | ✓ | ✓ | x | 750 (TAS to VIC) 500-750 (VIC to TAS) 540 (Hosting capacity) (Note 3) | 1,292-2,399
A new 220 kV switching station in the Burnie area adjacent to the converter station.
A new double-circuit 220 kV transmission line from Burnie to Sheffield.
A 220 kV double circuit line from Sheffield to Palmerston.
A 500 kV connection asset for connection of the converter station in the Hazelwood area to the Hazelwood 500 kV terminal station.
| 2x750 MW HVDC interconnectors between Burnie area in Tasmania and Latrobe Valley in Victoria | Marinus Link 2x750 MW (VIC-TAS option 4 in Input and Assumptions Workbook) | ✓ | ✓ | X | ✓ | X | 1,500 (TAS to VIC) 1,250-1,500 (VIC to TAS) 1,140 (Hosting capacity) (Note 4) | 2,209-4,102
A new 220 kV switching station in the Burnie area adjacent to the converter station.
A new double-circuit 220 kV transmission line from Burnie to Sheffield.
A new 220 kV double circuit line from Hampshire to Burnie.
A new 220 kV double circuit line from Hampshire to Staverton.
220 kV switching station at Staverton.
Cut-in two Sheffield-Mersey Forth double circuit 220 kV lines at Staverton.
A 220 kV double circuit line from Sheffield to Palmerston.
A 500 kV connection asset for connection of the converter station in the Hazelwood area to the Hazelwood 500 kV terminal station.
Central VIC | Installation of wind monitoring equipment and the upgrade of station limiting transmission plant on: - Red Cliffs–Wemen 220 kV line - Wemen–Kerang 220 kV line - Kerang–Bendigo 220 kV line - Moorabool–Terang 220 kV line - Ballarat–Terang 220 kV line | Increased renewable generation in Western Victoria and Murray REZ | ✓ | ✓ | ✓ | ✓ | ✓ | 450 (Hosting capacity) (Note 6) | Committed
| A new substation north of Ballarat |  | ✓ | ✓ | ✓ | ✓ | ✓ |  | Committed
A new 500 kV double-circuit transmission line from Sydenham to the new substation north of Ballarat
2 x 500/220 kV transformers at the new substation north of Ballarat
Cut-in the existing Ballarat–Bendigo 220 kV line at a new substation north of Ballarat
Moving the Waubra Terminal Station connection from the existing Ballarat–Ararat 220 kV line to one of the new substation north of Ballarat–Bulgana 220 kV lines
Moving the Waubra Terminal Station connection from the existing Ballarat–Ararat 220 kV line to one of the new substation north of Ballarat–Bulgana 220 kV lines
South West Victoria | Turn Tyron-Hunter Gully 500 kV line into Mortlake. Build an additional Mortlake-North Ballarat 500 kV line | Increased renewable generation in South West Victoria | x | ✓ | x | x | x | 2,750 (Hosting capacity) | 270-510
Note 1 | Network capacity for additional generation ~3,000 MW in Victoria. Additional generation of 2,000 MW for Shepparton REZ, 1,000 MW for Western Victoria REZ.
Note 2 | Network capacity for additional generation ~4,000 MW of which ~3,000 MW is in Victoria. Additional generation of 2,000 MW for Murray REZ and 1,000 MW for Western Victoria REZ.
Note 3 | Network capacity for additional generation is ~540 MW.
Note 4 | Network capacity for additional generation within REZs in Tasmania is ~1140 MW.
Note 5 | Mainly switching reconfiguration of the existing assets.
Note 6 | In addition to the existing and committed generation as of April 2020.
Hosting capacity | Hosting capacity is the approximate amount of additional generation (MW) that can be transported from a REZ to the load centre considering network limitations.