## Disclaimer
Disclaimer
The 2024 ISP Assumptions Workbook contains data provided by or collected from third parties,
and conclusions, opinions, assumptions or forecasts that are based on that data.
AEMO has made reasonable efforts to ensure the quality of the information in this publication but cannot
guarantee that information, forecasts and assumptions are accurate, complete or appropriate for your
circumstances.
Modelling work performed as part of preparing this publication inherently requires assumptions about future
behaviours and market interactions, which may result in forecasts that deviate from future conditions. There
will usually be differences between estimated and actual results, because events and circumstances
frequently do not occur as expected, and those differences may be material.
This publication does not include all of the information that an investor, participant or potential participant in
the National Electricity Market might require, and does not amount to a recommendation of any investment.
Anyone proposing to use the information in this publication (which includes information and forecasts from
third parties) should independently verify its accuracy, completeness and suitability for purpose, and obtain
independent and specific advice from appropriate experts.
Accordingly, to the maximum extent permitted by law, AEMO and its officers, employees and consultants
involved in the preparation of this publication:
• make no representation or warranty, express or implied, as to the currency, accuracy, reliability or
completeness of the information in this publication; and
• are not liable (whether by reason of negligence or otherwise) for any statements, opinions, information
or other matters contained in or derived from this publication, or any omissions from it, or in respect of
a person’s use of the information in this publication.

## Change Log
Version History
Version Number | Date | Description
1 | 2019-02-05 | First industry release of draft 2019 market modelling assumptions for consultation.
1.1 | 2019-08-16 | Scenarios tab updated with final 2019-20 modelling scenarios settings
Existing and committed generator lists reflect the 8th August release of Generation Information.
Minimum stable levels and capacity constraints have been updated in the "Generation limits" sheet
Forced outage rates have been updated consistent with the ESOO 2019.
Coal prices have been updated to reflect Wood Mackenzie's final 2019 forecast for AEMO.
Updated closure dates to those submitted by generators in the 8th August release of Generation Information
Fixed O&M cost for existing OCGT's has been changed to correct an error in previous version.
Offshore Wind has been included as a build candidate in the Gippsland REZ.
Included Snowy 2.0 and Battery of the Nation in the "Storage properties" sheet.
Demand forecasting components reflect DRAFT 2019 forecasts. Final forecasts will be available from http://forecasting.aemo.com.au upon publication of the ESOO.
Corrected Pumped Hydro connection costs, as these costs are included in the build costs.
Capacity factors are now available for all available reference years.
WACC updated following consultation feedback.
Charge and Discharge efficiency has been added to the "Storage properties" sheet
Economic and Technical life of Pumped Hydro and Batteries have been corrected after being mislabelled in the previous version
Summary sheets have been added for Demand, Existing Generator Data, New Entrant data, Fuel Prices and Regional Build costs
Technology specific regional cost factors have been included
Hydro inflows and hydro inflow factors added
The following candidate Renewable Energy Zones have been added: • Wide Bay (QLD) • Wagga Wagga (NSW) • Central North Vic (VIC) The following modifications have occurred: The former Northern New South Wales Tablelands and New England REZs have been joined and redrawn • The former Central New South Wales Tablelands and Central West New South Wales REZs have been joined and redrawn • The former Murray River REZ was split into two separate zones and redrawn • The Gippsland REZ in Victoria was expanded to include off-shore wind capability. • The former Moyne REZ was expanded to include a greater area of South West Victoria. • Tasmanian REZs were refined to focus on areas with observed generator connection interest.
The Interconnector capability has been changed to reflect operational and planning updates.
Interconnector augmentation options have been updated to reflect best information from TNSPs and AEMO.
Generator operating limits and behaviours have been updated to reflect latest data and technical information.
Resource limits have been revised to reflect updated methodology. See section 5.4.2 in 2019 Planning and Forecasting Consultation responses on Scenarios, Inputs, Assumptions and Methodology.
REZ expansion costs, Network Capacity, and Additional Network Capacity with IC augmentations have been updated following additional work to refine expansion options for specific REZ, and in consultation with stakeholders.
Shadow generators for committed and candidate generators have been updated based on review and new options (given new generation has been commissioned).
1.2 | 2019-09-13 | Labels have been updated to $/kW for all technologies in the Build Cost sheet to reflect reported values.
Mount Emerald Wind farm was incorrectly listed as a NSW generator in the 'Summary Mapping' sheet, this has been corrected to QLD.
VIC to NSW forward direction was incorrectly labelled as VIC to SA forward direction. Note 4 in 'Augmentation options' sheet has been corrected.
AC network expansion of VIC-TAS Second IC Option 1 and 2 in 'Augmentation options' sheet has been clarified.
Corrected MLF shadow connection point for Cattle Hill and North West Tas Solar and Wind Candidates
Updated Seasonal Ratings to reflect August release of Generation information for Murra Warra Wind Farm – stage 1 and Lincoln Gap Wind Farm – stage 1
Updated Max Capacity to reflect August release of Generation information for Bogong / Mackay, Trevallyn, Oakey Power Station, Berrybank Wind Farm, Capital Wind Farm, Lake Bonney 1 Wind Farm, Starfish Hill Wind Farm, Wattle Point Wind Farm, Challicum Hills Wind Farm, Mortons Lane Wind Farm, Mt Gellibrand Wind Farm, Portland Wind Farm, Yaloak South Wind Farm and Gannawarra Energy Storage System.
A note has been added to the "Existing Gen Data Summary" that the expected retirement date in this summary sheet is indicative of the first unit's retirement date.
Additional VIC-TAS options included in Augmentation Options work sheet. Split VIC-NSW augmentation options to consider HumeLink separately, and removal of option 11. Correction of typo in Note 4 in Augmentation Options work sheet. Updated proportioning factors work sheet including revision to interconnector augmentation options. Included new interconnector options in build limits information.
The New South Wales government has advised AEMO that development in the Southern NSW Tablelands (N4) REZ is to be precluded due to poor community support and high quality agricultural land. As advised, development in other areas of New South Wales would be more conducive to substantive development of renewables.
Updates to the 'Build Limits' sheet to reflect revised HumeLink and VNI augmentation approach.
Updated Millmerran unit MPP_1 Minimum stable level value in the 'Generation Limits' sheet.
Hydro climate factors updated to present specific factor trajectory for Tasmania
Added note to; Augmentation Options, Firm Capacity, Max Capacity, Seasonal Ratings sheets - "With the introduction of MarinusLink, the capacities of the following generators increase by: 100 MW across the west coast, 130 MW for Tarraleah and 90 MW capacity for Gordon."
Note added to Seasonal Rating: "Tamar Valley CCGT seasonal rating is based on being in a mothballed state. This unit can be recalled and may be explored in sensitivity analysis."
Updated calculation for PV uptake percentage for Demand Input Summary sheet.
Revised shadow MLF from Regional Reference Node to 1.0 for a number of projects.
Maximum demand has been updated to align PV generation with battery charging. Also, LIL in South Australia has increased.
Revised Electric Vehicle proportioning factors due to rounding errors.
Updated Tamer Valley CCGT FOM based on stakeholder feedback
Revised retirement and refurbishment dates for CS Power Stations based on stakeholder feedback.
Hydro Inflows update to capture historical observations for the Snowy scheme.
1.3 | 2019-12-12 | Waubra and Yambuk wind farm retirement dates corrected to capture 30 year technical life based on generic wind farm parameters.
Heat rate sheet updated to include "sent-out" note.
Added additional interconnector options QNI 2E and QNI 3E on Augmentation options and Proportioning factors
Revision of QNI Option 3D - Wollar used in place of Bayswater
Revision of VIC-NSW Option 5A - additional South Morang Transformer and cut in of Rowville-Thomastown 220 kV at South Morang, and change to Indicative Cost.
Revision of VIC-NSW Option 6 - location of powerflow controllers updated
Revision of VIC-NSW Option 7 - location of powerflow controllers updated
Revision of VIC-NSW Option 8 - location of powerflow controllers updated
Revision of VIC-NSW Option 11
Update of Build Limits Tab to reflect new IC options QNI 2E and 3E, update on EnergyConnect's impact on Riverland REZ
Update of Build Limits Tab to reflect group constraints for QLD
Update of Build Limits Tab to reflect additional capacity in V2 provided by VNI Option 8
Update to Electric Vehicles sheet to include % of fleet values for Residential, Vehicle to Home
Update to cost estimates to reflect latest advice from TNSPs on Augmentation options tab
Update of Energy Consumption tab for Operational Consumption as Sent-Out and Underlying Consumption.
1.4 | 2020-04-17 | Proportioning Factors tab: Update loss proportioning factors to include upgrade option QNI 2E.
Build Limits tab: Reduced cost/MW as a result of committed project for S8 (Eastern Eyre Peninsula)
Build Limits tab: Changed the Cost/MW for S6 and S7 (Leigh Creek) as a result of group constraint for S3 (Mid North SA) as well as dual pole changed to tower
Build Limits tab: Moved 500 MW capacity from Southern NSW tablelands to Wagga Wagga for HumeLink
Build Limits tab: Updated Riverland REZ from 1000 MW capacity gain for SA-NSW interconnector to 800 MW.
Build Limits tab: Solar resource capacity for V2 was increased as previously was not reflective of true interest in the area
Build Limits tab: Updated QLD REZ build limits to reflect calculation done in the MM
Build Limits tab: Updated Q1 cost/MW to remove small build uprate Woree 132 kV network to 275 kV network, as no longer considered feasible by Powerlink
Build Limits tab: Update N4 to have no cost/MW associated as no extra generation is allowed in the zone
Build Limits tab: Updated costing for TAS Midlands and North West - updated REZ capacity increase for MarinusLink for these two REZ zones too as per advice received from TasNetworks
Build Limits tab: Western Eyre, Eastern Eyre, Mid-North and Northern SA cost/MW changed to reflect costing for towers not dual pole
Build Limits tab: Yorke Peninsula cost/MW increased
Build Limits tab: South West Victoria cost/MW increased to accommodate 500 kV line from Moorabool to Sydenham
Build Limits tab: Central West transmission build limit decreased from 700 MW to 500 MW to account for newly committed generation
Build Limits tab: Mid North SA PV resource limit increased to 1300 MW to reflect updated generation information
Build Limits tab: Increase Central West Build Limit to 3000 MW to incorporate the NSW state government policy
Augmentation options tab: Increase transmission cost and REZ build costs
Augmentation options tab: Marinus Link cost estimate updated as per TasNetworks' advice on 28/02/2020.
Augmentation options tab: QNI options 2E, 3E and 3D limits changed.
Augmentation options tab: VNI Option 11 HVDC limits and cost estimates updated.
Update to Generation Information based on the 26th February release of Generation Information: •Added new Committed Projects (Goonumbla Solar Farm, Crudine Ridge Wind Farm, Gangarri Solar Farm, Lake Bonney BESS1) •Added Anticipated Projects (Berrybank Wind Farm - Stage 2, Murra Warra Wind Farm - Stage 2, Broadsound Solar Farm, Cape York Battery Power Plant - Storage, Cape York Battery Power Plant - Solar, Collector, Gunnedah Solar Farm, Metz Solar Farm, Suntop Solar Farm) •Update to Commission Dates and Installed Capacity of Committed Projects •Update to Expected Closure Dates •Update to Seasonal ratings •Update of Site Names
Renewable Policy Targets tab: Added TRET and edited VRET to apply to all scenarios
Scenarios policy tab: Added TRET and edited VRET to apply to all scenarios
Build Costs tab: updated to be based on draft CSIRO GenCost 2019-20
Renewable Energy Zones tab: V6 cost increased from medium to high based on consultation feedback
Generation Limits tab: Edited description following consultation feedback
Augmentation options tab: QNI Minor (Option 1A) now committed, removed alternative QNI Minor options from workbook.
Augmentation options tab: Update interconnector options for QNI 2E/3E/3D to reflect a terminal station at Boggabri rather than Gunnedah/Narrabri.
Augmentation options tab: Update to Option 3D and 2E on Augmentation tab: removed cut-in for second Bayswater-Mt Piper 500 kV line at Wollar (this is no longer included in QNI augmentation cost).
Augmentation options tab: VNI-NSW Option 11 (HVDC option between Victoria and New South Wales) included.
Augmentation options tab: Updated earliest service date for augmentation options to reflect latest into from TNSPs and potential for expedited processes in some scenarios. Estimates for inter-network testing have been incorporated into the timing (network capacity may be released in stages).
Augmentation options tab: Removed HVDC alternative for HumeLink to reflect latest outcomes from the RIT-T.
Max capacity and related tabs: Added MacIntyre Wind Farm to Anticipated projects
1.5 | 2020-07-30 | Build Limits tab: Changed footnote on Pumped Hydro Build limits to reflect updated approach.
Augmentation options tab: Added technical details for VIC-NSW Option 11.
Augmentation options tab: Minor wording changes to clarify options for VNI Option 1, QNI Option 3C, QNI option 2E.
Augmentations option tab: Power flow controller on Bannaby-Sydney West 330 kV line is removed from HumeLink for consistency with Transgrid's HumeLink PADR.
Augmentations option tab: Second 500/330 kV transformer at Wagga is removed from VNI Option 6, 7 and 8. This has been included with HumeLink option.
Augmentations option tab: Note 13 included in relation to SA-NSW option.
Additional Tab added: Interconnector representation. This describes how the interconnectors are represented in the capacity expansion models
Additional Tab added: Transmission component costs – this describes the unit costs for transmission build used in cost estimates.
Updated REZ name Central West NSW to Central-West Orana throughout workbook.
Augmentations option tab: Updated SA-NSW to reflect new terminal station at Bundey,
Augmentations option tab: Updated descriptions for VNI 6 and VNI 7 to reflect the new terminal station north of Ballarat
Build costs tab: deleted the repeated build cost table from CSIRO GenCost 2019-20
Additional Tab added: CCGT Unit Maximum Capacity. This tab provides the maximum capacity (MW) of CCGT gas and steam turbines separately.
Additional Tab added: GPG_Min Stable Level. This tab provides the minimum operating levels (MW) for large GPG units.
Additional Tab added: Max Ramp Rates. This tab provides the maximum rates of change (MW/min) for thermal unit output up and down.
Additional Tab added: Min Up&Down Times. This tab provides the minimum time (h) online or offline for large GPG units.
Additional Tab added: Complex Heat rates. This tab provides parameters to produce heat rate curves for thermal units.
Additional Tab added: Start Cost of GPG. This tab provides the notification time (h) and start up costs ($/MW) for CCGTs and gas-powered steam turbines.
Minimum capacity factor information provided for GPG units, represented in the DLT model
Additional clarity provided on TRET and VRET implementation
2.0 | 2020-09-01 | Demand forecast tabs (orange): Updated to reflect 2020 ESOO consumption and demand forecast
Gas and Liquid fuel price tab: Update Gas prices based on December 2019 Core Energy Gas price outlook
Build Costs tab: updated to be based on CSIRO GenCost 2019-20 final report
Maximum capacity tab: Updated based on July 2020 GenInfo
Firm capacity tab: Updated based on July 2020 GenInfo
Seasonal ratings tab: Updated based on July 2020 GenInfo
Fixed OPEX tab: Updated based on July 2020 GenInfo
Variable OPEX tab: Updated based on July 2020 GenInfo
MLF tab: Updated based on July 2020 Marginal loss factors
Carbon Budgets tab: Carbon budget updated for the period 2021 to 2050 (financial years ending)
Scenarios tab: Updated with 2020 modelling scenarios settings - Large-scale renewable build cost trajectories
Data correction for heat rate curves.
Australian dollars have been updated from $ 2019 to $ 2020 using All groups CPI index values - June 2020 from the Australian Bureau of Statistics at https://www.abs.gov.au/AUSSTATS/abs@.nsf/Lookup/6401.0Main+Features1June%202020?OpenDocument
Auxiliary tab: Auxiliary Load for existing, committed and anticipated generators updated based on July 2020 GenInfo
Generator Reliability Settings tab: Updated outage data for existing units based on 2020 ESOO
Gas infrastructure updated to reflect the 2020 GSOO information (with costs scaled to Real June 2020)
2.1 | 2020-11-27 | Seasonal ratings tab: Update to clarify Temporary Generation South summer availability assumption to align with 2020 ESOO.
2.2 | 2020-12-11 | Assumptions Summary tab: Added additional data source for emissions
Maximum capacity tab: Commissioning date and installed capacity corrections
Seasonal ratings tab: Data correction for Cullerin Range Wind Farm
Retirement tab: Minor data corrections
Fixed OPEX tab: Data correction for various CCGTs, OCGTs, Reciprocating engines and Gas-powered ST units
Variable OPEX tab: Data correction for various CCGTs, OCGTs, Reciprocating engines and Gas-powered ST units
Emissions tab: Data correction for various CCGTs, OCGTs, Reciprocating engines and Gas-powered ST units
3 | 2020-12-11 | New Tab: Scenarios (New) - describes proposed new scenarios for 2021-22 forecasting and planning activities.
Renewable Energy Zones tab: Added new Q9 Banana REZ. Removed N4 - Southern NSW Tablelands. Renamed T3 (Central Highlands) to Central Highlands. Boundaries for N6 (Wagga) and T3 (Central Highlands) adjusted.
Scenario Policy Settings: Updated with policy settings for the new proposed scenarios
Renewable Policy Targets: Updated renewable policy targets with latest legislation / data
Carbon Budgets: Updated carbon budgets for new proposed scenarios, derived by scaling down SSP/RCP global emission pathways to a NEM level
Gross State Product: Updated to reflect 2020 Covid-19 updated economic forecasts from BIS Oxford
New Tab: Household Disposable Income - contains 2020 Covid-19 updated economic forecasts from BIS Oxford
Network Capability tab: Revised reflect proposed zonal model.
Proportioning Factors tab: Updated to reflect proposed zonal model
Transmission Component costs tab: Updated costs to 30 June 2020 real dollars.
Updated to Generation Information based on November 2020 release of Generation Information: •Added new Committed Projects •Update to Commission Dates and Installed Capacity of Committed Projects •Update to Expected Closure Dates •Update to Seasonal ratings
Build Costs: Updated based on draft CSIRO GenCost 2020-21
Connection Costs tab: Updated costs to 30 June 2020 real dollars. Addition of system strength mitigation costs.
Build Limits tab: REZ resource limits updated to take into account recently committed generation. Group constraint table added. Transmission limits and expansion costs updated to 30 June 2020 real dollars. System Strength costs added. REZ resource limit violation penalty factor added.
Build Limits tab: Export Superpower scenario REZ expansion costs added. Updated impacts of interconnector upgrades on REZ capacities.
New tab: Power System Security constraints
Capacity Factors tab: updated capacity factors for most recent REZ locations and renewable resource data
Financial parameters tab (formerly WACC): updated discount rate and WACC based on latest assumptions, added VCRs
Updated New entrants technical parameters based on Aurecon 2020 AEMO costs and technical parameter review. Tabs: Seasonal rating, Maintenance, Generator Reliability Settings, Lead time, Storage properties, Heat rates, Auxiliary, Fixed OPEX, Variable OPEX, Emissions
Coal and Biomass price tab: Updated Coal Prices based on 2020 coal price forecast by Wood Mackenzie.
Gas and Liquid fuel price: updated based on data from Lewis Grey Advisory
MLF tab: Updated to reflect latest information
Heat Rate & Complex Heat Rate tabs: Updated Heat Rates for new entrant technologies based on 2020 Aurecon data
GPG Minimum Stable Level tab: Updated MSL for new CCGTs and OCGTs based on 2020 Aurecon data. These are now presented as a percentage of nameplate capacity
Gas Infrastructure tab: updated to reflect most recent information gathered for 2021 GSOO
Pipeline Transmission Tariffs tab: updated to reflect most recent information available
Gas Reserves and Resources tab: updated with 2020 Wood Mackenzie data
Gas Production Costs tab: updated with 2020 Wood Mackenzie data
Gas Expansion Candidates tab: updated to reflect most recent information available
Regional Costs - Hydrogen techs tab: regional costs added
Build Costs - Hydrogen techs: build costs added.
Hydrogen demand tab: demand projections added
Other assumptions - Hydrogen techs tab: various other hydrogen-related assumptions added
New tab: 'Transmission Reliability'
3.1 | 2021-07-31 | Major update for Finalisation of 2021 IASR. Updated to June 2021 $.
Scenario details revised for new scenarios.
Renewable Energy Zones: Updated for new REZs, including offshore wind zones.
Renewable Policy Targets: Updated with latest available policy information.
Carbon Budgets: Updated with new data based on CSIRO multi-sectoral modelling.
Demand and energy forecast inputs, including DER: Updated for latest consultancies and inputs, and to include sub-regional allocation.
Network capabilities, parameters and augmentations: Updated to reflect latest augmentation options and costs, seasonal transmission limits, loss factors and outage rate assumptions.
Generation technical assumptions: Updated based on latest Generation Information page. Generation limits revised to reflect ISP Methodology. Reliability settings updated based on latest assumptions for the 2021 ESOO. Minor other updates such as updated emissions factors to reflect recent observations.
Generation cost assumptions: Updated to reflect latest CSIRO projections as well as other updates to operating and maintenance assumptions. Removed refurbishment costs as now included in annual FOM. Updated regional cost factor assumptions.
Build Costs: The Hydrogen Export scenario assumes faster capital cost reductions for large-scale Solar PV than the High VRE GenCost scenario, as a key enabler of hydrogen expansion for export.
Build limit assumptions: Revised REZ limits for updated REZ assumptions. New tab added with revised pumped hydro limits. Additional tabs added for REZ Augmentation Options and Non-REZ assumptions.
Capacity factors: Revised for latest wind and solar production forecasts.
Lead time and project life: Minor updates including extending pumped hydro to 40-year economic life.
Financial parameters: Revisions to both discount rate and VCR based on consultation feedback.
Storage properties: Updated based on information provided by Tasmania and final assumptions from Aurecon 2020-21 AEMO costs and technical parameter review.
Fuel price assumptions: Minor updates to coal and gas prices.
Unit commitment-related assumptions: Minor updates to reflect latest available data.
Hydrogen assumptions: Updated to reflect final assumptions, added Hydrogen prices for hydrogen turbines, green steel demand.
Removed tabs: Scenarios (2020) (not needed), Firm capacity (refer to ISP Methodology), GPG Start Costs (refer to ISP Methodology), Energy Consumption and Maximum Demand (merged), Gross State Product and Household Disposable Income (merged), Transmission Cost Components (See Transmission Cost Database), Refurbishment (now included in FOM), Gas assumptions (see GSOO)
3.2 | 2021-08-10 | Corrected errors on the Aggregated energy storages and Embedded energy storages worksheets.
Minor corrections to Summary Mapping worksheet.
Added additional information on Project EnergyConnect loss functions.
Corrected transmission outage rate worksheet to refer to 'Liddell to Bulli Creek' rather than 'Liddell to Dumaresq'.
Revised the PEM Electrolyser Fixed OPEX to reflect Aurecon 2020-21 AEMO costs and technical parameter review assumption of 3% of capex.
Added additional details to the Battery & Plug-in EVs on the share of Vehicle-to-Grid charge profiles.
3.3 | 2021-12-10 | Changed scenario name for Net Zero 2050 to Progressive Change
Renewable Energy Zones: Updated OWZ O1 and O2 ISP sub-region locations to SNW and both REZ diagrams to refine the Central West Orana REZ shape based on information published by the NSW Government.
Existing Gen Data Summary: Added REZ Location column
Build limits tab: Corrected column name from 'REZ build limit' to 'REZ Network Transmission Limit'. Corrected N1, N2, S1, T1, T2, T3 and MN1 Transmission limits. Updated S3 and S5 REZ Network limits to reflect group constraints MN1 and NSA1, and not a need for separate network limits. Removed NQ3 limits to avoid duplication of the CNQ-SQ flow path. Updated NSW Hydrogen generic transmission cost to ensure that flow path upgrades are incorporated. Added tranche 2 and 3 transmission expansion costs. Additional detail added on land area constraints.
Augmentation Options tab: Updated VNI West (via Kerang) cost and description with data received from Transgrid (cost reduction due to parts of Project EnergyConnect being built at 500 kV). Updated VIC-SNSW Option 7, this option can be built with or without any VNI West option in place. Updated VIC-TAS Options 1 & 2 by removing combined limits of TAS to VIC direction of Basslink and Marinus Link (it can transfer full capacity of each of the links). Updated Project EnergyConnect with a double circuit 500 kV line from Dinawan to near Wagga Wagga, operating at 330 kV. Added a new VIC-SNSW Option 6A, this option can be built without VNI West (Kerang) option in place. Added CNSW-NNSW Option 6A and 6B (Option 6B includes line shunt reactors) for New England REZ. Added new options "H-Newcastle" and "H-Dapto" to provide access for REZs to supply ports in the Hydrogen scenario. Added to SNSW-CNSW Option 1 (HumeLink) a new double circuit 330 kV line from new Wagga Wagga substation to the existing Wagga Wagga substation (as per Transgrid's PACR published in July 2021). Changed description of capacity for CNSW-SNW option 2. Updated CQ-CNQ Option 1 description by replacing South West Queensland with Wandoan South.
REZ Augmentations Options: Updated description of N2 Option 2 REZ Augmentation to include 330kV line from Armidale to Lower Creek. Updated description of NQ2 REZ Augmentation to remove reference to Nebo-Bouldercombe. Added 330 kV Cooma-Monaro REZ build option. Added 500 kV option for Darling Downs REZ expansion. Added additional upgrade options for Central West Orana REZ.
Retirement: Changed Mount Piper retirement date to 2040 based on latest information in the October 2021 Generation Information release.
Carbon Budgets: Corrected the stated carbon budget horizon, from 2049-50 to 2050-51. This was a typographical error in the last version.
Added Torrens Island BESS to Existing Gen Data Summary, Fuel Price Summary, Maximum Capacity, Seasonal ratings, Retirement, Marginal Loss factors and Summary Mapping tabs.
Summary Mapping: Updated REZ Locations for existing, committed and anticipated VRE generators. Changed Mapping for BOTN - Cethana FOM and VOM to TAS Medium
Renewable Policy Targets: Updated to reflect new information on the VRET2 and the NSW Electricity Infrastructure Roadmap.
Network Capability: Updated network capabilities of SNSW – CNSW (Northern part of "VNI") and VIC – SNSW (Southern part of "VNI") flow paths representing Snowy 2.0 generation and pump load limits prior to HumeLink.
Augmentation Options tab: Adjusted Marinus Link cost to reflect 30 June 2021 real dollars, and combined early works costs into cable 1 costs.
3.4 | 2022-06-30 | Existing Gen Data Summary: Updated with new generators based on Feb 2022 GenInfo
Fuel Price Summary: Updated with new generators based on Feb 2022 GenInfo
New Entrant Data Summary: Additional note to reflect cost penalty factors applied to Q1 and Q2 generation to take into account declining MLFs
Build Limits: Minor corrections, inclusions of additional cost tranches, updated information for offshore wind zones, updated impact of major projects.
Renewable Energy Zones: Additional notes for clarity, new offshore wind zones.
Renewable Policy Targets: Updated NSW target to reflect updated committed and anticipated generation which reduces further development requirements.
Network Augmentation Options: Update Marinus Link costs and timings, update of PEC timing and other updates to transfer limits and impacts on REZ limits.
Network capability: Updated note 6 to include transfer limit increase from CNSW - SNW with a 700 MW SIPS battery scheme and Bannaby - Sydney West 330 kV line upgrade and included a table with committed project timing.
REZ Augmentation Options: Corrected metric for system strength cost from $/MW to $M/MW, included NQ2 option 2 augmentation
Marginal Loss Factor: Corrected wind and solar MLFs for N4 REZs and shadow connection point for N3_Solar REZ
Capacity Factors: Updated REZ wind capacity factors to reflect latest wind profiles used in modelling.
Maximum capacity: Updated based on Feb 2022 GenInfo
Seasonal ratings: Updated based on Feb 2022 GenInfo
Retirement: Updated based on Feb 2022 GenInfo
Summary Mapping: Updated with new generators based on Feb 2022 GenInfo
3.5 | 2022-08-31 | Existing Gen Data Summary: Updated with new generators based on July 2022 GenInfo
Fuel Price Summary: Updated with new generators based on July 2022 GenInfo, deleted 2020-2021 values to reflect latest gas price data, and updated scenario mapping for gas prices.
Economic Growth Forecasts: Updated with rebased forecasts using ABS FYE 2021 data
Energy Efficiency: Updated with rebased forecasts for 2021-22
PVNSG: Updated with rebased forecasts using 2021-22 actuals
Rooftop PV: Updated with rebased forecasts using 2021-22 actuals
DSP: Updated based on historical meter data analysis and information submitted to the DSP Information Portal in April 2022
Electrification: Updated with rebased forecasts for 2021-22
Battery and plug in EVs: Updated uptake and consumption due to rebasing of uptake data based on EVC numbers to end 2021
Aggregated Energy storages: Deleted Steady Progress to reflect current scenario collection
Sub-regional demand allocation: Deleted Steady Progress to reflect current scenario collection
Transmission Reliability: Updated based on latest assumptions for the 2022 ESOO
Proportioning factors: Updated loss equations, loss factor equations and proportioning factors for the current network to align with AEMO's 'Marginal Loss Factors: Financial Year 2022-23' publication.
Augmentation options: Updated Project EnergyConnect full capacity release date, consistent with the 2022 Final Integrated System Plan and advice from responsible transmission network service providers.
Maximum capacity: Updated based on July 2022 GenInfo
Seasonal ratings: Updated based on July 2022 GenInfo
Maintenance: Update for new entrant technologies based on Aurecon 2021-22 AEMO costs and technical parameters review.
Generator Reliability Settings: Updated for the existing technologies based on latest assumptions for the 2022 ESOO and for the new entrant technologies based on Aurecon 2021-22 AEMO costs and technical parameter review
Hydro Climate Factor: Deleted Steady Progress to reflect current scenario collection
Build costs: Updated based on Final CSIRO GenCost 2021-22
Regional Cost Factors: Updated based on based on Aurecon 2021-22 AEMO costs and technical parameter review
Lead time and project life: Updated based on based on Aurecon 2021-22 AEMO costs and technical parameter review
Storage properties: Updated based on based on Aurecon 2021-22 AEMO costs and technical parameter review
Coal and Biomass price: Deleted Steady Progress from scenario mapping
Gas, Liquid fuel, H2 price: Gas prices updated based on price forecasts delivered by Lewis Grey Advisory for the 2022 GSOO
Retirement: Updated based on July 2022 GenInfo
Heat rates - Update for new entrant technologies based on Aurecon 2021-22 AEMO costs and technical parameters review, and existing based on July 2022 GenInfo
Auxiliary: Updated auxiliary rates of existing generators based on latest assumptions for the 2022 ESOO / Update for new entrant technologies based on Aurecon 2021-22 AEMO costs and technical parameters review.
Fixed OPEX - Update for new entrant technologies based on Aurecon 2021-22 AEMO costs and technical parameters review, and existing based on July 2022 GenInfo
Variable OPEX: Update for new entrant technologies based on Aurecon 2021-22 AEMO costs and technical parameters review.
Emissions intensity: Update for new entrant technologies based on Aurecon 2021-22 AEMO costs and technical parameters review, and existing based on July 2022 GenInfo
Marginal Loss Factors: Updated to reflect latest information
Affine Heat rates: Update for new entrant technologies based on Aurecon 2021-22 AEMO costs and technical parameters review.
GPG Min Stable level: Update for new entrant technologies based on Aurecon 2021-22 AEMO costs and technical parameters review.
Build Costs - PEM: Updated based on Final CSIRO GenCost 2021-22
Other hydrogen assumptions: Updated the PEM Electrolyser Fixed OPEX based on Aurecon 2021-22 AEMO costs and technical parameter review
Summary: Updated based on GenInfo 2022 / Aurecon 2021-22 AEMO costs and technical parameters review
New version 4.0 supporting the Draft 2023 IASR
4 | 2022-12-16 | Scenarios: Updated with proposed scenarios in Draft 2023 IASR
Renewable Energy Zones: Updated to include new offshore wind renewable energy zones and revised boundaries. Inclusion of N9 - Hunter Central REZ and T5 - North East Tasmania Coast.
Existing Gen Data Summary: Updated with new generators based on November 2022 GenInfo
New Entrant Data Summary: Updated with new ISP sub-regions and reflecting updated new entrant technologies
Fuel Price Summary: Updated with new generators based on November 2022 GenInfo, and updated scenario mappings.
Regional Build Costs Summary: Reflects updated new entrant technologies
Renewable Policy Targets: Updated to reflect latest QRET, VRET, added the Victorian Energy Storage Target, and updated trajectory of NSW Electricity Infrastructure Roadmap.
Carbon budgets: Updated carbon budgets based on latest multi-sectoral modelling commissioned from the CSIRO and ClimateWorks Centre.
DSP: Initial year forecast shown based on ESOO 2022 projection. DSP as percentage of max demand forecast in future years shown based on the IASR assumptions. Once the new max demand forecasts are known in July 2023, the forecast will be provided in MW as well.
Economic Growth Forecasts: Update based on BIS Oxford Economics long term macroeconomic forecasts developed for AEMO in July 2022.
Energy Efficiency: Update based on 2022 forecasts developed by CSIRO and ClimateWorks Centre.
Rooftop PV: Updated rebased forecasts using updated actuals and new blended consultant forecasts
PVNSG: Updated rebased forecasts using updated actuals and new blended consultant forecasts
Battery and plug in EVs: Updated forecasts applying improved actuals data from new EV source data, and updated CSIRO forecasts
Fuel cell EVs:: Updated forecasts applying improved actuals data from new EV source data, and updated CSIRO forecasts
EV V2G: Updated forecasts applying improved actuals data from new EV source data, and updated CSIRO forecasts
Electrification: Update based on 2022 CSIRO's EV and Multi-sector studies.
Embedded energy storages: Updated rebased forecasts using updated actuals and new blended consultant forecasts
Aggregated energy storages: Updated rebased forecasts using updated actuals and new blended consultant forecasts
Sub-regional demand allocation: Subregional allocations will be finalised ahead of the Final 2023 IASR.
Network representation: Map of sub-regional representation updated include new sub-regions. New sub-regional flow paths added. Changes to load and generation representation in CQ-GG and CQ_NQ captured. Update regional topology for Victoria - New South Wales and Victoria to South Australia with Project Energy Connect.
Network losses: Proportioning Factors worksheet name changed to Network losses. For the existing interconnectors, loss and MLF equations presented as published in the 'Marginal Loss Factors: Financial Year 2022-23'. Intraregional losses for CQ-NQ and SQ-CQ added. VNI option 7 loss equations and MLF equations updated.
Network Capability: Transfer limits for new flow paths added. Uplifts of transfer limits with committed and anticipated projects added. Committed and anticipated project table with timing added. TAS-VIC interconnector transfer limit updated. Updated for the consideration of new sub-regions.
Augmentation options: Updated sub-regional model references. Updated Marinus Link and Basslink combined transfer limit. Updated additional REZ capacity for Humelink and VNI West Kerang
Maximum capacity: Updated based on November 2022 GenInfo and added QEJP pumped hydro candidates
Seasonal ratings: Updated based on November 2022 GenInfo and added QEJP pumped hydro candidates
Reserves: Changed minimum reserve levels in QLD, SA and TAS based on November 2022 Generation Information summer peak ratings.
Generation limits: Deleted new entrant coal minimum stable levels (on account of that technology no longer being an option) and max capacity factor constraints for coal
Maintenance: Updated new entrant technologies based on Aurecon 2022 AEMO costs and technical parameters review and added QEJP pumped hydro candidates
Generator Reliability Settings: Updated new entrant technologies based on Aurecon 2022 AEMO costs and technical parameters review and added QEJP pumped hydro candidates
Hydro Climate Factor: Updated scenario mappings
Build Costs: Updated with Draft CSIRO GenCost 2022-23, updated scenarios and added QEJP pumped hydro candidates
Regional Cost Factors: Updated with Aurecon 2022 AEMO costs and technical parameters review and latest new entrants
Connection Cost: Inclusion of additional REZs to tables. Removal of System Strength remediation cost from V2 and V3 based on Victorian RDP system strength projects
REZ Augmentations Options: Include new offshore REZs in table. Include new Group Constraint and Transmission Limit constraints in table. Removed NSA1 Option 1 as it is considered part of ElectraNet NCIPAP projects. Updated for new sub-regional model.
Build Limits: New group constraints added - SQ1, SWV1, NET1, new transmission limit constraints table added - SEVIC1, SWQLD1, new secondary REZ transmission limits table added - SWNSW1, V3-EAST, V3-WEST, N5 transmission limit adjusted to take into account updated N5 REZ generation mapping. Include table showing REZ transmission modifiers due to committed and anticipated network augmentations. For Tasmania T2 transmission limit was decreased to account for recent stability constraint binding outcomes and T3 transmission limit was reviewed based on historic line flows and ratings. NSA1 transmission limit increased to take into account ElectraNet NCIPAP upgrades. Resource limit violation penalty factor updated to 0.27$M/MW (CPI increase). Seasonal limits added to REZ transmission limits. New REZ N9 (Hunter Central Coast) and T5 (Tasmania East Coast) added. Offshore Wind Resource Limits split into Fixed and Floating capacities and updated based on land size.
Non-REZ Assumptions: Update to N0 land area to exclude areas now included in N9 (Hunter Central Coast REZ). Update of Resource Limit violation penalty factor to 0.27 $M/MW (CPI increase)
Power System Constraints: Updated the planning unit commitment requirements. These requirements will be applicable to the DLT and ST model
Capacity Factors: Updated to include 2021-22 reference year, new REZs and floating offshore wind. Solar thermal capacity factors have been recalculated using the new 15 hour storage configuration in Aurecon 2022.
Build limits - PHES: Adjusted limits in QLD, NSW and SA based on recent government policy announcements and developer proposals in November 2022 Generation Information, and added QEJP - Borumba and QEJP - Pioneer-Burdekin as a separate PHES category
Lead time and project life: Updated with Aurecon 2022 AEMO costs and technical parameters review and added QEJP pumped hydro candidates
Financial Parameters: Updated with latest discount rates and values of customer reliability.
Storage properties: Updated with Aurecon 2022 AEMO costs and technical parameters review and added pumped hydro properties for QEJP - Borumba and Pioneer-Burdekin
Gas, Liquid Fuel, H2 price: rebased liquid fuel price to real 2022 dollars. Updated H2 prices to latest outputs from MSM 2022.
Coal and Biomass price: rebased Biomass price to 2022 real dollars. Coal price: For export exposed using weighting of Woodmac 2021 prices and BIS 2022 export coal price. Non export exposed using Woodmac price
Retirement: Updated based on November 2022 GenInfo
Heat rates: Updated with Aurecon 2022 AEMO costs and technical parameters review
Auxiliary: Updated with Aurecon 2022 AEMO costs and technical parameters review and added QEJP pumped hydro candidates
Fixed OPEX: Updated with Aurecon 2022 AEMO costs and technical parameters review, rebased existing to real 2022 dollars
Variable OPEX: Updated with Aurecon 2022 AEMO costs and technical parameters review, rebased existing to real 2022 dollars
Emissions Intensity: Updated existing with NGER 2020-21 data, reduced emissions intensity for new entrant biomass generator to 20.8 kg/MWh to reflect DCCEEW estimates, updated new entrants with Aurecon 2022 heat rates, and added QEJP pumped hydro candidates
GPG emissions reduction - BioM: Added this new sheet which gives projected emissions reduction from GPG due to blending of biomethane into fuel gas based on CSIRO/CWA Multi-sector energy modelling (2022), and AEMO internal study.
Marginal Loss Factors: Updated to reflect latest information and sub-regional configuration.
Affine Heat rates: Updated for new entrant technologies based on Aurecon 2022 AEMO costs and technical parameters review.
Max Ramp Rates: Updated for new entrant technologies based on Aurecon 2022 AEMO costs and technical parameters review.
GPG Min Stable level: Updated for new entrant technologies based on Aurecon 2022 AEMO costs and technical parameters review.
Cost Summary - PEM: updated scenarios, updated technology cost breakdowns with Aurecon 2022 AEMO costs and technical parameters review data
Build Costs PEM: Updated with Draft CSIRO GenCost 2022-23, updated scenarios
Hydrogen demand - Domestic: Update based on 2022 forecasts developed by CSIRO and ClimateWorks Centre.
Hydrogen Monthly profiles: Added this new sheet which gives NEM monthly hydrogen consumption profiles
Hydrogen demand - Export&Steel: Update based on 2022 forecasts developed by CSIRO and ClimateWorks Centre.
Hydrogen export ports: Added additional Queensland ports
Other hydrogen assumptions: Updated with Aurecon 2022 AEMO costs and technical parameters review data and CSIRO, Multisector Modelling 2022 input assumptions
Summary Mapping: Updated with new generators based on November 2022 Generation Information and additional new entrant candidates based on new sub-regions, REZs and candidate technology list from Aurecon 2022.
5 | 2023-07-28 | 2023 IASR Assumptions Workbook release
All relevant tabs, updated to reflect July 2023 GenInfo.
All relevant tabs, removed QEJP projects from New Entrant tables.
All relevant tabs, updated to reflect latest set of scenarios.
Generation Limits, Heat Rates, Affine Heat Rates: Deleted Liddell which is now retired.
Hydro Scheme Inflows: Updated to include 2021 and 2022 inflows.
Max Ramp Rates: Updated to reflect recent changes in operator bids. Also corrected values for separated CCGTs.
Energy Policies: Renamed tab from Renewable Policy Targets: and updated to reflect 2023 IASR policies
Carbon Budgets: Updated with State-level carbon budgets
Sub-regional demand allocations: Percentage splits of different consumer energy resources by sub-region have been added
DSP: Initial year forecast updated to ESOO 2023 projection. DSP as percentage of max demand forecast in future years redone based on updated IASR assumptions. Once the new max demand forecasts are known in August 2023, the forecast will be provided in MW as well.
Economic Growth Forecasts: Update based on rebased Oxford Economics Australia long term macroeconomic forecasts developed for AEMO in July 2022.
Transmission Reliability: Split to show separate reclassification and single credible contingency values and updated with new values.
Generator Reliability Settings: Includes new outage classifications based on consultation on Reliability frameworks, rolled forward horizon and added new values.
Auxiliary: Update based on latest Generation Information.
Coal and Biomass price: rebased coal Biomass price to 2023 real dollars. Coal price: For export exposed using weighting of Woodmac 2021 prices and Oxford Economics Australia 2022 export coal price. Non export exposed using Woodmac price. (Note Liddell power station excluded as it is closed)
Hydrogen monthly percentage profiles: updated with new data
GPG emissions reduction: updated with new data
Hydrogen demand - Domestic: Updated forecasts, included lead times, added sub-regional splits
Hydrogen demand - Exports & Steel: updated forecasts, incorporated lead times
Hydrogen export ports: Updated map for REZ and offshore zones
Electrification: Update based on latest LIL development plans; Electrification alternatives sensitivity based on Step Change with reduced pace of industrial electrification
Energy efficiency: Update based on 2023 forecasts developed by Strategy Policy Research (SPR)
Biomethane prices added in $2023 dollars on tab gas, liquid, H2 prices
Battery and plug in EVs: Rebased CSIRO forecasts applying March 2023 actuals from VFACTS and minor revisions in PHEV forecasts to incorporate stakeholder feedback.
Build limits - PHES: Adjusted limits in QLD, NSW and SA to accommodate announced projects in July 2023 Generation Information, and removed QEJP - Borumba and QEJP - Pioneer-Burdekin categories
Capacity Factors: Updated to include 2022-23 reference year
Retirement: Updated based on July 2023 GenInfo and QEJP report.
Emissions Intensity: Removed Liddell Power Station and QEJP projects, updated to latest CER data.
Build costs: Updated with Final 2023 CSIRO GenCost
Financial parameters: Updated with latest discount rates and values of customer reliability.
Non-REZ Assumptions: Update to N0 and V0 land area. Inclusion of MW land use limits for wind and solar. Update of Resource Limit violation penalty factor to 1.0 $M/MW.
Build Costs - PEM: Updated based on Final CSIRO GenCost 2022-23
Renewable Energy Zone: Updated the REZ/Cost Zone maps offshore boundaries as per Federal Government announcements. Added the new NSW N12 REZ.
Network representation: Updated SESA-CSA
Network losses: Loss equations and footnotes updated as per new equations.
Network Capability: Updated as per the 2023 Transmission Expansion Options Report
Augmentation Options: Updated as per the 2023 Transmission Expansion Options Report
Connection Cost: Inclusion of additional REZs(N12) to tables. Update System Strength remediation cost from the updated Transmission Cost Database
REZ Augmentation Options: Updated as per the 2023 Transmission Expansion Options Report
Build Limits: Updated the Indicative transmission expansion cost ($M/MW)2; Added land use limits in MW for all scenarios; Updated REZ transmission modifiers due to committed and anticipated network augmentations table; Updated REZ Group Constraints Summary; Updated REZ Transmission Limit Constraint Summary
Non-REZ Assumptions: Added the land use limits in MW and updated the land area. Updated the total cost and System Strength Remediation costs
Power System Constraints: No updates since draft IASR
Marginal Loss Factors: Updated the tables with the updated shadow connection points, and updated MLF.
Added Kogan Gas and SA Hydrogen Turbine
5.1 | 2023-08-07 | Flow path augmentation options; Flow path costs forecast: Updated CQ-SQ Option 5 cost estimate and easement length to align with v1.1 of 2023 Transmission Expansion Options Report, and adjusted forecast accordingly; Corrected cost estimate class for Humelink.
REZ augmentation options; REZ costs forecast: Updated REZ Q2 Option 1 cost estimate to remove inclusion of Guybal Munjan substation, and adjusted forecast accordingly.
Network capability: Updated CNSW-SNW representation to include both northern and southern limits; Updated the list of committed and anticipated projects to align with July 2023 Transmission Augmentation Information page.
Auxiliary: Changed the new entrant wind auxiliary from 0% to 0.07%
Marginal Loss Factors: Aligned Kogan Gas MLF from 0.9764 to 0.9673, similar to Kogan Creek.
Fixed OPEX: Changed the Fixed OPEX for existing pumped hydro from $17.77 to $19.09, Cell D75 of sheet.
Summary Mapping: Changed subregion of Eraring Big Battery from CNSW to SNW
H2 GPG_emissions reduction: Added additional tab (H2 GPG_emissions reduction) for gas fired generation emissions reduction factor from hydrogen for Kogan Gas (Brigalow/Kogan Creek in Queensland) and SA Hydrogen Turbine (Whyalla in SA).
Max Capacity: Changed the commissioning date for Kogan Gas to 1/7/2026 and SA Hydrogen Turbine to 1/12/2025.
Summary Mapping, Fuel Price Summary, Emissions intensity: Updated relevant entries for Kogan Gas and SA Hydrogen Turbines in Summary Mapping, Fuel Price Summary, Emissions intensity tabs to account for hydrogen blending.
5.2 | 2023-09-05 | Carbon Budgets: Updated Victoria's carbon budget to use consistent treatment of calendar dates with other constraints such as RETs. Previous carbon budget assumed the targets for calendar years 2025 and 2030 were met in financial year-ending (FYE) 2026 and 2036; this has been modified to be FYE 2025 and 2035.
DSP: Full forecast to 2054 added for the three scenarios
Energy efficiency: Updated Business sector forecasts for Reduced Energy Efficiency Sensitivity
Electrification: Updated forecasts for Electrification Alternatives Sensitivity
Maximum capacity: A small subset of committed* and anticipated projects that have Full Commercial Use Date (FCUD) before 1 July 2025 had their commissioning dates shifted to 1 July 2025. This has now been corrected to reflect commissioning date at FCUD instead in line with approached described in the Final IASR.
Seasonal ratings: Updated ratings of certain committed* and anticipated projects, as discussed in the Maximum capacity log update above.
Generator reliability settings: Deleted QEJP objects as separate new entrant items, in line with the approach laid out in the 2023 IASR
Locational cost factors: Deleted QEJP objects as separate new entrant items, in line with the approach laid out in the 2023 IASR
Retirement dates: A small subset of new committed and anticipated projects had erroneous expected retirement years. This has now been corrected by applying the methodology discussed in the Retirement tab, where generators without an announced retirement date are given a retirement date of X years past the station’s commissioning date, where X is the technical life of that technology.
Auxiliary: Mapped new entrant offshore wind values to onshore wind.
Summary Mapping: Corrected the zone Eraring Big Battery is in to SNW.
Flow path augmentation options: Updated easement lengths for SQ-CQ (Option 1), VIC-SNSW (VNI-West), CNSW-SNW (Option 2), SNSW-CNSW (Humelink) , CNSW-SNW (Option 3), TAS-VIC (Marinus Link Stage 1 & 2) to align with v1.2 of 2023 Transmission Expansion Options Report; Updated cost estimate for SQ-CQ (Option 1) to align with v1.2 of 2023 Transmission Expansion Options Report.
Flow path costs forecast: Updated cost forecast for SQ-CQ (Option 1) to align with cost estimate for v1.2 of 2023 Transmission Expansion Options Report. Corrected the cost forecast for Marinus Link Stage 1 to reflect June 2023 dollar value.
Renewable Energy Zones: Updated the N11 offshore maps based on Department of Climate Change, Energy, the Environment and Water publication dated 14 August 2023 (Notice of proposal to declare an area in the Illawarra); Corrected REZ Q9 to be located within the CQ sub-region.
REZ Augmentations options: Corrected the easement lengths for NQ2 (Option 1) & South West Victoria (Option 1A), T2 (Option 1); Corrected SEVIC expansion cost to align with v1.2 of the 2023 Transmission Expansion Options Report; Removed system strength costs from T2, T3 & V2 as they are covered in connection costs. Updated cost estimate to reflect the updated route length for T2 (Option 1). Corrected the cost estimate for T3 (Option 1 with Marinus and without Marinus) to reflect new easement length consistent with v1.2 of the 2023 Transmission Expansion Options Report.
Summary Mapping: Updated the subregion location for Mr Mercer, Swanbank, Waratah Super Battery, Tailem Bend Solar Stage 1 & 2 and Tailem Bend Battery
Build Limits: Updated the offshore resource output for fixed and floating wind output for N11 to reflect update from Department of Climate Change, Energy, the Environment and Water publication dated 14 August 2023 (Notice of proposal to declare an area in the Illawarra).
Marginal Loss Factors: Corrected the Generic new entrant units ( NE_CSA, REZ V7_Wind & REZ_T4_Wind) MLFs and their shadow connection points.
REZ Cost forecast: Added cost forecast for South West NSW (Option 1). Updated T2 ( Option 1) cost forecast to align with the updated total cost estimate. Updated T3 (Option 1 with Marinus and without Marinus) cost forecast to align with updated new easement length value in v1.2 of the Transmission Expansion Options Report.
New Entrant Data Summary: Corrected the formula for Fuel Cost column to point to the correct fuel price.
Summary Mapping: corrected Snapper Point fuel type to gas, and auxiliary category to OCGT
5.3 | 2023-12-15 | Seasonal Ratings: corrected ratings for Mt. Piper unit 2 and Darling Downs units
Renewable Energy Zones: Updated the boundaries for North East Tasmania offshore REZ in the REZ Map and Regional Cost Zone Map (based on Federal Government announcement 23 October 2023 (https://www.dcceew.gov.au/energy/renewable/offshore-wind/areas/bass-strait), Noted a clarification that the AEMO KML map files have not yet been updated as this is subject to consultation. ; Added clarification note for the Regional Locational map explaining that "High" costs were assigned for Draft 2022 ISP onwards for Central North VIC REZ V6 based on feedback on the 2020 IASR and Draft 2020 ISP.
Network Capability: Added a note for SNSW-CNSW & VIC-SNSW to clarify that the 660 MW limit for Snowy 2.0 is applicable for the existing network, and explaining that the full capacity of 2,200 MW becomes available when HumeLink is in service; Added a note for some committed and anticipated project timings to clarify where the modelled service date is different to the project proponents' latest public advice.
Flow Path Augmentation options: Added a note to include in CQ-NQ option 2 the additional capacity of NQ2 of 3000 MW to align with 2023 Transmission Expansion Options report; Added note to SQ-CQ option 5 augmentation to provide clarity that Borumba pumped hydro generation capacity has access through this augmentation; Added note to Humelink augmentation (SNSW-CNSW) to provide clarity that Snowy 2.0 generation capacity is unlocked through Humelink augmentation; Added note to Project Marinus Stage 1 and Stage 2, Humelink and Gladstone Grid Reinforcement to note that the earliest in service date modelled differs slightly from the latest public proponent date which is reported in AEMO's December 2023 Transmission Augmentation Information page; Added latest costs for Project Marinus Stage 1 and Stage 2 as advised by project proponents; Added note clarifying that Humelink is a pre-requisite to for VNI West, consistent with latest VNI West design. Updated "footnote 4" to clarify that generator capabilities relating to the Project Marinus Stage 1 transfer level include non-scheduled generation.
Flow Path costs forecast: Revised Project Marinus Stage 1 and Stage 2 cost forecast consistent with proponents' updated costs.
Connection cost: Added Gippsland Coast (V7) connection costs to represent connection of offshore wind of this REZ as a connection cost rater than a network augmentation cost, consistent with jurisdictional planning body and government advice.
Connection Costs forecast: Updated Gippsland Coast (V7) cost forecast to reflect the connection cost updated note above.
REZ Augmentations Options: Updated Central West Orana REZ Transmission Link scope to align with latest advice from project proponent, including noting relationship with Hunter Transmission Project; Added a note to N3 option 1 to clarify that REZ network capacity is limited to 6 GW to align with the New South Wales Network Infrastructure Strategy; Corrected MN1 Option 4 description to align with 2023 Transmission Expansion Options Report; Updated North West Tasmania (T2) option 1 as per advise from project proponent.
Build Limits: Revised Tranche 2 transmission expansion cost for N3 Central West Orana from 0.08 to 0.16 to reflect updated scope and alignment with the New South Wales Network Infrastructure Strategy; Updated Hunter-Central Coast indicative transmission expansion cost to reflect lower cost as option 2 was considered for the modelling purposes; Removed Gippsland Coast ( V7) expansion costs as it is included in the "Connection Cost" tab; Updated the transmission expansion cost ($/MW) value for Leigh Creek REZ (S6) to a higher value to reflect cost for smaller option; Revised North West Tasmania (T2) transmission expansion cost to reflect updated scope advice from project proponent; Corrected REZ group constraint SWV1 to include a negative sign for Heywood Interconnector to make flow from SA-VIC have the same impact as generation in V8 and V4.
Hydrogen export ports: Updated the boundaries for North East Tasmania offshore REZ in the Candidate hydrogen export ports and REZs map(based on Federal Government announcement 23 October 2023 (https://www.dcceew.gov.au/energy/renewable/offshore-wind/areas/bass-strait); Noted a clarification that the AEMO KML map files have not yet been updated as this is subject to consultation.
Energy Policy Targets: Revised start year of the Victorian offshore wind targets from 2028-29 to 2030-31.
Maximum capacity: Changed footnote on generator capacity adjustments where MarinusLink is built to reflect an increase of 50 MW.
Seasonal ratings: Corrected the summer peak ratings for Bango 973 Wind Farm, Bango 999 Wind Farm, Canunda, Cathedral Rocks, Crudine Ridge Wind Farm, Mt Gellibrand Wind Farm, Mt Mercer Wind Farm, White Rock Wind Farm - Stage 1 and Willogoleche Wind Farm.
Summary Mapping: Updated fuel mapping for Kurri Kurri and Tallawarra B
6 | 2024-07-19 | Renewable Energy Zones: Updated the REZ/Cost Zone maps offshore boundaries for Southern Ocean (V8) as per Federal Government announcements in March 2024 (https://www.dcceew.gov.au/energy/renewable/offshore-wind/areas/southern-ocean-region).
Energy Policy Targets: Modified Powering Australia Plan trajectory to match 2024 ISP, added Capacity Investment Scheme constraints.
Carbon Budgets: Added Queensland carbon budgets, modified NSW carbon budgets to account for the 2035 target.
Aggregated energy storages: Corrected MW and MWh forecasts for Aggregated energy storages to be on a consistent basis with reporting for Embedded energy storages. Note that the 2024 Integrated System Plan used the Aggregated energy storage forecasts from version 5.3 of this workbook published in December 2023, however differences between those forecasts and the updated forecasts are not expected to have a material impact on modelling outcomes.
Network Representation: Corrected definition of load and generation in Sydney, Newcastle and Wollongong sub-region to add Avon and Dapto, and in Central New South Wales sub-region to remove Avon and Dapto.
Network losses: Updated NSW-VIC loss equations and Basslink MLF to reflect the updated publication from AEMO: "Marginal Loss Factors: Financial Year 2023-24".
Network Capability: Basslink transfer limits updated as advised by APA, including removal of temperature-dependent ratings and addition of energy throughput limits table; Committed and anticipated projects’ timing updated to align with 2024 ISP modelling and latest information from project proponents.
Flow path augmentation options: Updated Tasmania to Victoria combined transfer capability to account for Basslink dynamic capability as advised by APA; Updated easement length for HVAC component of Project Marinus to reflect the proposed scope and staging of the North West Transmission Developments project as advised by TasNetworks; Added note to account for an increased cost of Project Marinus Stage 2 if completed in more than 2 years after Stage 1; Added note to clarify the amount of grant funding available for Project Marinus; Updated scope, cost, and timing for CNSW-SNW Option 1 (advised by EnergyCo); Updated scope and cost for CNSW-SNW Option 2b (advised by Transgrid); Added new CNSW-SNW Option 2d (advised by Transgrid).
Flow Path costs forecast: Updated cost forecast for Project Marinus across all scenarios to align with the revised earliest in-service date (December 2030 for Stage 1 and December 2032 for Stage 2) provided by Marinus Link Pty Ltd in November 2023; Updated cost forecasts for CNSW-SNW Options 1, 2b and 2d to reflect cost updates noted in flow path augmentation options tab.
Maximum Capacity: Updated based on February 2024 Generation Information report and additional projects from policies.
Seasonal ratings: Updated based on February 2024 Generation Information and additional projects from policies
REZ Augmentation Options: South East Victoria Option 1 updated as advised by AEMO Victorian Planning (AVP); Updated scope, cost and timing for the group constraint MN1 S3 Option 1, S3 Option 1a and S3 Option 1b (advised by ElectraNet); Updated scope of N2 Option 1 (advised by EnergyCo).
REZ Cost forecast: Added cost forecast for MN1 Option 1, Option 1a and Option 1b for all scenarios, to align with updated options advised by ElectraNet.
Build Limits: Initial South West Victoria group constraint limit changed to 1,850 MW, and increase following Mortlake turn in updated to 1,100 MW (as advised by AEMO Victorian Planning); Southern Ocean (V8) offshore build limits decreased to 780 MW for offshore fixed and to 3,330MW for offshore floating to align with updated declared area by Federal Government on 6th March 2024 (https://www.dcceew.gov.au/energy/renewable/offshore-wind/areas/southern-ocean-region); Updated North Tasmania Coast (T4) offshore build limits to account for the boundary declaration based on Federal Government announcement 23 October 2023 (https://www.dcceew.gov.au/energy/renewable/offshore-wind/areas/bass-strait); Updated SWNSW1 RHS Limit from 550 MW to 940 MW based on advice from Transgrid in order to reflect finalised non-network RIT-T outcomes; Additional note clarifying basis of offshore wind capacities modelled for the Illawarra offshore REZ as per declared area by Federal Government on the 15th June 2024 (https://www.dcceew.gov.au/energy/renewable/offshore-wind/areas/illawarra); Change of MN1 RHS limit from 2,400 MW to 2,000 MW as advised by ElectraNet; Change of indicative transmission expansion cost ($M/MW) for MN1 from 0.46 to 0.33$M/MW due to updated options as advised by ElectraNet; Second tranche cost applied for MN1 to expand beyond 1,200 MW to reflect $ 0.29 M/MW to align with new options provided by ElectraNet; Inclusion of new MN1 and NSA1 northerly flow group constraints to reflect load in the MN1 and NSA1 region accordingly.
Retirement: Updated based on February 2024 Generation Information report and additional projects from policies
Marginal Loss Factors: Updated based on February 2024 Generation Information Reports and additional projects from policies.
Hydrogen demand exports and steel: updated electricity for green steel based on data received from industry survey.
Hydrogen export ports: Updated the boundaries for Southern Ocean (V8) offshore REZ in the Candidate hydrogen export ports and REZs map (based on Federal Government announcement in March 2024 https://www.dcceew.gov.au/energy/renewable/offshore-wind/areas/southern-ocean-region)
Summary Mapping: Updated based on February 2024 Generation Information and additional projects from policies.

## Assumptions Summary
2023-24 Modelling Assumptions
This file presents tables of input data for 2023-24 market modelling studies. It is a compilation of data from a number of sources, listed below.
All values in this workbook are as at 30 June 2023 real dollars except were explicitly noted otherwise.
Version History
Version Number | Date | Description
1 | 2019-02-05 | First industry release of draft 2019 market modelling assumptions for consultation.
1.1 | 2019-09-03 | Updates based on 2019 Consultation feedback, updated information from stakeholders and 2019 forecasting components.
1.2 | 2019-09-13 | Revisions based on feedback from publication of 1.1
1.3 | 2019-12-12 | Issued to accompany Draft ISP publication
1.4 | 2020-04-17 | Updates following Draft ISP publication feedback
1.5 | 2020-07-30 | Issued to accompany 2020 ISP publication
2 | 2020-09-01 | Issued to accompany 2020 ESOO
2.1 | 2020-11-27 | Revisions to 2020 ESOO assumptions - error corrections and clarifications
2.2 | 2020-12-11 | Revisions to 2020 ESOO assumptions - error corrections and clarifications
3 | 2020-12-11 | Issued to accompany Draft 2021 IASR
3.1 | 2021-07-31 | Released to accompany the release of the Final 2021 IASR Report
3.2 | 2021-08-10 | Minor corrections of prior release.
3.3 | 2021-12-10 | Issued to accompany Draft 2022 ISP publication
3.4 | 2022-06-30 | Issued to accompany Final 2022 ISP publication
3.5 | 2022-08-31 | Issued to accompany 2022 ESOO
4 | 2022-12-16 | Issued to accompany Draft 2023 IASR publication
5 | 2023-07-28 | 2023 IASR Assumptions Workbook
5.1 | 2023-08-07 | Minor corrections of prior release.
5.2 | 2023-09-05 | Minor updates of prior release.
5.3 | 2023-12-15 | Minor updates of prior release.
6 | 2024-07-19 | 2024 ISP Assumptions Workbook
Worksheet Descriptions
Worksheet | Assumptions Grouping | Description | Source
Scenarios | Scenario and REZ settings | Summary of scenario dimensions and parameters | AEMO
Renewable Energy Zones |  | Renewable Energy Zones | AEMO
Existing Gen Data Summary | Summaries | Summary (calculated) of the generator technical data | Calculated data
New Entrant Data Summary |  | Summary (calculated) of the new entrant's technical data
Fuel Price Summary |  | Summary (calculated) of generator fuel costs
Regional Build Costs Summary |  | Summary (calculated) of regional build costs for a selectable scenario / technology.
Summary Mapping |  | Master Look up table for generator and storage assets
Energy Policy Targets | Policy settings | Target renewable settings for the Queensland, Victorian,Tasmanian and New South Wales Renewable Energy Targets | Queensland public policy documents, Victorian, Tasmanian and New South Wales legislation
Carbon Budgets |  | Global mean temperature increases by 2100 aligned with each scenario, and cumulative carbon budgets over the period to 2050. | CSIRO/CWA Multi-sector energy modelling (2022)
Demand and Energy Forecasts | Demand | Electricity consumption forecasts | AEMO forecasts (ESOO 2022), BIS Oxford Economics, 2022 Macroeconomic projections report, CSIRO DER and EV and GEM DER forecasts (2022), CSIRO/CWA Multi-sector energy modelling (2022), CSIRO, 2022 Electric Vehicles Forecasts Report
Economic Growth Forecasts |  | Forecast of broader economic growth (GSP)
Energy Efficiency |  | Forecast of energy efficiency impact on annual consumption forecasts
Rooftop PV |  | Rooftop PV capacity and generation forecast
PVNSG |  | PV non-scheduled generation (PVNSG) capacity and generation forecast
DSP |  | Demand side participation forecast
Battery & Plug-in EVs |  | Battery and plug-in electric vehicles uptake, energy, and charge profile forecast
EV V2G |  | Vehicle to Grid battery characteristics
Fuel cell EVs |  | Fuel cell electric vehicles uptake
Electrification |  | Electrification in all sectors including transportation
Embedded energy storages |  | Embedded consumer energy storage (battery) forecast
Aggregated energy storages |  | The 'aggregated' share of embedded energy storages that is modelled like a Virtual Power Plant (VPP).
Sub-regional demand allocation |  | Details of the sub-regional allocation of CER components.
Network Representation | Interconnector and transmission settings | Description of how the network is modelled in the capacity expansion models. | AEMO (Following consultation on IASR)
Network Capability |  | Maximum forward and reverse flow path capability for capacity expansion modelling. | AEMO (Review by TNSPs and consultation via IASR) AEMO NEM public data
Network losses |  | Proportion of interconnector losses applied to regional reference nodes and loss equations. | Marginal Loss Factors: Financial Year 2023-24
Flow Path Augmentation options |  | Capability, cost and timing for flow path augmentation options. | AEMO (Following consultation on IASR and Transmission Cost Report)
Transmission Reliability |  | Defines the outage rates modelled to key flowpaths in the ESOO. | AEMO internal study
Connection Costs forecast | Transmission costs forecasts | Forecast of transmission connection cost | AEMO internal study
REZ Costs forecast |  | Forecast of REZ augmentation cost | AEMO internal study
Flow Path costs forecast |  | Forecast of transmission flow path cost | AEMO internal study
Maximum capacity | Generator reliability settings | Installed capacity of existing, committed and anticipated generators. | AEMO Generation Information (July 2023 release)
Seasonal ratings |  | Winter and summer ratings for existing, committed, advanced and new entrant generators | AEMO Generation Information (July 2023 release), GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review,
Reserves |  | Minimum reserve levels for reliable regional supply | AEMO Generation Information (July 2023 release)
Generation limits |  | Generator operating limits | AEMO internal study, Aurecon, 2022 AEMO costs and technical parameter review
Maintenance |  | The percentage of time per year that a generator is expected to be out of service for maintenance. De-rating applied to generators under maintenance, staged construction or to track age-related degradation | GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review, AEMO Internal study
Generator Reliability Settings |  | Defines a generators' forced outage rate, mean time to repair after an outage, and the derating experienced during a partial outage | GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review, AEMO Internal study, AEMO data (ESOO 2022)
Hydro Climate Factor |  | Hydro inflow adjustments to capture climate risks | AEMO internal study; BoM & CSIRO: Electricity Sector Climate Information Project
Hydro Scheme Inflows |  | Monthly aggregated inflow trends for reference years | AEMO internal study and Hydro operators
Build costs | Generator technical and financial settings | Capital Cost projections for new entrant generators | Entura, 2018, Pumped hydro cost modelling CSIRO, GenCost 2022-23
Locational Cost Factors |  | Locational cost factors provide an indication of the variation in new entrants generators cost based on the shift in labour, equipment and shipping/delivery cost between regions. | GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review, AEMO Internal study
Connection cost |  | Cost to connect different generation technologies. | AEMO internal study
Build limits |  | Modelled limitations impacting build constraints within the expansion modelling | AEMO internal study
Build limits - PHES |  | Modelled limitations for PHES impacting build constraints within the expansion modelling | Entura, 2018, Pumped hydro cost modelling, AEMO internal study
REZ Augmentations Options |  | Capability, cost and timing for REZ augmentation options. | AEMO internal study AEMO, 2021 Transmission Cost Report
Non-REZ Assumptions |  | Summary of assumptions for non-rez locations | AEMO internal study
Power System Constraints |  | Reflect power system constraints to reflect secure operating limits | AEMO internal study
Capacity Factors |  | Capacity factors for renewable generators in the renewable energy zones | DNVGL, AEMO analysis outcomes
Lead time and project life |  | Modelled limitations impacting build timings within the expansion modelling | GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review, Hydro Tas, for pumped hydro economic life.
Financial parameters |  | Financial parameters (discount rate, weighted average cost of capital, value of customer reliability) used during cost benefit analysis | AEMO internal analysis, AER Rate of return - Annual Update - December 2020 AER, Values of Customer Reliability, December 2019 Synergies Economic Consulting, Updating the 2022 ISP Discount rate Oxford Economics Australia, Cost of Capital Survey 2023
Storage properties |  | Battery storage to power ratio and round-trip efficiency | Aurecon, 2022 AEMO costs and technical parameter review, CSIRO, Small-scale solar and battery projections 2022, Snowy Hydro Hydro Tasmania QLD QEJP, Queensland SuperGrid Infrastructure Blueprint Kidston Pumped Storage Hydro Project Financial Close Report August 2021
Coal and Biomass price |  | Coal fuel price for each coal generator | Wood Mackenzie, 2021 Coal price forecast, Oxford Economics Australia, 2022-23 Commodities Scenario Forecasts Report, AEMO internal study
Gas, Liquid fuel, H2 price |  | Fuel price for each gas and liquid fuel generator | ACIL Allen, 2023 Gas Price Forecasts, ACIL Allen, 2014 liquid fuel and technical cost review, Multi-sector Modelling, 2022 CSIRO/CWA
Retirement |  | Announced and end-of-technical-life generator retirement | AEMO Generation Information (July 2023 release), GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review QEJP, 2022 Queensland SuperGrid Infrastructure Blueprint
Heat rates |  | Efficiency of conversion of fuel to output for thermal generators | GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review
Auxiliary |  | Auxiliary (self) load for each generator or generator class | Aurecon, 2022 AEMO costs and technical parameter review, Hydro Tasmania, AEMO Internal study
Fixed OPEX |  | Fixed operating cost regardless of output for each generator or generator class | GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review, Entura, 2018 Pumped hydro cost modelling, Generator owner provided inputs
Variable OPEX |  | Variable operating cost per MWh of output for each generator or generator class | GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review, Generator owner provided inputs
Emissions intensity |  | Emissions production per MWh of output for each generator or generator class | CER - Greenhouse and energy information by designated generation facility 2021-22, GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO Costs and Technical Parameter Review, DCCEEW, 2022 Australian National Greenhouse Accounts Factors, AEMO Internal study
H2 GPG_emissions reduction |  | Factors projecting emissions reduction from GPG due to blending of hydrogen | CSIRO/CWA Multi-sector energy modelling (2022), AEMO internal study
GPG emissions reduction - BioM |  | Factors projecting emissions reduction from GPG due to blending of biomethane into fuel gas | CSIRO/CWA Multi-sector energy modelling (2022), AEMO internal study
Marginal Loss Factors |  | Marginal loss factors for each generator | Regions and Marginal Loss Factors: FY 2022-23 (2022 July release)
Affine Heat Rates | ST model properties | Heat rate curves for large thermal units | GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO costs and technical parameter review, AEMO Internal study
Max Ramp Rates |  | Maximum rates of change for thermal unit output up and down | GHD, 2018 AEMO costs and technical parameter review, Aurecon, 2022 AEMO Costs and Technical Parameter Review, AEMO Internal study
CCGT Unit Max Capacity |  | Maximum capacity of CCGT gas and steam turbines | AEMO Generation Information (July 2022 release)
GPG Min Stable Level |  | Minimum operating levels for large GPG units | Aurecon, 2022 AEMO Costs and Technical Parameter Review, AEMO Internal study
Min Up&Down Times |  | Minimum time online or offline for large GPG units | ACIL Allen, 2014 AEMO Fuel and Technology Cost Review, AEMO internal study
Costs Summary - PEM | Hydrogen properties | Locational cost factors for each cost region and regional cost summary for hydrogen technologies | Aurecon, 2022 AEMO costs and technical parameter review, GHD, 2018 AEMO costs and technical parameter review.
Build Costs - PEM |  | Costs to construct various hydrogen technologies | Aurecon, 2022 AEMO costs and technical parameter review, CSIRO, GenCost 2022-23
Hydrogen demand - Domestic |  | Projections of domestic hydrogen demand | CSIRO/CWA Multi-sector energy modelling (2022), Stakeholder engagement, including a targeted hydrogen workshop on Friday 18/09/2020
Hydrogen monthly profiles |  | Projections of monthly profiles of domestic hydrogen demand | CSIRO/CWA Multi-sector energy modelling (2022), AEMO internal study
Hydrogen demand_Export&Steel |  | Projections of demand for export hydrogen and green steel production | CSIRO/CWA Multi-sector energy modelling (2022)), Stakeholder engagement, including a targeted hydrogen workshop on Friday 18/09/2020
Hydrogen export ports |  | Location of hydrogen export ports for the Hydrogen Export scenario | ARUP, 2019, Australian Hydrogen Hubs Study, AEMO internal study
Other hydrogen assumptions |  | Various hydrogen-related assumptions | Aurecon, 2021-22 and 2022 AEMO costs and technical parameter review, CSIRO, National Hydrogen Roadmap (2018), Kopp et al. (2017), Energiepark Mainz: Technical and economic analysis of the worldwide largest Power-to-Gas plant with PEM electrolysis, Stakeholder engagement
Supporting Materials
Source | Materials
Aurecon, 2022 AEMO Costs and Technical Parameter Review | https://aemo.com.au/consultations/current-and-closed-consultations/2023-inputs-assumptions-and-scenarios
BIS Oxford Economics, 2022 Macroeconomic Projections Report
BIS Oxford Economics, 2022 Commodities Scenario Forecast Report
CSIRO, Draft GenCost 2022-23 Report
CSIRO, 2022 Electric Vehicle Projections Report
CSIRO/CWA, Multi-sector energy modelling (2022)
CSIRO, 2022 Solar PV and Battery Projections Report
Entura, 2018 Pumped hydro cost modelling
GEM, 2022 Solar PV and Battery Projections Report
Lewis Grey Advisory, 2023 gas price projections
Synergies Economic Consulting, 2021 Discount Rate report
Synergies Economic Consulting, Updating the 2022 ISP Discount Rate
AEMO, Generator information (November 2022 release) | https://www.aemo.com.au/energy-systems/electricity/national-electricity-market-nem/nem-forecasting-and-planning/forecasting-and-planning-data/generation-information
AEMO, Transmission Cost Database | https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation
AEMO, 2023 Transmission Expansion Options Report | https://aemo.com.au/consultations/current-and-closed-consultations/2023-transmission-expansion-options-report-consultation
ACIL Allen, 2014 Fuel and Technology Cost Review | https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/ntndp/2014/data-sources/fuel_and_technology_cost_review_report_acil_allen.pdf
AEMO, 2020 GSOO stakeholder surveys and gas supply input data | 2020 Gas Statement of Opportunities supply input data files. Available at: https://www.aemo.com.au/-/media/files/gas/national_planning_and_forecasting/gsoo/2020/2020-gsoo-supply-input-data-files.zip?la=en
AEP Elical, 2020 Assessment of Ageing Coal-Fired Generation Reliability | https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/inputs-assumptions-methodologies/2020/aep-elical-assessment-of-ageing-coal-fired-generation-reliability.pdf?la=en
CSIRO, 2018 National Hydrogen Roadmap, Pathways to an economically sustainable hydrogen industry in Australia | https://www.csiro.au/en/Showcase/Hydrogen
Energiepark Mainz, 2017 Technical and economic analysis of the worldwide largest Power-to-Gas plant with PEM electrolysis | https://doi.org/10.1016/j.ijhydene.2016.12.145
GHD, 2018 AEMO costs and technical parameter review | https://www.aemo.com.au/consultations/current-and-closed-consultations/2021-Planning-and-Forecasting-Consultation-on-Inputs-Assumptions-and-Scenarios
Powerlink, Prepatory Activities | https://aemo.com.au/en/energy-systems/major-publications/integrated-system-plan-isp/2022-integrated-system-plan-isp/current-inputs-assumptions-and-scenarios
Wood Mackenzie, 2021 Coal Cost Report | https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/isp/2021/wood-mackenzie-2021-final-coal-price-forecast.pdf?la=en

## Scenarios
Go to Assumptions Summary
Summary of scenario parameters
Summary of parameters for scenarios in the 2023 IASR and 2024 ISP.
Parameter | Green Energy Exports | Step Change | Progressive Change
National decarbonisation targets
National Decarbonisation target | At least 43% emissions reduction by 2030.​ Net zero by 2050. | At least 43% emissions reduction by 2030.​ Net zero by 2050. | 43% emissions reduction by 2030.​ Net zero by 2050.
Demand drivers
Global economic growth and policy coordination​ | High economic growth, stronger coordination​ | Moderate economic growth, stronger coordination​ | Slower economic growth, lesser coordination​
Australian economic and demographic drivers​ | Higher (partly driven by green energy)​ | Moderate​ | Lower​
Energy Efficiency | Higher​ | Moderate | Lower​
Consumer engagement​ e.g. VPP and DSP uptake | Higher​ | High (VPP) and Moderate (DSP) | Lower​
CER uptake
CER uptake (i.e. batteries, PV and EVs)​ | Higher​ | High | Lower​
Hydrogen and Biomethane
Hydrogen​ use | Faster cost reduction. High production for domestic and export use | Medium-Low production for domestic use, with minimal export hydrogen. | Low production for domestic use, with no export hydrogen.
Hydrogen blending in gas distribution network * | Up to 10% vol | Up to 10% vol | Up to 10% vol
Biomethane/ synthetic methane | Allowed, but no specific targets to introduce it | Allowed, but no specific targets to introduce it | Allowed, but no specific targets to introduce it
Scenario alignment
Global/domestic temperature settings and outcomes | Applies RCP 1.9 where relevant (~ 1.5°C) | Applies RCP 2.6 where relevant (~ 1.8°C) | Applies RCP 4.5 where relevant (~ 2.6°C)
IEA 2021 World Energy Outlook scenario | Net Zero by 2050 (NZE) | Sustainable Development Scenario (SDS) | Stated Policy Scenario (STEPS)
Build cost trajectories
Generator and storage build costs | CSIRO GenCost NZE by 2050 | CSIRO GenCost NZE post 2050 | CSIRO GenCost Current Policies
Fuel price settings
Gas prices | ACIL Allen (2023), Green Energy Exports | ACIL Allen (2023), Step Change | ACIL Allen (2023), Progressive Change
Coal prices | Wood Mackenzie (2021) & Oxford Economics Australia (2022): Low price | Wood Mackenzie (2021) & Oxford Economics Australia (2022): Central | Wood Mackenzie (2021) & Oxford Economics Australia (2022): High price
Gas Market Settings **
New gas supplies | As forecast in AEMO's 2023 GSOO
All other gas market settings | Consistent with AEMO's 2023 GSOO Green Energy Exports scenario | Consistent with AEMO's 2023 GSOO Orchestrated Step Change scenario | Consistent with AEMO's 2023 GSOO Progressive Change scenario
* Hydrogen blending into the gas distribution network will need to accommodate the technical requirements of distribution pipelines, as well as the capabilities of connected gas appliances.
** Gas Market Settings will be updated in March 2024 for the 2024 GSOO.
360
290
650
540

## Renewable Energy Zones
Go to Assumptions Summary
Candidate Renewable Energy Zones | [5 empty] | Renewable Energy Zone Map | NEM Regional Cost Zone Map
List of Candidate Renewable Energy Zones (REZs) by NEM region and zone
Build cost at each REZ that reflects the NEM regional cost zone map
A KMZ file with the REZ boundaries is available at https://aemo.com.au/consultations/current-and-closed-consultations/2023-inputs-assumptions-and-scenarios
ID | Name | NEM Region | NTNDP Zone | ISP Sub-region | Regional Cost Zones
Q1 | Far North QLD | QLD | NQ | NQ | Low1
Q2 | North Qld Clean Energy Hub | QLD | NQ | NQ | Low1
Q3 | Northern Qld | QLD | NQ | NQ | Low
Q4 | Isaac | QLD | NQ | CQ | Low1
Q5 | Barcaldine | QLD | CQ | CQ | Medium
Q6 | Fitzroy | QLD | CQ | CQ | Low
Q7 | Wide Bay | QLD | CQ | SQ | Low1
Q8 | Darling Downs | QLD | SWQ | SQ | Low1
Q9 | Banana | QLD | CQ | CQ | Medium
N1 | North West NSW | NSW | NNS | NNSW | Medium
N2 | New England | NSW | NNS | NNSW | Low
N3 | Central-West Orana | NSW | NCEN | CNSW | Medium
N4 | Broken Hill | NSW | SWNSW | SNSW | High3
N5 | South West NSW | NSW | SWNSW | SNSW | High
N6 | Wagga Wagga | NSW | SWNSW | SNSW | Medium1
N7 | Tumut | NSW | CAN | SNSW | Medium
N8 | Cooma-Monaro | NSW | CAN | SNSW | Medium
N9 | Hunter-Central Coast | NSW | NCEN | CNSW | Low4
N10 | Hunter Coast | NSW | NCEN | SNW | Low
N11 | Illawarra Coast | NSW | NCEN | SNW | Low
N12 | Illawarra | NSW | NCEN | SNW | Low
V1 | Ovens Murray | VIC | NVIC | VIC | Medium2
V2 | Murray River | VIC | NVIC | VIC | Medium1
V3 | Western Victoria | VIC | CVIC | VIC | Medium2
V4 | South West Victoria | VIC | MEL | VIC | Medium2
V5 | Gippsland | VIC | LV | VIC | Low1
V6 | Central North Vic | VIC | NVIC | VIC | High
V7 | Gippsland Coast | VIC | LV | VIC | Low6
V8 | Southern Ocean | VIC | MEL | VIC | Low
S1 | South East SA | SA | SESA | SESA | Low1
S2 | Riverland | SA | NSA | CSA | Low
S3 | Mid-North SA | SA | NSA | CSA | Low1
S4 | Yorke Peninsula | SA | NSA | CSA | Low
S5 | Northern SA | SA | NSA | CSA | Medium | Note: † The REZ boundaries for N5 and N9 are indicative and aligned with the New South Wales Government’s declaration for these REZs. ‡ The Illawarra REZ was formally declared by the Minister for Energy in New South Wales on 27 February 2023 . The REZ boundaries are aligned with the indicative geographical area defined in New South Wales Department of Planning, industry and Environment publication * AEMO has aligned the boundaries for the Gippsland Coast REZ to the area published in the Commonwealth Notice of proposal to declare an area – Bass Strait off Gippsland ** The Commonwealth Government formally declared the Pacific Ocean off the Hunter as the second area suitable for developing offshore wind energy projects. AEMO has aligned the boundaries for the Hunter Coast to the area published in Offshore renewable energy infrastructure area proposal: Pacific Ocean off Hunter. *** AEMO has updated the REZ boundary for T4 in alignment with the Bass Strait, Northern Tasmania proposed offshore REZ. At: https://consult.dcceew.gov.au/oei-bass-strait. **** V8 renamed from 'Portland' to 'Southern Ocean' and boundaries updated as per Federal Government announcements in March 2024 (https://www.dcceew.gov.au/energy/renewable/offshore-wind/areas/southern-ocean-region). | Note: * Not all costs are homogenous under each category zone. Regional factors result in variances amongst each category. ** Central North VIC costs increased to "High" category based on feedback to AEMO's 2020 Draft ISP and 2020 Inputs and Assumptions Consultation. A North VIC region was previously used in AEMO's National Transmission Network Development Project (NTNDP), which is not visible on the map.
S6 | Leigh Creek | SA | NSA | CSA | Medium1
S7 | Roxby Downs | SA | NSA | CSA | Medium1
S8 | Eastern Eyre Peninsula | SA | NSA | CSA | Medium
S9 | Western Eyre Peninsula | SA | NSA | CSA | Medium
S10 | South East SA Coast | SA | SESA | SESA | Low
T1 | North East Tasmania | TAS | TAS | TAS | Low1
T2 | North West Tasmania | TAS | TAS | TAS | Medium2
T3 | Central Highlands | TAS | TAS | TAS | Low1
T4 | North Tasmania Coast | TAS | TAS | TAS | Low
Note:
1. When a REZ zone covers two regional cost zones, the lower cost zone is utilised.
2. When a REZ zone covers all three regional cost zones, the medium cost zone is utilised.
3. When a REZ zone crosses state borders, the regional cost zones from the NEM Region of the REZ are utilised.
4.A new candidate REZ – Hunter-Central Coast REZ – has been added to assess the benefits of this new zone. The REZ boundaries are aligned with the indicative geographical area defined in Schedule 1 of the draft Hunter-Central Coast REZ declaration
5. The Queensland Government released its draft REZ roadmap in July 2023, nominating 12 potential future REZs across the southern, central and northern Queenland REZs. Broadly, Northern QREZ includes Q1, Q2, Q3, Q4 and Q5; Central QREZ includes Q6, Q7 and Q9; Southern QREZ includes Q8. AEMO will engage with the Queensland Governnment as the roadmap is devleoped.
6. All offshore wind zones are specified as having a low locational cost factor. The factors which drive the different cost factors for onshore REZs are not relevant for offshore wind, where the base costs are inherently for typical offshore locations.
7. V8 'Portland' renamed to 'Southern Ocean' to align with governments' references and naming.

## New Entrant Data Summary
Go to Assumptions Summary
Generator Summary - New Entrants
Notes
1. Fuel costs represent the selected Scenario in cell T10 on the Fuel Price summary sheet and the selected year in cell T11.
2. Build cost are for the selected scenario (cell L10) and the selected year (cell L11).
3.Emissions for all gas based generators are dependent on the blending biomethane into the gas network , the values presented here are for a 100% gas operation.
New entrant generators
Technology type | Fuel type | Region | ISP sub-region | REZ location | Cost zone | Seasonal rating |  |  | Maintenance | Equivalent average days per year on planned outage | Build cost ($/kW) | Connection cost ($/kW) | Total lead time (years) | Economic life (years) | Technical life (years) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate (GJ/MWh HHV s.o.) | Fuel cost ($/GJ)1 | Emissions (kg/MWh) | Auxiliary load (%) | SRMC ($/MWh)
[6 empty] | Summer Peak (% of nameplate) | Summer Typical (% of nameplate) | Winter (% of nameplate) |  |  | Green Energy Exports | [7 empty] | Green Energy Exports | Green Energy Exports
[9 empty] | % of time out |  | 2022-23 | [7 empty] | 2047-48 | 2051-52
OCGT (small GT) | Gas | QLD | NQ | N/A | QLD Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 110.4943 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 16.9304 | 248.8123 | 1.7 | 185.356
OCGT (small GT) | Gas | QLD | CQ | N/A | QLD Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 110.4943 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 16.9304 | 248.8123 | 1.7 | 185.356
OCGT (small GT) | Gas | QLD | GG | N/A | QLD Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 110.4943 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 16.9304 | 248.8123 | 1.7 | 185.356
OCGT (small GT) | Gas | QLD | SQ | N/A | QLD Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 110.4943 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 16.9304 | 248.8123 | 1.7 | 185.356
OCGT (small GT) | Gas | NSW | NNSW | N/A | NSW Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 85.544 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 17.4592 | 248.8123 | 1.7 | 190.7453
OCGT (small GT) | Gas | NSW | CNSW | N/A | NSW Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 85.544 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 17.4592 | 248.8123 | 1.7 | 190.7453
OCGT (small GT) | Gas | NSW | SNW | N/A | NSW Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 85.544 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 17.4592 | 248.8123 | 1.7 | 190.7453
OCGT (small GT) | Gas | NSW | SNSW | N/A | NSW Medium | 97.7017 | 100 | 100 | 0.82192 | 3 | 1672.1251 | 85.544 | 4 | 25 | 40 | 14.551 | 13.8581 | 10.1902 | 17.4592 | 248.8123 | 1.7 | 191.7718
OCGT (small GT) | Gas | VIC | VIC | N/A | VIC Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 115.4844 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 16.7312 | 248.8123 | 1.7 | 183.3263
OCGT (small GT) | Gas | SA | CSA | N/A | SA Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 110.4943 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 16.983 | 248.8123 | 1.7 | 185.8927
OCGT (small GT) | Gas | SA | SESA | N/A | SA Medium | 97.7017 | 100 | 100 | 0.82192 | 3 | 1636.3809 | 110.4943 | 4 | 25 | 40 | 15.09 | 14.3714 | 10.1902 | 16.983 | 248.8123 | 1.7 | 187.4325
OCGT (small GT) | Gas | TAS | TAS | N/A | TAS Low | 97.7017 | 100 | 100 | 0.82192 | 3 | 1602.8807 | 115.4844 | 4 | 25 | 40 | 13.4732 | 12.8316 | 10.1902 | 17.1564 | 248.8123 | 1.7 | 187.6594
OCGT (large GT) | Gas | QLD | NQ | N/A | QLD Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 110.4943 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 16.9304 | 266.9053 | 1.1 | 192.8759
OCGT (large GT) | Gas | QLD | CQ | N/A | QLD Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 110.4943 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 16.9304 | 266.9053 | 1.1 | 192.8759
OCGT (large GT) | Gas | QLD | GG | N/A | QLD Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 110.4943 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 16.9304 | 266.9053 | 1.1 | 192.8759
OCGT (large GT) | Gas | QLD | SQ | N/A | QLD Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 110.4943 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 16.9304 | 266.9053 | 1.1 | 192.8759
OCGT (large GT) | Gas | NSW | NNSW | N/A | NSW Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 85.544 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 17.4592 | 266.9053 | 1.1 | 198.657
OCGT (large GT) | Gas | NSW | CNSW | N/A | NSW Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 85.544 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 17.4592 | 266.9053 | 1.1 | 198.657
OCGT (large GT) | Gas | NSW | SNW | N/A | NSW Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 85.544 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 17.4592 | 266.9053 | 1.1 | 198.657
OCGT (large GT) | Gas | NSW | SNSW | N/A | NSW Medium | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1062.8008 | 85.544 | 4 | 25 | 40 | 11.7794 | 8.4304 | 10.9312 | 17.4592 | 266.9053 | 1.1 | 199.2815
OCGT (large GT) | Gas | VIC | VIC | N/A | VIC Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 115.4844 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 16.7312 | 266.9053 | 1.1 | 190.6986
OCGT (large GT) | Gas | SA | CSA | N/A | SA Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 110.4943 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 16.983 | 266.9053 | 1.1 | 193.4516
OCGT (large GT) | Gas | SA | SESA | N/A | SA Medium | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1041.0204 | 110.4943 | 4 | 25 | 40 | 12.2157 | 8.7426 | 10.9312 | 16.983 | 266.9053 | 1.1 | 194.3883
OCGT (large GT) | Gas | TAS | TAS | N/A | TAS Low | 86.3842 | 92.1887 | 98.5177 | 1.3699 | 5 | 1018.4334 | 115.4844 | 4 | 25 | 40 | 10.9069 | 7.8059 | 10.9312 | 17.1564 | 266.9053 | 1.1 | 195.3468
CCGT | Gas | QLD | NQ | N/A | QLD Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 110.4943 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 15.7488 | 173.5024 | 2.5 | 118.1229
CCGT | Gas | QLD | CQ | N/A | QLD Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 110.4943 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 15.7488 | 173.5024 | 2.5 | 118.1229
CCGT | Gas | QLD | GG | N/A | QLD Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 110.4943 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 15.7488 | 173.5024 | 2.5 | 118.1229
CCGT | Gas | QLD | SQ | N/A | QLD Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 110.4943 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 15.7488 | 173.5024 | 2.5 | 118.1229
CCGT | Gas | NSW | NNSW | N/A | NSW Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 85.544 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 16.1932 | 173.5024 | 2.5 | 121.3448
CCGT | Gas | NSW | CNSW | N/A | NSW Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 85.544 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 16.1932 | 173.5024 | 2.5 | 121.3448
CCGT | Gas | NSW | SNW | N/A | NSW Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 85.544 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 16.1932 | 173.5024 | 2.5 | 121.3448
CCGT | Gas | NSW | SNSW | N/A | NSW Medium | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1970.1508 | 85.544 | 5 | 25 | 40 | 12.5878 | 4.2729 | 7.2492 | 16.1932 | 173.5024 | 2.5 | 121.6613
CCGT | Gas | VIC | VIC | N/A | VIC Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 80.1975 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 15.6048 | 173.5024 | 2.5 | 117.0795
CCGT | Gas | SA | CSA | N/A | SA Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 110.4943 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 15.9975 | 173.5024 | 2.5 | 119.9259
CCGT | Gas | SA | SESA | N/A | SA Medium | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1927.851 | 110.4943 | 5 | 25 | 40 | 13.054 | 4.4312 | 7.2492 | 15.9975 | 173.5024 | 2.5 | 120.4006
CCGT | Gas | TAS | TAS | N/A | TAS Low | 87.2673 | 92.9095 | 97.5487 | 3.5068 | 12.8 | 1888.3838 | 115.4844 | 5 | 25 | 40 | 11.6554 | 3.9564 | 7.2492 | 16.0301 | 173.5024 | 2.5 | 120.162
CCGT with CCS | Gas | QLD | NQ | N/A | QLD Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 110.4943 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 15.7488 | 26.3912 | 9.2 | 148.8573
CCGT with CCS | Gas | QLD | CQ | N/A | QLD Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 110.4943 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 15.7488 | 26.3912 | 9.2 | 148.8573
CCGT with CCS | Gas | QLD | GG | N/A | QLD Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 110.4943 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 15.7488 | 26.3912 | 9.2 | 148.8573
CCGT with CCS | Gas | QLD | SQ | N/A | QLD Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 110.4943 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 15.7488 | 26.3912 | 9.2 | 148.8573
CCGT with CCS | Gas | NSW | NNSW | N/A | NSW Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 85.544 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 16.1932 | 26.3912 | 9.2 | 152.841
CCGT with CCS | Gas | NSW | CNSW | N/A | NSW Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 85.544 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 16.1932 | 26.3912 | 9.2 | 152.841
CCGT with CCS | Gas | NSW | SNW | N/A | NSW Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 85.544 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 16.1932 | 26.3912 | 9.2 | 152.841
CCGT with CCS | Gas | NSW | SNSW | N/A | NSW Medium | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4856.3943 | 85.544 | 6 | 25 | 40 | 18.8817 | 8.3149 | 8.9631 | 16.1932 | 26.3912 | 9.2 | 153.4569
CCGT with CCS | Gas | VIC | VIC | N/A | VIC Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 80.1975 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 15.6048 | 26.3912 | 9.2 | 147.5673
CCGT with CCS | Gas | SA | CSA | N/A | SA Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 110.4943 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 15.9975 | 26.3912 | 9.2 | 151.0866
CCGT with CCS | Gas | SA | SESA | N/A | SA Medium | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4750.7091 | 110.4943 | 6 | 25 | 40 | 19.581 | 8.6228 | 8.9631 | 15.9975 | 26.3912 | 9.2 | 152.0105
CCGT with CCS | Gas | TAS | TAS | N/A | TAS Low | 81.1854 | 85.9413 | 90.0714 | 3.5068 | 12.8 | 4655.7322 | 115.4844 | 6 | 25 | 40 | 17.4831 | 7.699 | 8.9631 | 16.0301 | 26.3912 | 9.2 | 151.3786
Biomass | Biomass | QLD | NQ | N/A | QLD Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 110.4943 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Biomass | Biomass | QLD | CQ | N/A | QLD Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 110.4943 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Biomass | Biomass | QLD | GG | N/A | QLD Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 110.4943 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Biomass | Biomass | QLD | SQ | N/A | QLD Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 110.4943 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Biomass | Biomass | NSW | NNSW | N/A | NSW Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 85.544 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Biomass | Biomass | NSW | CNSW | N/A | NSW Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 85.544 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Biomass | Biomass | NSW | SNW | N/A | NSW Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 85.544 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Biomass | Biomass | NSW | SNSW | N/A | NSW Medium | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8766.3914 | 85.544 | 6 | 30 | 50 | 174.3976 | 11.1558 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.9991
Biomass | Biomass | VIC | VIC | N/A | VIC Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 115.4844 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Biomass | Biomass | SA | CSA | N/A | SA Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 110.4943 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Biomass | Biomass | SA | SESA | N/A | SA Medium | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8613.2703 | 110.4943 | 6 | 30 | 50 | 180.8568 | 11.569 | 17.37 | 0.62425 | 20.844 | 7.3 | 22.4123
Biomass | Biomass | TAS | TAS | N/A | TAS Low | 94.9299 | 100 | 100 | 6.2466 | 22.8 | 8367.2725 | 115.4844 | 6 | 30 | 50 | 161.4793 | 10.3294 | 17.37 | 0.62425 | 20.844 | 7.3 | 21.1727
Large scale Solar PV | Solar | QLD | NQ | Far North QLD | QLD Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 253.67 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | QLD | NQ | North Qld Clean Energy Hub | QLD Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 297 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | QLD | NQ | Northern Qld | QLD Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 253.67 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | QLD | CQ | Isaac | QLD Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 250.33 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | QLD | CQ | Barcaldine | QLD Medium | 100 | 100 | 100 | 0 | 0 | 1790.0326 | 150 | 2 | 30 | 30 | 20.3595 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | QLD | CQ | Fitzroy | QLD Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 250.33 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | QLD | SQ | Wide Bay | QLD Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 113.33 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | QLD | SQ | Darling Downs | QLD Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 116.67 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | QLD | SQ | Banana | QLD Medium | 100 | 100 | 100 | 0 | 0 | 1790.0326 | 367 | 2 | 30 | 30 | 20.3595 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | NNSW | North West NSW | NSW Medium | 100 | 100 | 100 | 0 | 0 | 1788.3516 | 135 | 2 | 30 | 30 | 19.6323 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | NNSW | New England | NSW Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 135 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | CNSW | Central-West Orana | NSW Medium | 100 | 100 | 100 | 0 | 0 | 1788.3516 | 135 | 2 | 30 | 30 | 19.6323 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | SNSW | Broken Hill | NSW High | 100 | 100 | 100 | 0 | 0 | 1841.6374 | 176 | 2 | 30 | 30 | 21.2684 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | SNSW | South West NSW | NSW High | 100 | 100 | 100 | 0 | 0 | 1841.6374 | 135 | 2 | 30 | 30 | 21.2684 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | SNSW | Wagga Wagga | NSW Medium | 100 | 100 | 100 | 0 | 0 | 1788.3516 | 272 | 2 | 30 | 30 | 19.6323 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | SNSW | Tumut | NSW Medium | 100 | 100 | 100 | 0 | 0 | 1788.3516 | 100 | 2 | 30 | 30 | 19.6323 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | SNSW | Cooma-Monaro | NSW Medium | 100 | 100 | 100 | 0 | 0 | 1788.3516 | 100 | 2 | 30 | 30 | 19.6323 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | CNSW | Hunter-Central Coast | NSW Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 100 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | SNW | Illawarra | NSW Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 100 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | VIC | VIC | Ovens Murray | VIC Medium | 100 | 100 | 100 | 0 | 0 | 1714.3903 | 136 | 2 | 30 | 30 | 18.7234 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | VIC | VIC | Murray River | VIC Medium | 100 | 100 | 100 | 0 | 0 | 1714.3903 | 269 | 2 | 30 | 30 | 18.7234 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | VIC | VIC | Western Victoria | VIC Medium | 100 | 100 | 100 | 0 | 0 | 1714.3903 | 277 | 2 | 30 | 30 | 18.7234 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | VIC | VIC | South West Victoria | VIC Medium | 100 | 100 | 100 | 0 | 0 | 1714.3903 | 277 | 2 | 30 | 30 | 18.7234 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | VIC | VIC | Gippsland | VIC Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 340 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | VIC | VIC | Central North Vic | VIC High | 100 | 100 | 100 | 0 | 0 | 1713.0455 | 321 | 2 | 30 | 30 | 19.087 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | SA | SESA | South East SA | SA Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 287 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | SA | CSA | Riverland | SA Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 166.67 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | SA | CSA | Mid-North SA | SA Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 257 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | SA | CSA | Yorke Peninsula | SA Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 120 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | SA | CSA | Northern SA | SA Medium | 100 | 100 | 100 | 0 | 0 | 1773.8956 | 250.337 | 2 | 30 | 30 | 20.3595 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | SA | CSA | Leigh Creek | SA Medium | 100 | 100 | 100 | 0 | 0 | 1773.8956 | 153.33 | 2 | 30 | 30 | 20.3595 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | SA | CSA | Roxby Downs | SA Medium | 100 | 100 | 100 | 0 | 0 | 1773.8956 | 283.67 | 2 | 30 | 30 | 20.3595 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | SA | CSA | Eastern Eyre Peninsula | SA Medium | 100 | 100 | 100 | 0 | 0 | 1773.8956 | 283.67 | 2 | 30 | 30 | 20.3595 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | SA | CSA | Western Eyre Peninsula | SA Medium | 100 | 100 | 100 | 0 | 0 | 1773.8956 | 146.67 | 2 | 30 | 30 | 20.3595 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | TAS | TAS | North East Tasmania | TAS Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 410.33 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | TAS | TAS | North West Tasmania | TAS Medium | 100 | 100 | 100 | 0 | 0 | 1781.2917 | 377 | 2 | 30 | 30 | 19.8141 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | TAS | TAS | Central Highlands | TAS Low | 100 | 100 | 100 | 0 | 0 | 1697.749 | 357 | 2 | 30 | 30 | 18.1781 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | NSW | CNSW | New South Wales Non-REZ | NSW Medium | 100 | 100 | 100 | 0 | 0 | 1788.3516 | 367 | 2 | 30 | 30 | 19.6323 | 0 | 0 | 0 | 0 | 0.017458 | 0
Large scale Solar PV | Solar | VIC | VIC | Victoria Non-REZ | VIC Medium | 100 | 100 | 100 | 0 | 0 | 1714.3903 | 347 | 2 | 30 | 30 | 18.7234 | 0 | 0 | 0 | 0 | 0.017458 | 0
Solar Thermal (15hrs storage) | Solar | QLD | NQ | Far North QLD | QLD Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 253.67 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | QLD | NQ | North Qld Clean Energy Hub | QLD Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 297 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | QLD | NQ | Northern Qld | QLD Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 253.67 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | QLD | CQ | Isaac | QLD Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 250.33 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | QLD | CQ | Barcaldine | QLD Medium | 100 | 100 | 100 | 1.9178 | 7 | 7461.399 | 150 | 6 | 25 | 40 | 158.0853 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | QLD | CQ | Fitzroy | QLD Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 250.33 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | QLD | SQ | Wide Bay | QLD Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 113.33 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | QLD | SQ | Darling Downs | QLD Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 116.67 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | QLD | SQ | Banana | QLD Medium | 100 | 100 | 100 | 1.9178 | 7 | 7461.399 | 367 | 6 | 25 | 40 | 158.0853 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | NNSW | North West NSW | NSW Medium | 100 | 100 | 100 | 1.9178 | 7 | 7395.1157 | 135 | 6 | 25 | 40 | 152.4394 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | NNSW | New England | NSW Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 135 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | CNSW | Central-West Orana | NSW Medium | 100 | 100 | 100 | 1.9178 | 7 | 7395.1157 | 135 | 6 | 25 | 40 | 152.4394 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | SNSW | Broken Hill | NSW High | 100 | 100 | 100 | 1.9178 | 7 | 7787.2334 | 176 | 6 | 25 | 40 | 165.1427 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | SNSW | South West NSW | NSW High | 100 | 100 | 100 | 1.9178 | 7 | 7787.2334 | 135 | 6 | 25 | 40 | 165.1427 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | SNSW | Wagga Wagga | NSW Medium | 100 | 100 | 100 | 1.9178 | 7 | 7395.1157 | 272 | 6 | 25 | 40 | 152.4394 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | SNSW | Tumut | NSW Medium | 100 | 100 | 100 | 1.9178 | 7 | 7395.1157 | 100 | 6 | 25 | 40 | 152.4394 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | SNSW | Cooma-Monaro | NSW Medium | 100 | 100 | 100 | 1.9178 | 7 | 7395.1157 | 100 | 6 | 25 | 40 | 152.4394 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | CNSW | Hunter-Central Coast | NSW Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 100 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | SNW | Illawarra | NSW Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 100 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | VIC | VIC | Ovens Murray | VIC Medium | 100 | 100 | 100 | 1.9178 | 7 | 7162.7756 | 136 | 6 | 25 | 40 | 145.382 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | VIC | VIC | Murray River | VIC Medium | 100 | 100 | 100 | 1.9178 | 7 | 7162.7756 | 269 | 6 | 25 | 40 | 145.382 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | VIC | VIC | Western Victoria | VIC Medium | 100 | 100 | 100 | 1.9178 | 7 | 7162.7756 | 277 | 6 | 25 | 40 | 145.382 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | VIC | VIC | South West Victoria | VIC Medium | 100 | 100 | 100 | 1.9178 | 7 | 7162.7756 | 277 | 6 | 25 | 40 | 145.382 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | VIC | VIC | Gippsland | VIC Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 340 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | VIC | VIC | Central North Vic | VIC High | 100 | 100 | 100 | 1.9178 | 7 | 7277.8991 | 321 | 6 | 25 | 40 | 148.205 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | SA | SESA | South East SA | SA Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 287 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | SA | CSA | Riverland | SA Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 166.67 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | SA | CSA | Mid-North SA | SA Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 257 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | SA | CSA | Yorke Peninsula | SA Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 120 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | SA | CSA | Northern SA | SA Medium | 100 | 100 | 100 | 1.9178 | 7 | 7450.2355 | 250.337 | 6 | 25 | 40 | 158.0853 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | SA | CSA | Leigh Creek | SA Medium | 100 | 100 | 100 | 1.9178 | 7 | 7450.2355 | 153.33 | 6 | 25 | 40 | 158.0853 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | SA | CSA | Roxby Downs | SA Medium | 100 | 100 | 100 | 1.9178 | 7 | 7450.2355 | 283.67 | 6 | 25 | 40 | 158.0853 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | SA | CSA | Eastern Eyre Peninsula | SA Medium | 100 | 100 | 100 | 1.9178 | 7 | 7450.2355 | 283.67 | 6 | 25 | 40 | 158.0853 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | SA | CSA | Western Eyre Peninsula | SA Medium | 100 | 100 | 100 | 1.9178 | 7 | 7450.2355 | 146.67 | 6 | 25 | 40 | 158.0853 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | TAS | TAS | North East Tasmania | TAS Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 410.33 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | TAS | TAS | North West Tasmania | TAS Medium | 100 | 100 | 100 | 1.9178 | 7 | 7390.2317 | 377 | 6 | 25 | 40 | 153.8509 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | TAS | TAS | Central Highlands | TAS Low | 100 | 100 | 100 | 1.9178 | 7 | 6977.1825 | 357 | 6 | 25 | 40 | 141.1476 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | NSW | CNSW | New South Wales Non-REZ | NSW Medium | 100 | 100 | 100 | 1.9178 | 7 | 7395.1157 | 367 | 6 | 25 | 40 | 152.4394 | 0 | 0 | 0 | 0 | 10 | 0
Solar Thermal (15hrs storage) | Solar | VIC | VIC | Victoria Non-REZ | VIC Medium | 100 | 100 | 100 | 1.9178 | 7 | 7162.7756 | 347 | 6 | 25 | 40 | 145.382 | 0 | 0 | 0 | 0 | 10 | 0
Battery Storage (1hr storage) | Battery | QLD | NQ | N/A | QLD Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 103.3657 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | QLD | CQ | N/A | QLD Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 103.3657 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | QLD | GG | N/A | QLD Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 103.3657 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | QLD | SQ | N/A | QLD Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 103.3657 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | NSW | NNSW | N/A | NSW Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 77.5242 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | NSW | CNSW | N/A | NSW Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 77.5242 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | NSW | SNW | N/A | NSW Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 77.5242 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | NSW | SNSW | N/A | NSW Medium | 100 | 100 | 99.9494 | 0 | 0 | 1038.8233 | 77.5242 | 2 | 20 | 20 | 8.1994 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | VIC | VIC | N/A | VIC Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 106.93 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | SA | CSA | N/A | SA Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 103.3657 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | SA | SESA | N/A | SA Medium | 100 | 100 | 99.9494 | 0 | 0 | 1022.3973 | 103.3657 | 2 | 20 | 20 | 8.5031 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | Battery | TAS | TAS | N/A | TAS Low | 100 | 100 | 99.9494 | 0 | 0 | 995.5183 | 106.93 | 2 | 20 | 20 | 7.592 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | QLD | NQ | N/A | QLD Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 103.3657 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | QLD | CQ | N/A | QLD Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 103.3657 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | QLD | GG | N/A | QLD Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 103.3657 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | QLD | SQ | N/A | QLD Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 103.3657 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | NSW | NNSW | N/A | NSW Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 77.5242 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | NSW | CNSW | N/A | NSW Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 77.5242 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | NSW | SNW | N/A | NSW Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 77.5242 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | NSW | SNSW | N/A | NSW Medium | 100 | 100 | 99.8476 | 0 | 0 | 1505.6285 | 77.5242 | 2 | 20 | 20 | 11.6639 | 0 | 0 | 0 | 0 | 0 | 0
Battery storage (2hrs storage) | Battery | VIC | VIC | N/A | VIC Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 106.93 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | SA | CSA | N/A | SA Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 103.3657 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | SA | SESA | N/A | SA Medium | 100 | 100 | 99.8476 | 0 | 0 | 1488.5011 | 103.3657 | 2 | 20 | 20 | 12.0959 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | Battery | TAS | TAS | N/A | TAS Low | 100 | 100 | 99.8476 | 0 | 0 | 1439.2778 | 106.93 | 2 | 20 | 20 | 10.7999 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | QLD | NQ | N/A | QLD Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 103.3657 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | QLD | CQ | N/A | QLD Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 103.3657 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | QLD | GG | N/A | QLD Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 103.3657 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | QLD | SQ | N/A | QLD Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 103.3657 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | NSW | NNSW | N/A | NSW Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 77.5242 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | NSW | CNSW | N/A | NSW Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 77.5242 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | NSW | SNW | N/A | NSW Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 77.5242 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | NSW | SNSW | N/A | NSW Medium | 100 | 100 | 99.8975 | 0 | 0 | 2455.1547 | 77.5242 | 3 | 20 | 20 | 18.7085 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | VIC | VIC | N/A | VIC Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 106.93 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | SA | CSA | N/A | SA Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 103.3657 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | SA | SESA | N/A | SA Medium | 100 | 100 | 99.8975 | 0 | 0 | 2448.8493 | 103.3657 | 3 | 20 | 20 | 19.4014 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | Battery | TAS | TAS | N/A | TAS Low | 100 | 100 | 99.8975 | 0 | 0 | 2335.3512 | 106.93 | 3 | 20 | 20 | 17.3227 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | QLD | NQ | N/A | QLD Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 103.3657 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | QLD | CQ | N/A | QLD Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 103.3657 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | QLD | GG | N/A | QLD Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 103.3657 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | QLD | SQ | N/A | QLD Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 103.3657 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | NSW | NNSW | N/A | NSW Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 77.5242 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | NSW | CNSW | N/A | NSW Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 77.5242 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | NSW | SNW | N/A | NSW Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 77.5242 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | NSW | SNSW | N/A | NSW Medium | 100 | 100 | 99.8435 | 0 | 0 | 4328.9456 | 77.5242 | 3 | 20 | 20 | 33.144 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | VIC | VIC | N/A | VIC Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 106.93 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | SA | CSA | N/A | SA Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 103.3657 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | SA | SESA | N/A | SA Medium | 100 | 100 | 99.8435 | 0 | 0 | 4336.8284 | 103.3657 | 3 | 20 | 20 | 34.3716 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | Battery | TAS | TAS | N/A | TAS Low | 100 | 100 | 99.8435 | 0 | 0 | 4107.3952 | 106.93 | 3 | 20 | 20 | 30.6889 | 0 | 0 | 0 | 0 | 0 | 0
Wind | Wind | QLD | NQ | Far North QLD | QLD Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 253.67 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | QLD | NQ | North Qld Clean Energy Hub | QLD Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 297 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | QLD | NQ | Northern Qld | QLD Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 253.67 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | QLD | CQ | Isaac | QLD Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 250.33 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | QLD | CQ | Barcaldine | QLD Medium | 100 | 100 | 100 | 0 | 0 | 2972.8428 | 150 | 2 | 25 | 30 | 29.9404 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | QLD | CQ | Fitzroy | QLD Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 250.33 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | QLD | SQ | Wide Bay | QLD Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 113.33 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | QLD | SQ | Darling Downs | QLD Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 116.67 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | QLD | SQ | Banana | QLD Medium | 100 | 100 | 100 | 0 | 0 | 2972.8428 | 367 | 2 | 25 | 30 | 29.9404 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | NNSW | North West NSW | NSW Medium | 100 | 100 | 100 | 0 | 0 | 2955.8923 | 135 | 2 | 25 | 30 | 28.8711 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | NNSW | New England | NSW Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 135 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | CNSW | Central-West Orana | NSW Medium | 100 | 100 | 100 | 0 | 0 | 2955.8923 | 135 | 2 | 25 | 30 | 28.8711 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | SNSW | Broken Hill | NSW High | 100 | 100 | 100 | 0 | 0 | 3094.0392 | 176 | 2 | 25 | 30 | 31.277 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | SNSW | South West NSW | NSW High | 100 | 100 | 100 | 0 | 0 | 3094.0392 | 135 | 2 | 25 | 30 | 31.277 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | SNSW | Wagga Wagga | NSW Medium | 100 | 100 | 100 | 0 | 0 | 2955.8923 | 272 | 2 | 25 | 30 | 28.8711 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | SNSW | Tumut | NSW Medium | 100 | 100 | 100 | 0 | 0 | 2955.8923 | 100 | 2 | 25 | 30 | 28.8711 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | SNSW | Cooma-Monaro | NSW Medium | 100 | 100 | 100 | 0 | 0 | 2955.8923 | 100 | 2 | 25 | 30 | 28.8711 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | CNSW | Hunter-Central Coast | NSW Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 100 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | SNW | Illawarra | NSW Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 100 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | VIC | VIC | Ovens Murray | VIC Medium | 100 | 100 | 100 | 0 | 0 | 2861.5343 | 136 | 2 | 25 | 30 | 27.5345 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | VIC | VIC | Murray River | VIC Medium | 100 | 100 | 100 | 0 | 0 | 2861.5343 | 269 | 2 | 25 | 30 | 27.5345 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | VIC | VIC | Western Victoria | VIC Medium | 100 | 100 | 100 | 0 | 0 | 2861.5343 | 277 | 2 | 25 | 30 | 27.5345 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | VIC | VIC | South West Victoria | VIC Medium | 100 | 100 | 100 | 0 | 0 | 2861.5343 | 277 | 2 | 25 | 30 | 27.5345 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | VIC | VIC | Gippsland | VIC Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 340 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | VIC | VIC | Central North Vic | VIC High | 100 | 100 | 100 | 0 | 0 | 2897.6954 | 321 | 2 | 25 | 30 | 28.0691 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | SA | SESA | South East SA | SA Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 287 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | SA | CSA | Riverland | SA Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 166.67 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | SA | CSA | Mid-North SA | SA Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 257 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | SA | CSA | Yorke Peninsula | SA Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 120 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | SA | CSA | Northern SA | SA Medium | 100 | 100 | 100 | 0 | 0 | 2963.8025 | 250.337 | 2 | 25 | 30 | 29.9404 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | SA | CSA | Leigh Creek | SA Medium | 100 | 100 | 100 | 0 | 0 | 2963.8025 | 153.33 | 2 | 25 | 30 | 29.9404 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | SA | CSA | Roxby Downs | SA Medium | 100 | 100 | 100 | 0 | 0 | 2963.8025 | 283.67 | 2 | 25 | 30 | 29.9404 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | SA | CSA | Eastern Eyre Peninsula | SA Medium | 100 | 100 | 100 | 0 | 0 | 2963.8025 | 283.67 | 2 | 25 | 30 | 29.9404 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | SA | CSA | Western Eyre Peninsula | SA Medium | 100 | 100 | 100 | 0 | 0 | 2963.8025 | 146.67 | 2 | 25 | 30 | 29.9404 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | TAS | TAS | North East Tasmania | TAS Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 410.33 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | TAS | TAS | North West Tasmania | TAS Medium | 100 | 100 | 100 | 0 | 0 | 2951.9372 | 377 | 2 | 25 | 30 | 29.1384 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | TAS | TAS | Central Highlands | TAS Low | 100 | 100 | 100 | 0 | 0 | 2796.8397 | 357 | 2 | 25 | 30 | 26.7325 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | NSW | CNSW | New South Wales Non-REZ | NSW Medium | 100 | 100 | 100 | 0 | 0 | 2955.8923 | 367 | 2 | 25 | 30 | 28.8711 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind | Wind | VIC | VIC | Victoria Non-REZ | VIC Medium | 100 | 100 | 100 | 0 | 0 | 2861.5343 | 347 | 2 | 25 | 30 | 27.5345 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (fixed) | Wind | NSW | SNW | Hunter Coast | NSW Low | 100 | 100 | 100 | 0 | 0 | 6075.7626 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 169.7311 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (fixed) | Wind | NSW | SNW | Illawarra Coast | NSW Low | 100 | 100 | 100 | 0 | 0 | 6075.7626 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 169.7311 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (fixed) | Wind | VIC | VIC | Gippsland Coast | VIC Low | 100 | 100 | 100 | 0 | 0 | 6075.7626 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 169.7311 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (fixed) | Wind | VIC | VIC | Portland Coast | VIC Low | 100 | 100 | 100 | 0 | 0 | 6075.7626 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 169.7311 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (fixed) | Wind | SA | SESA | South East SA Coast | SA Low | 100 | 100 | 100 | 0 | 0 | 6075.7626 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 169.7311 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (fixed) | Wind | TAS | TAS | North West Tasmania Coast | TAS Low | 100 | 100 | 100 | 0 | 0 | 6075.7626 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 169.7311 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (fixed) | Wind | TAS | TAS | North East Tasmania Coast | TAS Low | 100 | 100 | 100 | 0 | 0 | 6075.7626 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 169.7311 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (floating) | Wind | NSW | SNW | Hunter Coast | NSW Low | 100 | 100 | 100 | 0 | 0 | 8417.5296 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 625.6348 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (floating) | Wind | NSW | SNW | Illawarra Coast | NSW Low | 100 | 100 | 100 | 0 | 0 | 8417.5296 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 625.6348 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (floating) | Wind | VIC | VIC | Gippsland Coast | VIC Low | 100 | 100 | 100 | 0 | 0 | 8417.5296 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 625.6348 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (floating) | Wind | VIC | VIC | Portland Coast | VIC Low | 100 | 100 | 100 | 0 | 0 | 8417.5296 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 625.6348 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (floating) | Wind | SA | SESA | South East SA Coast | SA Low | 100 | 100 | 100 | 0 | 0 | 8417.5296 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 625.6348 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (floating) | Wind | TAS | TAS | North West Tasmania Coast | TAS Low | 100 | 100 | 100 | 0 | 0 | 8417.5296 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 625.6348 | 0 | 0 | 0 | 0 | 0.069759 | 0
Wind - offshore (floating) | Wind | TAS | TAS | North East Tasmania Coast | TAS Low | 100 | 100 | 100 | 0 | 0 | 8417.5296 | The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report. | 9 | 25 | 30 | 625.6348 | 0 | 0 | 0 | 0 | 0.069759 | 0
Pumped Hydro (8hrs storage) | Water | QLD | NQ | N/A | NQ | 100 | 100 | 100 | 0.27397 | 1 | 3389.018 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | QLD | CQ | N/A | CQ | 100 | 100 | 100 | 0.27397 | 1 | 3389.018 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | QLD | GG | N/A | GG | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | QLD | SQ | N/A | SQ | 100 | 100 | 100 | 0.27397 | 1 | 3737.9862 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | NSW | NNSW | N/A | NNSW | 100 | 100 | 100 | 0.27397 | 1 | 2956.1633 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | NSW | CNSW | N/A | CNSW | 100 | 100 | 100 | 0.27397 | 1 | 3439.35 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | NSW | SNW | N/A | SNW | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | NSW | SNSW | N/A | SNSW | 100 | 100 | 100 | 0.27397 | 1 | 3503.1038 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | VIC | VIC | N/A | VIC | 100 | 100 | 100 | 0.27397 | 1 | 3355.4634 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | SA | CSA | N/A | CSA | 100 | 100 | 100 | 0.27397 | 1 | 4533.2311 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | SA | SESA | N/A | SESA | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (8hrs storage) | Water | TAS | TAS | N/A | TAS | 100 | 100 | 100 | 0.27397 | 1 | 2509.8866 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | QLD | NQ | N/A | NQ | 100 | 100 | 100 | 0.27397 | 1 | 4144.0935 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | QLD | CQ | N/A | CQ | 100 | 100 | 100 | 0.27397 | 1 | 4144.0935 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | QLD | GG | N/A | GG | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | QLD | SQ | N/A | SQ | 100 | 100 | 100 | 0.27397 | 1 | 4539.6661 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | NSW | NNSW | N/A | NNSW | 100 | 100 | 100 | 0.27397 | 1 | 3870.9601 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | NSW | CNSW | N/A | CNSW | 100 | 100 | 100 | 0.27397 | 1 | 5085.933 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | NSW | SNW | N/A | SNW | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | NSW | SNSW | N/A | SNSW | 100 | 100 | 100 | 0.27397 | 1 | 4728.034 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | VIC | VIC | N/A | VIC | 100 | 100 | 100 | 0.27397 | 1 | 4709.1972 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | SA | CSA | N/A | CSA | 100 | 100 | 100 | 0.27397 | 1 | 7850.2317 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | SA | SESA | N/A | SESA | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (24hrs storage) | Water | TAS | TAS | N/A | TAS | 100 | 100 | 100 | 0.27397 | 1 | 2910.2839 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | QLD | NQ | N/A | NQ | 100 | 100 | 100 | 0.27397 | 1 | 6112.3583 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | QLD | CQ | N/A | CQ | 100 | 100 | 100 | 0.27397 | 1 | 6112.3583 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | QLD | GG | N/A | GG | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | QLD | SQ | N/A | SQ | 100 | 100 | 100 | 0.27397 | 1 | 6197.2522 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | NSW | NNSW | N/A | NNSW | 100 | 100 | 100 | 0.27397 | 1 | 4414.481 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | NSW | CNSW | N/A | CNSW | 100 | 100 | 100 | 0.27397 | 1 | 7930.5019 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | NSW | SNW | N/A | SNW | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | NSW | SNSW | N/A | SNSW | 100 | 100 | 100 | 0.27397 | 1 | 6444.8593 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | VIC | VIC | N/A | VIC | 100 | 100 | 100 | 0.27397 | 1 | 7074.4888 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | SA | CSA | N/A | CSA | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | SA | SESA | N/A | SESA | 100 | 100 | 100 | 0.27397 | 1 | 0 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
Pumped Hydro (48hrs storage) | Water | TAS | TAS | N/A | TAS | 100 | 100 | 100 | 0.27397 | 1 | 3282.5628 | 0 | 6 | 40 | 50 | 19.0925 | 0 | 0 | 0 | 0 | 0.5 | 0
BOTN - Cethana | Water | TAS | TAS | N/A | TAS | 100 | 100 | 100 | 0.27397 | 1 | 2400.7511 | 0 | 6 | 40 | 50 | 20.8108 | 0 | 0 | 0 | 0 | 0.5 | 0
Hydrogen reciprocating engines | Hydrogen | QLD | NQ | N/A | QLD Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 110.4943 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | QLD | CQ | N/A | QLD Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 110.4943 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | QLD | GG | N/A | QLD Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 110.4943 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | QLD | SQ | N/A | QLD Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 110.4943 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | NSW | NNSW | N/A | NSW Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 85.544 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | NSW | CNSW | N/A | NSW Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 85.544 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | NSW | SNW | N/A | NSW Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 85.544 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | NSW | SNSW | N/A | NSW Medium | 100 | 100 | 100 | 0.73973 | 2.7 | 2731.3051 | 85.544 | 4 | 25 | 40 | 38.1099 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | VIC | VIC | N/A | VIC Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 115.4844 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | SA | CSA | N/A | SA Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 110.4943 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | SA | SESA | N/A | SA Medium | 100 | 100 | 100 | 0.73973 | 2.7 | 2683.5978 | 110.4943 | 4 | 25 | 40 | 39.5213 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004
Hydrogen reciprocating engines | Hydrogen | TAS | TAS | N/A | TAS Low | 100 | 100 | 100 | 0.73973 | 2.7 | 2606.9534 | 115.4844 | 4 | 25 | 40 | 35.2869 | 0 | 11.7031 | 18.8155 | 0 | 4 | 220.2004

## Existing Gen Data Summary
Go to Assumptions Summary
Generator Summary - Existing, Committed and Anticipated generators
Notes
1. Fuel costs represent the selected Scenario on the Fuel Price summary sheet and the selected year in cell P11.
2. Seasonal ratings represent the selected year in Cell I11 to Cell K11.
3. SRMC is a calculation involving fuel costs, and as such will vary across scenario and year.
4. Expected retirement date in this summary sheet is indicative of the first unit's retirement date.
Existing generators
| Generator | Generator type | Region | ISP sub-region | REZ location | Fuel/technology type | Maximum capacity (MW) | Summer rating (MW) | Summer typical rating (MW) | Winter rating (MW) | Maintenance duration (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate (GJ/MWh HHV s.o.) | Fuel cost ($/GJ) | Emissions (kg/MWh) | MLF | Auxiliary load (%) | SRMC ($/MWh) | Expected retirement year
[15 empty] | Green Energy Exports | Green Energy Exports
[8 empty] | 2030-31 | 2030-31 | 2031 |  |  |  |  | 2041-42 | 2024-25
| Bayswater | Steam Sub Critical | NSW | CNSW | N/A | Black Coal NSW | 2715 | 2595 | 2715 | 2715 | 5.4795 | 64.5 | 5.1012 | 9.4488 | 2.537 | 889.202 | 0.9651 | 5.4639 | 29.0731 | 2033
| Eraring | Steam Sub Critical | NSW | SNW | N/A | Black Coal NSW | 2880 | 0 | 0 | 0 | 5.4795 | 64.5 | 5.1012 | 9.5491 | 2.6433 | 878.938 | 0.9848 | 5.4639 | 30.3427 | 2025
| Mt Piper | Steam Sub Critical | NSW | CNSW | N/A | Black Coal NSW | 1390 | 1380 | 1390 | 1430 | 5.4795 | 64.5 | 5.1012 | 9.2545 | 2.6433 | 801.1644 | 0.9164 | 5.4639 | 29.564 | 2040
| Vales Point B | Steam Sub Critical | NSW | SNW | N/A | Black Coal NSW | 1320 | 1320 | 1320 | 1320 | 5.4795 | 64.5 | 5.1012 | 9.6774 | 2.8406 | 944.7033 | 0.9869 | 5.4639 | 32.5906 | 2033
| Callide B | Steam Sub Critical | QLD | CQ | N/A | Black Coal QLD | 700 | 0 | 0 | 0 | 5.4795 | 63.48 | 5.0237 | 9.1603 | 2.3328 | 942.8409 | 0.9138 | 6.671 | 26.3926 | 2028
| Callide C | Steam Super Critical | QLD | CQ | N/A | Black Coal QLD | 844 | 854 | 886 | 886 | 5.4795 | 63.48 | 5.0237 | 9.3023 | 2.3328 | 873.9527 | 0.9138 | 6.671 | 26.7239 | 2051
| Gladstone | Steam Sub Critical | QLD | GG | N/A | Black Coal QLD | 1680 | 1680 | 1680 | 1680 | 5.4795 | 63.48 | 5.0237 | 9.4737 | 2.7836 | 985.8045 | 0.9323 | 6.671 | 31.3951 | 2035
| Kogan Creek | Steam Super Critical | QLD | SQ | N/A | Black Coal QLD | 744 | 710 | 730 | 750 | 5.4795 | 63.48 | 5.0237 | 8.802 | 1.6188 | 861.9335 | 0.9673 | 6.671 | 19.2723 | 2042
| Millmerran | Steam Super Critical | QLD | SQ | N/A | Black Coal QLD | 852 | 670 | 800 | 852 | 5.4795 | 63.48 | 5.0237 | 9.2072 | 1.4726 | 825.2499 | 0.9763 | 6.671 | 18.5819 | 2051
| Stanwell | Steam Sub Critical | QLD | CQ | N/A | Black Coal QLD | 1460 | 1460 | 1460 | 1460 | 5.4795 | 63.48 | 5.0237 | 9.068 | 2.4296 | 863.4613 | 0.9181 | 6.671 | 27.0556 | 2043
| Tarong | Steam Sub Critical | QLD | SQ | N/A | Black Coal QLD | 1400 | 1400 | 1400 | 1400 | 5.4795 | 63.48 | 5.0237 | 9.2072 | 3.0441 | 886.5998 | 0.9712 | 6.671 | 33.0515 | 2036
| Tarong North | Steam Super Critical | QLD | SQ | N/A | Black Coal QLD | 450 | 443 | 443 | 443 | 5.4795 | 63.48 | 5.0237 | 8.6538 | 3.0441 | 886.5998 | 0.9712 | 6.671 | 31.3672 | 2037
| Loy Yang A Power Station | Steam Sub Critical | VIC | VIC | N/A | Brown Coal VIC | 2210 | 2080 | 2190 | 2210 | 5.4795 | 163.64 | 4.7846 | 12.1622 | 0.75934 | 1168.8606 | 0.9782 | 8.2146 | 14.0199 | 2035
| Loy Yang B | Steam Sub Critical | VIC | VIC | N/A | Brown Coal VIC | 1160 | 1090 | 1115 | 1160 | 5.4795 | 163.64 | 4.7846 | 12.5436 | 0.75934 | 1111.1528 | 0.9782 | 8.2146 | 14.3095 | 2047
| Yallourn W | Steam Sub Critical | VIC | VIC | N/A | Brown Coal VIC | 1450 | 0 | 0 | 0 | 5.4795 | 163.64 | 4.7846 | 13.8996 | 0.75182 | 1286.6019 | 0.9624 | 8.2146 | 15.2347 | 2028
| Tallawarra | CCGT | NSW | SNW | N/A | CCGT | 440 | 405 | 415 | 425 | 5.4795 | 12.53 | 8.7945 | 6.9903 | 15.9331 | 370.9712 | 0.9856 | 1.7476 | 120.1718 | 2043
| Condamine A | CCGT | QLD | SQ | N/A | CCGT | 144.4 | 138.53 | 139.1 | 144.23 | 5.4795 | 12.53 | 8.7945 | 7.2874 | 15.7308 | 448.78 | 0.9832 | 1.7476 | 123.4319 | 2039
| Darling Downs | CCGT | QLD | SQ | N/A | CCGT | 644.5 | 563 | 579 | 630 | 5.4795 | 12.53 | 8.7945 | 7.377 | 15.7308 | 420.6678 | 0.9617 | 1.7476 | 124.8414 | 2045
| Swanbank E GT | CCGT | QLD | SQ | N/A | CCGT | 385 | 350 | 355 | 365 | 5.4795 | 12.53 | 8.7945 | 7.438 | 15.6691 | 393.9767 | 0.9987 | 1.7476 | 125.3417 | 2036
| Townsville Power Station | CCGT | QLD | NQ | N/A | CCGT | 244 | 0 | 0 | 0 | 5.4795 | 12.53 | 8.7945 | 7.5949 | 15.7305 | 571.8092 | 0.9519 | 1.7476 | 128.2664 | 2046
| Yarwun Cogen | CCGT | QLD | GG | N/A | CCGT | 180 | 180 | 180 | 180 | 5.4795 | 12.53 | 8.7945 | 10.3746 | 15.7963 | 458.8084 | 0.9349 | 1.7476 | 172.6754 | 2050
| Osborne | CCGT | SA | CSA | N/A | CCGT | 180 | 0 | 0 | 0 | 5.4795 | 12.53 | 8.7945 | 8.1633 | 15.6937 | 414.6692 | 0.9997 | 1.7476 | 136.9062 | 2026
| Pelican Point | CCGT | SA | CSA | N/A | CCGT | 529 | 416 | 468 | 498 | 5.4795 | 12.53 | 8.7945 | 7.3469 | 15.6937 | 400.2491 | 0.9984 | 1.7476 | 124.095 | 2037
| Tamar Valley Combined Cycle | CCGT | TAS | TAS | N/A | CCGT | 208 | 0 | 0 | 0 | 5.4795 | 125.93 | 8.7945 | 7.2874 | 15.7402 | 618.7694 | 1 | 1.7476 | 123.5001 | 2050
| Colongra | OCGT | NSW | SNW | N/A | OCGT | 724 | 640 | 680 | 724 | 1.3699 | 18.08 | 12.5652 | 11.1455 | 17.3809 | 625.4489 | 0.9831 | 0.6143 | 206.2839 | 2070
| Smithfield Energy Facility | OCGT | NSW | SNW | N/A | OCGT | 185 | 108 | 108 | 125.7 | 1.3699 | 18.08 | 12.5652 | 13.6882 | 17.1423 | 704.9693 | 1 | 0.6143 | 247.2127 | 2044
| Uranquinty | OCGT | NSW | SNSW | N/A | OCGT | 692 | 640 | 656 | 692 | 1.3699 | 18.08 | 12.5652 | 11.1455 | 16.6981 | 564.2196 | 0.8383 | 0.6143 | 198.674 | 2044
| Barcaldine Power Station | OCGT | QLD | CQ | N/A | OCGT | 37 | 32 | 36 | 37 | 1.3699 | 18.08 | 12.5652 | 12.7208 | 17.0671 | 793.2629 | 0.938 | 0.6143 | 229.6735 | 2034
| Braemar | OCGT | QLD | SQ | N/A | OCGT | 564 | 501 | 519 | 543 | 1.3699 | 18.08 | 12.5652 | 11.8812 | 16.9064 | 616.5276 | 0.9617 | 0.6143 | 213.4333 | 2046
| Braemar 2 Power Station | OCGT | QLD | SQ | N/A | OCGT | 519 | 495 | 495 | 519 | 1.3699 | 18.08 | 12.5652 | 11.8812 | 16.9064 | 616.5276 | 0.9617 | 0.6143 | 213.4333 | 2049
| Mt Stuart | OCGT | QLD | NQ | N/A | Liquid Fuel | 423.5 | 387 | 396 | 400 | 1.3699 | 18.08 | 12.5652 | 11.8812 | 35.4315 | 1001.6306 | 0.9164 | 0.66986 | 433.534 | 2033
| Oakey Power Station | OCGT | QLD | SQ | N/A | OCGT | 346 | 288 | 300 | 346 | 1.3699 | 18.08 | 12.5652 | 10.9422 | 16.9105 | 663.6832 | 0.9628 | 0.6143 | 197.6039 | 2050
| Roma | OCGT | QLD | SQ | N/A | OCGT | 80 | 54 | 60 | 68 | 1.3699 | 18.08 | 12.5652 | 11.8812 | 16.6156 | 649.8984 | 0.9643 | 0.6143 | 209.9778 | 2034
| Bolivar Power Station | OCGT | SA | CSA | N/A | OCGT | 123.2 | 95.2 | 108.4 | 125.6 | 1.3699 | 13.47 | 12.8318 | 10.19 | 16.9028 | 541.6007 | 0.9949 | 0.6143 | 185.0718 | 2045
| Dry Creek GT | OCGT | SA | CSA | N/A | OCGT | 156 | 117 | 122 | 0 | 1.3699 | 18.08 | 12.5652 | 13.6882 | 16.9028 | 892.1893 | 0.9992 | 0.6143 | 243.935 | 2030
| Hallett GT | OCGT | SA | CSA | N/A | OCGT | 276.86 | 223 | 235 | 249 | 1.3699 | 18.08 | 12.5652 | 14.876 | 16.6006 | 642.6559 | 0.9599 | 0.6143 | 259.5156 | 2032
| Ladbroke Grove | OCGT | SA | SESA | N/A | OCGT | 80 | 70 | 74 | 84 | 1.3699 | 18.08 | 12.5652 | 11.8812 | 16.6006 | 516.2364 | 0.9736 | 0.6143 | 209.7996 | 2035
| Mintaro GT | OCGT | SA | CSA | N/A | OCGT | 90 | 68 | 73 | 0 | 1.3699 | 18.08 | 12.5652 | 12.7208 | 16.9028 | 693.5416 | 0.9746 | 0.6143 | 227.5838 | 2030
| Port Lincoln GT | OCGT | SA | CSA | N/A | Liquid Fuel | 73.5 | 57 | 62 | 0 | 1.3699 | 18.08 | 12.5652 | 12.8114 | 35.4315 | 1334.5888 | 0.9822 | 0.66986 | 466.4924 | 2027
| Quarantine | OCGT | SA | CSA | N/A | OCGT | 234 | 189 | 200 | 224 | 1.3699 | 18.08 | 12.5652 | 10.7143 | 16.9028 | 603.9767 | 0.9946 | 0.6143 | 193.6671 | 2053
| Snapper Point Power Station | OCGT | SA | CSA | N/A | OCGT | 154 | 123 | 138.1 | 156.9 | 1.3699 | 13.47 | 12.8318 | 10.1902 | 16.7517 | 541.6007 | 0.9993 | 0.6143 | 183.5355 | 2046
| Snuggery | OCGT | SA | SESA | N/A | Liquid Fuel | 63 | 54 | 57 | 0 | 1.3699 | 18.08 | 12.5652 | 13.4328 | 35.4315 | 1106.8763 | 0.9877 | 0.66986 | 488.5112 | 2027
| Bell Bay Three | OCGT | TAS | TAS | N/A | OCGT | 120 | 105 | 105 | 105 | 1.3699 | 18.08 | 12.5652 | 12.0401 | 16.9493 | 618.7694 | 0.9968 | 0.6143 | 216.6372 | 2040
| Tamar Valley Peaking | OCGT | TAS | TAS | N/A | OCGT | 58 | 58 | 58 | 58 | 1.3699 | 18.08 | 12.5652 | 12.7208 | 15.7402 | 618.7694 | 0.9968 | 0.6143 | 212.7934 | 2050
| Bairnsdale | OCGT | VIC | VIC | N/A | OCGT | 94 | 57 | 73 | 88 | 1.3699 | 18.08 | 12.5652 | 10.4956 | 16.5724 | 537.0489 | 0.9804 | 0.6143 | 186.5025 | 2042
| Jeeralang A | OCGT | VIC | VIC | N/A | OCGT | 212 | 186.4 | 200 | 222 | 1.3699 | 18.08 | 12.5652 | 15.2542 | 16.3219 | 757.9581 | 0.9764 | 0.6143 | 261.544 | 2039
| Jeeralang B | OCGT | VIC | VIC | N/A | OCGT | 228 | 212.9 | 230 | 257 | 1.3699 | 18.08 | 12.5652 | 15.2542 | 16.3219 | 757.9581 | 0.9764 | 0.6143 | 261.544 | 2039
| Laverton North | OCGT | VIC | VIC | N/A | OCGT | 312 | 336 | 344 | 344 | 1.3699 | 18.08 | 12.5652 | 11.5016 | 16.6242 | 638.1801 | 0.9979 | 0.6143 | 203.7705 | 2070
| Mortlake | OCGT | VIC | VIC | N/A | OCGT | 584 | 514 | 532 | 584 | 1.3699 | 18.08 | 12.5652 | 11.1455 | 16.7406 | 467.1118 | 0.9927 | 0.6143 | 199.1478 | 2047
| Somerton | OCGT | VIC | VIC | N/A | OCGT | 170 | 140 | 170 | 170 | 1.3699 | 18.08 | 12.5652 | 14.876 | 16.3219 | 732.5947 | 0.996 | 0.6143 | 255.371 | 2033
| Valley Power | OCGT | VIC | VIC | N/A | OCGT | 300 | 285 | 300 | 336 | 1.3699 | 18.08 | 12.5652 | 14.876 | 16.6242 | 805.7837 | 0.9782 | 0.6143 | 259.8679 | 2070
| Torrens Island B | Gas-powered steam turbine | SA | CSA | N/A | Gas-powered steam turbine | 800 | 0 | 0 | 0 | 0.68493 | 56.24 | 2.7787 | 10.7143 | 16.9028 | 593.0411 | 0.9997 | 5.0021 | 183.8807 | 2026
| Newport | Gas-powered steam turbine | VIC | VIC | N/A | Gas-powered steam turbine | 500 | 475 | 510 | 510 | 0.68493 | 56.24 | 2.7787 | 10.2857 | 16.3219 | 532.5429 | 0.9937 | 5.0021 | 170.6616 | 2039
| Angaston | Reciprocating Engine | SA | CSA | N/A | Liquid Fuel | 36 | 36 | 36 | 36 | 1.6438 | 18.04 | 13.3409 | 12.775 | 35.4315 | 685.758 | 1.0048 | 0.66986 | 465.9794 | 2070
| Barker Inlet Power Station | Reciprocating Engine | SA | CSA | N/A | OCGT | 210 | 205.2 | 210 | 210 | 1.6438 | 18.04 | 13.3409 | 7.8947 | 16.6006 | 567.5073 | 1 | 0.6143 | 144.3979 | 2044
| Lonsdale | Reciprocating Engine | SA | CSA | N/A | Liquid Fuel | 20.7 | 21.06 | 21.06 | 21.06 | 1.6438 | 18.04 | 13.3409 | 7.8947 | 35.4315 | 657.9846 | 1.0039 | 0.66986 | 293.0635 | 2070
| Port Stanvac 1 | Reciprocating Engine | SA | CSA | N/A | Liquid Fuel | 46.8 | 46.8 | 46.8 | 46.8 | 1.6438 | 18.04 | 13.3409 | 7.8947 | 35.4315 | 657.9846 | 1.0039 | 0.66986 | 293.0635 | 2070
| Blowering | Hydro | NSW | SNSW | N/A | Hydro | 80 | 70 | 70 | 70 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9241 | 0.34269 | 8.5797 | 2070
| Guthega | Hydro | NSW | SNSW | N/A | Hydro | 60 | 68 | 68 | 68 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.893 | 0.34269 | 8.5797 | 2070
| Hume Dam NSW | Hydro | NSW | SNSW | N/A | Hydro | 29 | 29 | 29 | 0 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9205 | 0.34269 | 8.5797 | 2057
| Shoalhaven | Hydro | NSW | CNSW | N/A | Hydro | 247 | 247 | 247 | 247 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9732 | 0.34269 | 8.5797 | 2069
| Tumut 3 | Hydro | NSW | SNSW | N/A | Hydro | 1500 | 1800 | 1800 | 1800 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9318 | 0.34269 | 8.5797 | 2070
| Upper Tumut | Hydro | NSW | SNSW | N/A | Hydro | 616 | 724 | 724 | 724 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9318 | 0.34269 | 8.5797 | 2070
| Barron Gorge | Hydro | QLD | NQ | N/A | Hydro | 70 | 66 | 66 | 66 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.959 | 0.34269 | 8.5797 | 2042
| Kareeya | Hydro | QLD | NQ | N/A | Hydro | 86.4 | 86.4 | 86.4 | 86.4 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9559 | 0.34269 | 8.5797 | 2037
| Wivenhoe | Hydro | QLD | SQ | N/A | Hydro | 570 | 570 | 570 | 570 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9994 | 0.34269 | 8.5797 | 2084
| Bastyan | Hydro | TAS | TAS | N/A | Hydro | 79.9 | 84 | 84 | 84 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9202 | 0.34269 | 8.5797 | 2100
| Catagunya / Liapootah / Wayatinah | Hydro | TAS | TAS | N/A | Hydro | 176.7 | 174 | 174 | 174 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9809 | 0.34269 | 8.5797 | 2100
| Cethana | Hydro | TAS | TAS | N/A | Hydro | 85 | 95 | 95 | 95 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9504 | 0.34269 | 8.5797 | 2100
| Devils Gate | Hydro | TAS | TAS | N/A | Hydro | 60 | 63 | 63 | 63 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9537 | 0.34269 | 8.5797 | 2100
| Fisher | Hydro | TAS | TAS | N/A | Hydro | 43.2 | 46 | 46 | 46 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9557 | 0.34269 | 8.5797 | 2100
| Gordon | Hydro | TAS | TAS | N/A | Hydro | 432 | 378 | 378 | 378 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9731 | 0.34269 | 8.5797 | 2100
| John Butters | Hydro | TAS | TAS | N/A | Hydro | 144 | 144 | 144 | 144 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9208 | 0.34269 | 8.5797 | 2100
| Lake Echo | Hydro | TAS | TAS | N/A | Hydro | 32.4 | 30 | 30 | 30 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.8888 | 0.34269 | 8.5797 | 2100
| Lemonthyme / Wilmot | Hydro | TAS | TAS | N/A | Hydro | 81.6 | 88 | 88 | 88 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9567 | 0.34269 | 8.5797 | 2100
| Mackintosh | Hydro | TAS | TAS | N/A | Hydro | 79.9 | 84 | 84 | 84 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9059 | 0.34269 | 8.5797 | 2100
| Meadowbank | Hydro | TAS | TAS | N/A | Hydro | 40 | 44 | 44 | 44 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9688 | 0.34269 | 8.5797 | 2100
| Poatina | Hydro | TAS | TAS | N/A | Hydro | 300 | 285 | 285 | 342 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9555 | 0.34269 | 8.5797 | 2100
| Reece | Hydro | TAS | TAS | N/A | Hydro | 231.2 | 240 | 240 | 240 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9052 | 0.34269 | 8.5797 | 2100
| Tarraleah | Hydro | TAS | TAS | N/A | Hydro | 90 | 72 | 72 | 72 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.8977 | 0.34269 | 8.5797 | 2100
| Trevallyn | Hydro | TAS | TAS | N/A | Hydro | 93 | 100 | 100 | 100 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9825 | 0.34269 | 8.5797 | 2100
| Tribute | Hydro | TAS | TAS | N/A | Hydro | 82.8 | 0 | 0 | 0 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9089 | 0.34269 | 8.5797 | 2100
| Tungatinah | Hydro | TAS | TAS | N/A | Hydro | 125 | 130 | 130 | 130 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.8782 | 0.34269 | 8.5797 | 2100
| Bogong / MacKay | Hydro | VIC | VIC | N/A | Hydro | 300.02 | 300.02 | 300.02 | 300.02 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9715 | 0.34269 | 8.5797 | 2057
| Dartmouth | Hydro | VIC | VIC | N/A | Hydro | 185 | 170 | 170 | 170 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9622 | 0.34269 | 8.5797 | 2057
| Eildon | Hydro | VIC | VIC | N/A | Hydro | 135 | 120 | 120 | 120 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9975 | 0.34269 | 8.5797 | 2057
| Hume Dam VIC | Hydro | VIC | VIC | N/A | Hydro | 29 | 29 | 29 | 0 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9389 | 0.34269 | 8.5797 | 2057
| Murray 1 | Hydro | VIC | VIC | N/A | Hydro | 950 | 950 | 950 | 950 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.985 | 0.34269 | 8.5797 | 2070
| Murray 2 | Hydro | VIC | VIC | N/A | Hydro | 552 | 600 | 600 | 600 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.985 | 0.34269 | 8.5797 | 2070
| West Kiewa | Hydro | VIC | VIC | N/A | Hydro | 68 | 68 | 68 | 68 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 1.011 | 0.34269 | 8.5797 | 2057
| Avonlie Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Solar | 254.1 | 189.98 | 189.98 | 189.98 | 0 | 18.18 | 0 | 0 | 0 | 0 | 1 | 0.017458 | 0 | 2058
| Beryl Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 98.4 | 77.4 | 82.8 | 87 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9339 | 0.017458 | 0 | 2049
| Bomen Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Solar | 121 | 97.68 | 99 | 99.88 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.911 | 0.017458 | 0 | 2050
| Broken Hill Solar Farm | Large scale Solar PV | NSW | SNSW | Broken Hill | Solar | 53 | 53 | 53 | 53 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8324 | 0.017458 | 0 | 2043
| Coleambally Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Solar | 150.3 | 150.03 | 150.03 | 150.03 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8894 | 0.017458 | 0 | 2038
| Corowa Solar Farm | Large scale Solar PV | NSW | SNSW | South West NSW | Solar | 36.01 | 30 | 30 | 30 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9365 | 0.017458 | 0 | 2051
| Darlington Point Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Solar | 274.97 | 263.3 | 266 | 274.96 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8958 | 0.017458 | 0 | 2055
| Finley Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Solar | 162.36 | 116.72 | 129.98 | 132.66 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9255 | 0.017458 | 0 | 2049
| Goonumbla Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 69.75 | 67.73 | 69.31 | 69.75 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9 | 0.017458 | 0 | 2050
| Gullen Range Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Solar | 10 | 10 | 10 | 10 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.958 | 0.017458 | 0 | 2100
| Gunnedah Solar Farm | Large scale Solar PV | NSW | NNSW | North West NSW | Solar | 110 | 110 | 110 | 110 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8273 | 0.017458 | 0 | 2056
| Hillston Sun Farm | Large scale Solar PV | NSW | SNSW | N/A | Solar | 110 | 76.52 | 85 | 85 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8979 | 0.017458 | 0 | 2046
| Jemalong Solar | Large scale Solar PV | NSW | CNSW | N/A | Solar | 55 | 50 | 50 | 50 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8964 | 0.017458 | 0 | 2050
| Junee Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Solar | 36.01 | 30 | 30 | 30 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9108 | 0.017458 | 0 | 2050
| Limondale Solar Farm 1 | Large scale Solar PV | NSW | SNSW | South West NSW | Solar | 230 | 207.1 | 220 | 220 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8255 | 0.017458 | 0 | 2050
| Limondale Solar Farm 2 | Large scale Solar PV | NSW | SNSW | South West NSW | Solar | 28.98 | 28.99 | 28.99 | 28.99 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.831 | 0.017458 | 0 | 2050
| Manildra Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 50 | 43.4 | 45.4 | 46.7 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9557 | 0.017458 | 0 | 2048
| Molong Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 36.08 | 32.4 | 36.01 | 36.01 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9733 | 0.017458 | 0 | 2045
| Moree Solar Farm | Large scale Solar PV | NSW | NNSW | North West NSW | Solar | 56 | 56 | 56 | 56 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.7977 | 0.017458 | 0 | 2046
| Nevertire Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 104.64 | 104.64 | 104.64 | 104.64 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9439 | 0.017458 | 0 | 2049
| New England Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Solar | 400 | 400 | 400 | 400 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8718 | 0.017458 | 0 | 2052
| Nyngan Solar Plant | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 102.03 | 102.02 | 102.02 | 102.02 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9897 | 0.017458 | 0 | 2042
| Parkes Solar Farm | Large scale Solar PV | NSW | CNSW | N/A | Solar | 55 | 50.5 | 50.5 | 50.5 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9 | 0.017458 | 0 | 2058
| Sunraysia Solar Farm | Large scale Solar PV | NSW | SNSW | South West NSW | Solar | 228.8 | 191.36 | 199.68 | 199.68 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8255 | 0.017458 | 0 | 2049
| Suntop Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 150 | 150 | 150 | 150 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9224 | 0.017458 | 0 | 2056
| Wagga North Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Solar | 56 | 46.36 | 46.36 | 46.36 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.907 | 0.017458 | 0 | 2050
| Wellington Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 216.08 | 169.88 | 169.88 | 169.88 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9439 | 0.017458 | 0 | 2051
| West Wyalong Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Solar | 105.27 | 90.01 | 90.01 | 90.01 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9108 | 0.017458 | 0 | 2058
| White Rock Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Solar | 20 | 20 | 20 | 20 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8289 | 0.017458 | 0 | 2043
| Bluegrass Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 148 | 140.47 | 140.47 | 143.54 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9546 | 0.017458 | 0 | 2057
| Childers Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Solar | 64.38 | 55.87 | 55.87 | 55.87 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9704 | 0.017458 | 0 | 2049
| Clare Solar Farm | Large scale Solar PV | QLD | NQ | Northern Qld | Solar | 110.4 | 95.22 | 96.6 | 99.98 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8981 | 0.017458 | 0 | 2047
| Clermont Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Solar | 92.5 | 71.41 | 72.89 | 74.99 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.915 | 0.017458 | 0 | 2049
| Collinsville Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Solar | 42.5 | 39.95 | 41.31 | 42.5 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9132 | 0.017458 | 0 | 2044
| Columboola Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 217.25 | 161.95 | 161.95 | 161.95 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9746 | 0.017458 | 0 | 2046
| Darling Downs Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 121 | 108.5 | 108.5 | 110 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9762 | 0.017458 | 0 | 2036
| Daydream Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Solar | 167.75 | 145.79 | 147.07 | 149.99 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9098 | 0.017458 | 0 | 2048
| Edenvale Solar Park | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 180 | 146 | 146 | 146 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.972 | 0.017458 | 0 | 2053
| Emerald Solar Farm | Large scale Solar PV | QLD | CQ | N/A | Solar | 72 | 67.68 | 69.12 | 72 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9111 | 0.017458 | 0 | 2048
| Gangarri Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 162 | 119.88 | 119.88 | 119.88 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9837 | 0.017458 | 0 | 2051
| Hamilton Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Solar | 57.5 | 54.11 | 54.9 | 56 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.906 | 0.017458 | 0 | 2048
| Haughton Solar Farm | Large scale Solar PV | QLD | NQ | Northern Qld | Solar | 132.6 | 100.03 | 100.03 | 100.03 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9151 | 0.017458 | 0 | 2050
| Hayman Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Solar | 57.75 | 47.83 | 48 | 50 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9098 | 0.017458 | 0 | 2048
| Hughenden Solar Farm | Large scale Solar PV | QLD | NQ | North Qld Clean Energy Hub | Solar | 20.97 | 20.97 | 20.97 | 20.97 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9222 | 0.017458 | 0 | 2048
| Kennedy Energy Park Solar Farm | Large scale Solar PV | QLD | NQ | North Qld Clean Energy Hub | Solar | 15 | 14.28 | 14.58 | 15 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9667 | 0.017458 | 0 | 2046
| Kidston Solar Farm | Large scale Solar PV | QLD | NQ | North Qld Clean Energy Hub | Solar | 50 | 48.5 | 48.5 | 48.5 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9222 | 0.017458 | 0 | 2037
| Lilyvale Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Solar | 118.4 | 97.53 | 98.79 | 99.97 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9064 | 0.017458 | 0 | 2048
| Longreach Solar Farm | Large scale Solar PV | QLD | CQ | Barcaldine | Solar | 14 | 14 | 14 | 14 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.915 | 0.017458 | 0 | 2043
| Maryrorough Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 34.5 | 27.3 | 27.3 | 27.3 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9914 | 0.017458 | 0 | 2048
| Middlemount Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Solar | 26 | 26 | 26 | 26 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9111 | 0.017458 | 0 | 2050
| Moura Solar Farm | Large scale Solar PV | QLD | CQ | Fitzroy | Solar | 99 | 81.72 | 81.72 | 81.72 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9081 | 0.017458 | 0 | 2057
| Oakey 1 Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 25 | 23.1 | 24.22 | 25 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9869 | 0.017458 | 0 | 2043
| Oakey 2 Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 55.64 | 52.31 | 53.43 | 54.99 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9869 | 0.017458 | 0 | 2049
| Ross River Solar Farm | Large scale Solar PV | QLD | NQ | Northern Qld | Solar | 128 | 115.96 | 115.96 | 115.96 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9222 | 0.017458 | 0 | 2043
| Rugby Run Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Solar | 65 | 65 | 65 | 65 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9185 | 0.017458 | 0 | 2049
| Sun Metals Corporation Solar Farm | Large scale Solar PV | QLD | NQ | Northern Qld | Solar | 143 | 120.12 | 121.16 | 121.16 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9979 | 0.017458 | 0 | 2042
| Susan River Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Solar | 85.26 | 75.01 | 75.01 | 75.01 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9704 | 0.017458 | 0 | 2049
| Warwick Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 64.2 | 64.2 | 64.2 | 64.2 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9914 | 0.017458 | 0 | 2046
| Western Downs Green Power Hub | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 399.97 | 394.95 | 399.96 | 399.96 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9712 | 0.017458 | 0 | 2046
| Whitsunday Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Solar | 57.5 | 54.11 | 54.9 | 56 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.901 | 0.017458 | 0 | 2048
| Yarranlea Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 102.96 | 102.96 | 102.96 | 102.96 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9914 | 0.017458 | 0 | 2044
| Adelaide Desalination Plant Solar Farm | Large scale Solar PV | SA | CSA | N/A | Solar | 11 | 10.34 | 10.56 | 11 | 0 | 18.18 | 0 | 0 | 0 | 0 | 1.0039 | 0.017458 | 0 | 2041
| Bolivar Waste Water Treatment Solar Farm | Large scale Solar PV | SA | CSA | N/A | Solar | 11.25 | 10.57 | 10.8 | 11.25 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9949 | 0.017458 | 0 | 2045
| Bungala One Solar Farm | Large scale Solar PV | SA | CSA | Northern SA | Solar | 135 | 104.76 | 109.62 | 109.62 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9601 | 0.017458 | 0 | 2044
| Bungala Two Solar Farm | Large scale Solar PV | SA | CSA | Northern SA | Solar | 135 | 104.76 | 109.62 | 109.62 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9601 | 0.017458 | 0 | 2044
| Happy Valley Reservoir | Large scale Solar PV | SA | CSA | N/A | Solar | 8.34 | 7.82 | 7.99 | 8.32 | 0 | 18.18 | 0 | 0 | 0 | 0 | 1.0041 | 0.017458 | 0 | 2041
| Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | Large scale Solar PV | SA | SESA | South East SA | Solar | 16.8 | 15.79 | 16.12 | 16.8 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9943 | 0.017458 | 0 | 2041
| Mannum Adelaide Pumping Station No 3 - MAPL3 (Tungkillo) | Large scale Solar PV | SA | SESA | South East SA | Solar | 12.36 | 11.64 | 11.88 | 12.36 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9946 | 0.017458 | 0 | 2041
| Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | Large scale Solar PV | SA | CSA | Riverland | Solar | 6.12 | 5.76 | 5.88 | 6.12 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9847 | 0.017458 | 0 | 2031
| Morgan To Whyalla Pipeline No 2 PS | Large scale Solar PV | SA | CSA | Riverland | Solar | 5.88 | 5.5 | 5.62 | 5.86 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.988 | 0.017458 | 0 | 2041
| Morgan To Whyalla Pipeline No 3 PS | Large scale Solar PV | SA | CSA | Riverland | Solar | 7.38 | 6.93 | 7.07 | 7.37 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9847 | 0.017458 | 0 | 2045
| Morgan To Whyalla Pipeline No 4 PS | Large scale Solar PV | SA | CSA | Riverland | Solar | 5.88 | 5.5 | 5.62 | 5.86 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9796 | 0.017458 | 0 | 2041
| Murray Bridge - Onkaparinga Pipeline Pump 2 | Large scale Solar PV | SA | SESA | South East SA | Solar | 13.74 | 12.91 | 13.19 | 13.74 | 0 | 18.18 | 0 | 0 | 0 | 0 | 1.0006 | 0.017458 | 0 | 2041
| Port Augusta Renewable Energy Park - Solar | Large scale Solar PV | SA | CSA | Northern SA | Solar | 79.2 | 79.2 | 79.2 | 79.2 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9654 | 0.017458 | 0 | 2047
| Tailem Bend Solar Farm | Large scale Solar PV | SA | CSA | N/A | Solar | 108 | 95 | 95 | 95 | 0 | 18.18 | 0 | 0 | 0 | 0 | 1.003 | 0.017458 | 0 | 2049
| Tailem Bend Solar Farm - stage 2 | Large scale Solar PV | SA | CSA | N/A | Solar | 105 | 87 | 87 | 87 | 0 | 18.18 | 0 | 0 | 0 | 0 | 1.0079 | 0.017458 | 0 | 2053
| Bannerton Solar Park | Large scale Solar PV | VIC | VIC | Murray River | Solar | 100 | 84 | 84 | 88 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8947 | 0.017458 | 0 | 2049
| Cohuna Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Solar | 31.16 | 24.51 | 27.17 | 27.17 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9413 | 0.017458 | 0 | 2045
| Gannawarra Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Solar | 55 | 47.76 | 49.01 | 50 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9413 | 0.017458 | 0 | 2048
| Glenrowan West Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Solar | 132 | 102.96 | 106.94 | 110.01 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9675 | 0.017458 | 0 | 2051
| Karadoc Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Solar | 104.5 | 90.02 | 90.02 | 90.02 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8877 | 0.017458 | 0 | 2048
| Kiamal Solar Farm stage 1 | Large scale Solar PV | VIC | VIC | Murray River | Solar | 199.95 | 189 | 198 | 199.95 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8775 | 0.017458 | 0 | 2049
| Numurkah Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Solar | 101.09 | 99.95 | 99.95 | 99.95 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9738 | 0.017458 | 0 | 2044
| Wemen Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Solar | 97.5 | 82.36 | 85.52 | 87.98 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8947 | 0.017458 | 0 | 2049
| Winton Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Solar | 85 | 84.99 | 85 | 85 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9675 | 0.017458 | 0 | 2051
| Wyalong Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Solar | 62.32 | 53.01 | 53.01 | 53.01 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9108 | 0.017458 | 0 | 2053
| Yatpool Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Solar | 94 | 79.2 | 81 | 81 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8877 | 0.017458 | 0 | 2050
| Bango 973 Wind Farm | Wind | NSW | SNSW | N/A | Wind | 159 | 0 | 159 | 159 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9159 | 0.069759 | 0 | 2045
| Bango 999 Wind Farm | Wind | NSW | SNSW | N/A | Wind | 84.8 | 0 | 84.8 | 84.8 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9288 | 0.069759 | 0 | 2045
| Boco Rock Wind Farm | Wind | NSW | SNSW | Cooma-Monaro | Wind | 113 | 104.08 | 113.18 | 113.18 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9444 | 0.069759 | 0 | 2040
| Bodangora Wind Farm | Wind | NSW | CNSW | Central-West Orana | Wind | 113.19 | 113.19 | 113.19 | 113.19 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9622 | 0.069759 | 0 | 2049
| Capital Wind Farm | Wind | NSW | SNSW | N/A | Wind | 140.7 | 140.7 | 140.7 | 140.7 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9575 | 0.069759 | 0 | 2040
| Collector Wind Farm | Wind | NSW | SNSW | N/A | Wind | 226.8 | 124.2 | 210.6 | 218.7 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9576 | 0.069759 | 0 | 2046
| Crookwell 2 Wind Farm | Wind | NSW | SNSW | N/A | Wind | 96.04 | 91 | 91 | 91 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9608 | 0.069759 | 0 | 2043
| Crudine Ridge Wind Farm | Wind | NSW | CNSW | N/A | Wind | 141.71 | 0 | 138.01 | 138.01 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.926 | 0.069759 | 0 | 2041
| Cullerin Range Wind Farm | Wind | NSW | SNSW | N/A | Wind | 30 | 30 | 30 | 30 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9437 | 0.069759 | 0 | 2038
| Gullen Range Wind Farm | Wind | NSW | SNSW | N/A | Wind | 165.5 | 165.5 | 165.5 | 165.5 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.958 | 0.069759 | 0 | 2100
| Gullen Range Wind Farm 2 | Wind | NSW | SNSW | N/A | Wind | 110.67 | 105.4 | 110.67 | 110.67 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.958 | 0.069759 | 0 | 2120
| Gunning Wind Farm | Wind | NSW | SNSW | N/A | Wind | 46.5 | 46.5 | 46.5 | 46.5 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9437 | 0.069759 | 0 | 2036
| Sapphire Wind Farm | Wind | NSW | NNSW | New England | Wind | 270 | 155.7 | 252 | 270 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9086 | 0.069759 | 0 | 2043
| Silverton Wind Farm | Wind | NSW | SNSW | Broken Hill | Wind | 198.94 | 119.48 | 198.01 | 198.01 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8101 | 0.069759 | 0 | 2043
| Taralga Wind Farm | Wind | NSW | CNSW | N/A | Wind | 106.8 | 106.8 | 106.8 | 106.8 | 0 | 26.73 | 0 | 0 | 0 | 0 | 1.0095 | 0.069759 | 0 | 2040
| White Rock Wind Farm - Stage 1 | Wind | NSW | NNSW | New England | Wind | 172.48 | 0 | 172.48 | 172.48 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8289 | 0.069759 | 0 | 2038
| Woodlawn Wind Farm | Wind | NSW | SNSW | N/A | Wind | 48.3 | 48.3 | 48.3 | 48.3 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9575 | 0.069759 | 0 | 2041
| Coopers Gap Wind Farm | Wind | QLD | SQ | Darling Downs | Wind | 452.89 | 439.97 | 439.97 | 439.97 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9658 | 0.069759 | 0 | 2044
| Kaban Green Power Hub - Wind Farm | Wind | QLD | NQ | Far North QLD | Wind | 156.8 | 151.98 | 151.98 | 151.98 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9575 | 0.069759 | 0 | 2048
| Kennedy Energy Park Wind Farm | Wind | QLD | NQ | North Qld Clean Energy Hub | Wind | 43.2 | 36 | 43.2 | 43.2 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9667 | 0.069759 | 0 | 2046
| Mount Emerald Wind Farm | Wind | QLD | NQ | Far North QLD | Wind | 180.52 | 166.95 | 180.46 | 180.46 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9472 | 0.069759 | 0 | 2043
| Canunda Wind Farm | Wind | SA | SESA | South East SA | Wind | 46 | 0 | 46 | 46 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9671 | 0.069759 | 0 | 2035
| Cathedral Rocks Wind Farm | Wind | SA | CSA | Eastern Eyre Peninsula | Wind | 62 | 0 | 0 | 0 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9319 | 0.069759 | 0 | 2030
| Clements Gap Wind Farm | Wind | SA | CSA | Mid-North SA | Wind | 56.7 | 56.7 | 56.7 | 56.7 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9522 | 0.069759 | 0 | 2039
| Hallett 4 North Brown Hill Wind Farm | Wind | SA | CSA | Mid-North SA | Wind | 132.3 | 88.2 | 131.98 | 131.98 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9599 | 0.069759 | 0 | 2036
| Hallett 5 The Bluff Wind Farm | Wind | SA | CSA | Mid-North SA | Wind | 52.5 | 35 | 52.5 | 52.5 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.957 | 0.069759 | 0 | 2036
| Hallett Stage 1 Brown Hill Wind Farm | Wind | SA | CSA | Mid-North SA | Wind | 94.5 | 63 | 94.5 | 94.5 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9599 | 0.069759 | 0 | 2043
| Hallett Stage 2 Hallett Hill Wind Farm | Wind | SA | CSA | Mid-North SA | Wind | 71.4 | 47.6 | 71.4 | 71.4 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.957 | 0.069759 | 0 | 2035
| Hornsdale Wind Farm Stage 1 | Wind | SA | CSA | Mid-North SA | Wind | 102.4 | 100 | 100 | 100 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9467 | 0.069759 | 0 | 2056
| Hornsdale Wind Farm Stage 2 | Wind | SA | CSA | Mid-North SA | Wind | 102.4 | 100 | 100 | 100 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9467 | 0.069759 | 0 | 2057
| Hornsdale Wind Farm Stage 3 | Wind | SA | CSA | Mid-North SA | Wind | 112 | 108.99 | 108.99 | 108.99 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9467 | 0.069759 | 0 | 2057
| Lake Bonney 1 Wind Farm | Wind | SA | SESA | South East SA | Wind | 80.5 | 80.5 | 80.5 | 80.5 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9656 | 0.069759 | 0 | 2035
| Lake Bonney 2 Wind Farm | Wind | SA | SESA | South East SA | Wind | 159 | 159 | 159 | 159 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9656 | 0.069759 | 0 | 2038
| Lake Bonney 3 Wind Farm | Wind | SA | SESA | South East SA | Wind | 39 | 39 | 39 | 39 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9656 | 0.069759 | 0 | 2040
| Lincoln Gap Wind Farm - stage 1 | Wind | SA | CSA | Northern SA | Wind | 126 | 42 | 122.5 | 122.5 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9601 | 0.069759 | 0 | 2045
| Lincoln Gap Wind Farm - stage 2 | Wind | SA | CSA | Northern SA | Wind | 86.4 | 38.4 | 84 | 84 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9601 | 0.069759 | 0 | 2045
| Mount Millar Wind Farm | Wind | SA | CSA | Eastern Eyre Peninsula | Wind | 72.28 | 72.28 | 72.28 | 72.28 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9259 | 0.069759 | 0 | 2035
| Port Augusta Renewable Energy Park - Wind | Wind | SA | CSA | Northern SA | Wind | 210 | 210 | 210 | 210 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9654 | 0.069759 | 0 | 2052
| Snowtown S2 Wind Farm | Wind | SA | CSA | Mid-North SA | Wind | 270 | 249.75 | 270 | 270 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9638 | 0.069759 | 0 | 2039
| Snowtown Wind Farm | Wind | SA | CSA | Mid-North SA | Wind | 98.7 | 65.8 | 98.7 | 98.7 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8968 | 0.069759 | 0 | 2033
| Starfish Hill Wind Farm | Wind | SA | CSA | N/A | Wind | 33 | 0 | 0 | 0 | 0 | 26.73 | 0 | 0 | 0 | 0 | 1.0039 | 0.069759 | 0 | 2027
| Waterloo Wind Farm | Wind | SA | CSA | Mid-North SA | Wind | 130.8 | 9 | 129.9 | 130.8 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9599 | 0.069759 | 0 | 2045
| Wattle Point Wind Farm | Wind | SA | CSA | Yorke Peninsula | Wind | 90.75 | 0 | 0 | 0 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8073 | 0.069759 | 0 | 2029
| Willogoleche Wind Farm | Wind | SA | CSA | Mid-North SA | Wind | 119.36 | 0 | 119.36 | 119.36 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9534 | 0.069759 | 0 | 2043
| Cattle Hill Wind Farm | Wind | TAS | TAS | Central Highlands | Wind | 144 | 144 | 144 | 144 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8888 | 0.069759 | 0 | 2044
| Granville Harbour Wind Farm | Wind | TAS | TAS | North West Tasmania | Wind | 111.6 | 111.6 | 111.6 | 111.6 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9388 | 0.069759 | 0 | 2055
| Musselroe Wind Farm | Wind | TAS | TAS | N/A | Wind | 168 | 168 | 168 | 168 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9119 | 0.069759 | 0 | 2050
| Woolnorth Wind Farm | Wind | TAS | TAS | N/A | Wind | 139.75 | 139.75 | 139.75 | 139.75 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9112 | 0.069759 | 0 | 2050
| Ararat Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 240 | 150 | 240 | 240 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8899 | 0.069759 | 0 | 2047
| Bald Hills Wind Farm | Wind | VIC | VIC | N/A | Wind | 106.6 | 106.6 | 106.6 | 106.6 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9825 | 0.069759 | 0 | 2040
| Berrybank Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 290 | 281.1 | 281.1 | 281.1 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9397 | 0.069759 | 0 | 2050
| Bulgana Green Power Hub - Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 204.4 | 204.4 | 204.4 | 204.4 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8821 | 0.069759 | 0 | 2049
| Challicum Hills Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 52.5 | 52.5 | 52.5 | 52.5 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9759 | 0.069759 | 0 | 2033
| Cherry Tree Wind Farm | Wind | VIC | VIC | N/A | Wind | 57.6 | 43.2 | 53.6 | 57.6 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9974 | 0.069759 | 0 | 2050
| Crowlands Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 79.95 | 79.95 | 79.95 | 79.95 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8904 | 0.069759 | 0 | 2050
| Dulacca Wind Farm | Wind | QLD | SQ | Darling Downs | Wind | 172.99 | 160 | 164 | 172.98 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9776 | 0.069759 | 0 | 2053
| Dundonnell Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 336 | 216 | 304 | 336 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.987 | 0.069759 | 0 | 2045
| Elaine Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 83.6 | 59.4 | 73.7 | 83.6 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9576 | 0.069759 | 0 | 2049
| Kiata Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 31.05 | 27 | 29.7 | 31.05 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8827 | 0.069759 | 0 | 2042
| Macarthur Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 420 | 420 | 420 | 420 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9849 | 0.069759 | 0 | 2038
| Moorabool Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 312 | 312 | 312 | 312 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9576 | 0.069759 | 0 | 2044
| Mortlake South Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 157.5 | 157.5 | 157.5 | 157.5 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9528 | 0.069759 | 0 | 2047
| Mortons Lane Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 19.5 | 19.5 | 19.5 | 19.5 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9933 | 0.069759 | 0 | 2042
| Mt Gellibrand Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 138.6 | 0 | 132 | 132 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9896 | 0.069759 | 0 | 2043
| Mt Mercer Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 131.2 | 0 | 131.2 | 131.2 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9576 | 0.069759 | 0 | 2043
| Murra Warra Wind Farm - stage 1 | Wind | VIC | VIC | Western Victoria | Wind | 225.7 | 176.04 | 225.7 | 225.7 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8768 | 0.069759 | 0 | 2049
| Murra Warra Wind Farm - stage 2 | Wind | VIC | VIC | Western Victoria | Wind | 209 | 189.24 | 209 | 209 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.8768 | 0.069759 | 0 | 2052
| Oaklands Hill Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 67.2 | 40.99 | 63 | 63 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9933 | 0.069759 | 0 | 2037
| Portland Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 151.7 | 151.7 | 151.7 | 151.7 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9656 | 0.069759 | 0 | 2040
| Salt Creek Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 54 | 37.5 | 51 | 54 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9476 | 0.069759 | 0 | 2043
| Stockyard Hill Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 527.56 | 510.99 | 510.99 | 510.99 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9869 | 0.069759 | 0 | 2045
| Waubra Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 192 | 192 | 192 | 192 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.924 | 0.069759 | 0 | 2034
| Yaloak South Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 28.7 | 28.7 | 28.7 | 28.7 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9759 | 0.069759 | 0 | 2048
| Yambuk Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 30 | 30 | 30 | 30 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9933 | 0.069759 | 0 | 2040
| Yendon Wind Farm | Wind | VIC | VIC | Western Victoria | Wind | 144.4 | 102.6 | 127.3 | 144.4 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9522 | 0.069759 | 0 | 2049
Committed generators
| Generator | Generator type | Region | ISP sub-region | REZ location | Fuel/technology type | Maximum capacity (MW) | Summer rating (MW) | Summer typical rating (MW) | Winter rating (MW) | Maintenance duration (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate (GJ/MWh HHV s.o.) | Fuel cost ($/GJ) | Emissions (kg/MWh) | MLF | Auxiliary load (%) | SRMC ($/MWh) | Expected retirement year
[15 empty] | Green Energy Exports | Green Energy Exports
[8 empty] | 2030-31 | 2030-31 | 2031 |  |  |  |  | 2041-42 | 2041-42
| Kurri Kurri OCGT | OCGT | NSW | SNW | N/A | OCGT | 750 | 660 | 660 | 660 | 1.3699 | 10.91 | 7.806 | 10.9312 | 17.3809 | 342.6843 | 0.9831 | 0.6143 | 197.8005 | 2064
| Tallawarra B* | OCGT | NSW | SNW | N/A | OCGT | 320 | 318 | 318 | 320 | 1.3699 | 10.91 | 7.806 | 10.9312 | 16.84 | 342.6843 | 0.9856 | 0.6143 | 191.8883 | 2053
| Kidston | Pumped Hydro | QLD | NQ | N/A | Hydro | 250 | 250 | 250 | 250 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9222 | 0.34269 | 8.5797 | 2105
| Snowy 2.0 | Pumped Hydro | NSW | SNSW | Tumut | Hydro | 2200 | 2200.2 | 2200.2 | 2200.2 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9092 | 0.34269 | 8.5797 | 2129
| Girgarre Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Solar | 93.48 | 69.54 | 75.81 | 75.81 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9738 | 0.017458 | 0 | 2054
| Glenrowan Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Solar | 126.5 | 101.98 | 101.98 | 101.98 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9671 | 0.017458 | 0 | 2053
| Mannum Solar Farm 2* | Large scale Solar PV | SA | CSA | Riverland | Solar | 29.99 | 29.98 | 29.98 | 29.98 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9943 | 0.017458 | 0 | 2058
| Metz Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Solar | 135 | 107.08 | 111.72 | 115.02 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8831 | 0.017458 | 0 | 2052
| Riverina Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Solar | 32.4 | 32.4 | 32.4 | 32.4 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8894 | 0.017458 | 0 | 2047
| Sebastopol Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Solar | 90 | 85.8 | 90 | 90 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9108 | 0.017458 | 0 | 2052
| Stubbo Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 400 | 400 | 400 | 400 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9339 | 0.017458 | 0 | 2073
| Walla Walla Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Solar | 303.94 | 299.52 | 299.52 | 299.52 | 0 | 18.18 | 0 | 0 | 0 | 0 | 1 | 0.017458 | 0 | 2054
| Wandoan South Solar Farm - stage 1 | Large scale Solar PV | QLD | SQ | Darling Downs | Solar | 160 | 125 | 125 | 125 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9832 | 0.017458 | 0 | 2053
| Wellington North Solar Farm (Lightsource) | Large scale Solar PV | NSW | CNSW | Central-West Orana | Solar | 436.8 | 329.99 | 329.99 | 329.99 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9439 | 0.017458 | 0 | 2054
| Wollar Solar Farm | Large scale Solar PV | NSW | CNSW | N/A | Solar | 280 | 280 | 280 | 280 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9339 | 0.017458 | 0 | 2054
| Woolooga Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Solar | 222.5 | 157.53 | 175.95 | 175.95 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9832 | 0.017458 | 0 | 2052
| Wunghnu Solar Farm | Large scale Solar PV | VIC | VIC | N/A | Solar | 93.5 | 75 | 75 | 75 | 0 | 18.18 | 0 | 0 | 0 | 0 | 1 | 0.017458 | 0 | 2054
| Clarke Creek Wind Farm | Wind | QLD | CQ | Isaac | Wind | 450 | 439 | 439 | 439 | 0 | 26.73 | 0 | 0 | 0 | 0 | 1 | 0.069759 | 0 | 2049
| Crookwell 3 Wind Farm | Wind | NSW | SNSW | N/A | Wind | 57.6 | 57.6 | 57.6 | 57.6 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9611 | 0.069759 | 0 | 2054
| Flyers Creek Wind Farm | Wind | NSW | CNSW | Central-West Orana | Wind | 145.54 | 145.54 | 145.54 | 145.54 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.926 | 0.069759 | 0 | 2063
| Golden Plains Wind Farm East | Wind | VIC | VIC | South West Victoria | Wind | 756.4 | 756.4 | 756.4 | 756.4 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9576 | 0.069759 | 0 | 2054
| Goyder South Wind Farm 1A | Wind | SA | CSA | Mid-North SA | Wind | 209 | 200.98 | 200.98 | 200.98 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.957 | 0.069759 | 0 | 2048
| Goyder South Wind Farm 1B | Wind | SA | CSA | Mid-North SA | Wind | 203.5 | 195.69 | 195.69 | 195.69 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.957 | 0.069759 | 0 | 2049
| Hawkesdale Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 96.6 | 96.6 | 96.6 | 96.6 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9849 | 0.069759 | 0 | 2054
| Ryan Corner Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 218.4 | 218.4 | 218.4 | 218.4 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9849 | 0.069759 | 0 | 2054
| Rye Park Wind Farm | Wind | NSW | SNSW | N/A | Wind | 396 | 225.06 | 335.28 | 386.1 | 0 | 26.73 | 0 | 0 | 0 | 0 | 1 | 0.069759 | 0 | 2048
| Wambo Wind Farm | Wind | QLD | SQ | Darling Downs | Wind | 252 | 252 | 252 | 252 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9658 | 0.069759 | 0 | 2055
Anticipated projects
| Generator | Generator type | Region | ISP sub-region | REZ location | Fuel/technology type | Maximum capacity (MW) | Summer rating (MW) | Summer typical rating (MW) | Winter rating (MW) | Maintenance duration (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate (GJ/MWh HHV s.o.) | Fuel cost ($/GJ) | Emissions (kg/MWh) | MLF | Auxiliary load (%) | SRMC ($/MWh) | Expected retirement year
[15 empty] | Green Energy Exports | Green Energy Exports
[8 empty] | 2030-31 | 2030-31 | 2027 |  |  |  |  | 2041-42 | 2041-42
| SA Hydrogen Turbine | Hydrogen-based gas turbines | SA | CSA | N/A | Hydrogen-based gas turbines | 200 | 200 | 200 | 200 | 1.37 | 69.5045 | 40.6334 | 12.72 | 22.8511 | 290.4923 | 0.9601 | 1.5 | 331.2989 | 2065
| Borumba | Pumped Hydro | QLD | SQ | Banana | Hydro | 1998 | 0 | 0 | 0 | 0.27397 | 69.51 | 8.5797 | 0 | 0 | 0 | 0.9736 | 0.34269 | 8.5797 | 2130
| Aramara Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Solar | 101.4 | 101.4 | 101.4 | 101.4 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9704 | 0.017458 | 0 | 2048
| Banksia Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Solar | 60 | 58.8 | 60 | 60 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9704 | 0.017458 | 0 | 2055
| Culcairn Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Solar | 349.98 | 332.44 | 349.98 | 349.98 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.907 | 0.017458 | 0 | 2050
| Cultana Solar Farm | Large scale Solar PV | SA | CSA | Northern SA | Solar | 357.45 | 279.76 | 279.76 | 279.76 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9601 | 0.017458 | 0 | 2055
| Derby Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Solar | 95.1 | 95.1 | 95.1 | 95.1 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9413 | 0.017458 | 0 | 2053
| Frasers Solar Farm | Large scale Solar PV | VIC | VIC | Gippsland | Solar | 77 | 77 | 77 | 77 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9764 | 0.017458 | 0 | 2054
| Horsham Solar Farm | Large scale Solar PV | VIC | VIC | Western Victoria | Solar | 118.8 | 118.8 | 118.8 | 118.8 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8775 | 0.017458 | 0 | 2066
| Lockhart Hybrid Facility - Solar | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Solar | 10 | 9.9 | 9.9 | 9.9 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.907 | 0.017458 | 0 | 2055
| Quorn Park Solar Farm | Large scale Solar PV | NSW | CNSW | N/A | Solar | 96.8 | 79.86 | 79.86 | 79.86 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9 | 0.017458 | 0 | 2055
| Tamworth Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Solar | 65 | 65 | 65 | 65 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8289 | 0.017458 | 0 | 2053
| Tilbuster Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Solar | 248.82 | 200.64 | 200.64 | 200.64 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8718 | 0.017458 | 0 | 2055
| MacIntyre Wind Farm | Wind | QLD | SQ | Darling Downs | Wind | 923.4 | 923.4 | 923.4 | 923.4 | 0 | 26.73 | 0 | 0 | 0 | 0 | 1 | 0.069759 | 0 | 2053
Uungula Wind Farm Green Energy Exports | Uungula Wind Farm | Wind | NSW | CNSW | Central-West Orana | Wind | 414 | 0 | 414 | 414 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9622 | 0.069759 | 0 | 2055
Woolsthorpe Wind Farm Green Energy Exports | Woolsthorpe Wind Farm | Wind | VIC | VIC | South West Victoria | Wind | 73.2 | 73.2 | 73.2 | 73.2 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9933 | 0.069759 | 0 | 2055
Existing, Committed and Anticipated batteries
| Generator | Generator type | Region | ISP sub-region | REZ location | Fuel/technology type | Maximum capacity (MW) | Summer rating (MW) | Summer typical rating (MW) | Winter rating (MW) | Maintenance duration (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate (GJ/MWh HHV s.o.) | Fuel cost ($/GJ) | Emissions (kg/MWh) | MLF | Auxiliary load (%) | SRMC ($/MWh) | Expected retirement year
[15 empty] | Green Energy Exports | Green Energy Exports
[8 empty] | 2030-31 | 2030-31 | 2027 |  |  |  |  | 2041-42 | 2041-42
| Adelaide Desalination Plant BESS | Battery Storage | SA | CSA | N/A | Battery Storage | 6.27 | 6 | 6 | 6 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.0036 | 0 | 0 | 2041
| Aldoga BESS Stage 1 | Battery Storage | QLD | GG | N/A | Battery Storage | 400 | 400 | 400 | 400 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.9329 | 0 | 0 | 2045
| Ballarat Energy Storage System | Battery Storage | VIC | VIC | Western Victoria | Battery Storage | 30 | 19.2 | 19.9 | 29.9 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.9756 | 0 | 0 | 2033
| Blyth BESS | Battery Storage | SA | CSA | Mid-North SA | Battery Storage | 200 | 193.98 | 200 | 200 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.8968 | 0 | 0 | 2044
| Bolivar Waste Water Treatment BESS | Battery Storage | SA | CSA | N/A | Battery Storage | 2.46 | 2 | 2 | 2 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.0002 | 0 | 0 | 2045
| Bouldercombe Battery project | Battery Storage | QLD | CQ | Fitzroy | Battery Storage | 50 | 50 | 50 | 50 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9181 | 0 | 0 | 2042
| Broken Hill BESS | Battery Storage | NSW | SNSW | Broken Hill | Battery Storage | 50 | 50 | 50 | 50 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.8324 | 0 | 0 | 2043
| Bulgana Green Power Hub BESS | Battery Storage | VIC | VIC | Western Victoria | Battery Storage | 20 | 20 | 20 | 20 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.8821 | 0 | 0 | 2049
| Bungama Solar BESS | Battery Storage | SA | CSA | Mid-North SA | Battery Storage | 150 | 150 | 150 | 150 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.8968 | 0 | 0 | 2045
| Capital Battery | Battery Storage | NSW | SNSW | Tumut | Battery Storage | 100.32 | 99 | 99.99 | 99.99 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9575 | 0 | 0 | 2048
| Chinchilla BESS | Battery Storage | QLD | SQ | Darling Downs | Battery Storage | 100 | 100 | 100 | 100 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9712 | 0 | 0 | 2038
| Christies Beach Wastewater Treatment Plant BESS | Battery Storage | SA | CSA | N/A | Battery Storage | 2.09 | 2 | 2 | 2 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.0036 | 0 | 0 | 2041
| Dalrymple BESS | Battery Storage | SA | CSA | Yorke Peninsula | Battery Storage | 30 | 0 | 0 | 30 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.8954 | 0 | 0 | 2030
| Darlington Point Energy Storage System | Battery Storage | NSW | SNSW | N/A | Battery Storage | 25 | 25 | 25 | 25 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.8958 | 0 | 0 | 2051
| Eraring Big Battery | Battery Storage | NSW | SNW | Hunter Central Coast | Battery Storage | 460 | 460 | 460 | 460 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9848 | 0 | 0 | 2045
| Gannawarra Energy Storage System | Battery Storage | VIC | VIC | Murray River | Battery Storage | 25.33 | 25.33 | 25.33 | 25.33 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.029 | 0 | 0 | 2033
| Gnarwarre BESS | Battery Storage | VIC | VIC | South West Victoria | Battery Storage | 290 | 250 | 250 | 250 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9848 | 0 | 0 | 2054
| Happy Valley Reservoir BESS | Battery Storage | SA | CSA | N/A | Battery Storage | 4.41 | 4 | 4 | 4 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.0041 | 0 | 0 | 2041
| Hazelwood BESS | Battery Storage | VIC | VIC | Gippsland | Battery Storage | 200.07 | 150 | 150 | 150 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.9764 | 0 | 0 | 2043
| Hornsdale Power Reserve Unit 1 | Battery Storage | SA | CSA | Mid-North SA | Battery Storage | 150 | 150 | 150 | 150 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.9653 | 0 | 0 | 2057
| Koorangie Energy Storage System | Battery Storage | VIC | VIC | Murray River | Battery Storage | 185 | 185 | 185 | 185 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.029 | 0 | 0 | 2055
| Lake Bonney BESS | Battery Storage | SA | SESA | South East SA | Battery Storage | 25 | 25 | 25 | 25 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.979 | 0 | 0 | 2034
| Liddell BESS | Battery Storage | NSW | CNSW | Hunter-Central Coast | Battery Storage | 500 | 500 | 500 | 500 | 0 | 17.32 | 0 | 0 | 0 | 0 | 0.9831 | 0 | 0 | 2045
| Lincoln Gap Wind Farm BESS | Battery Storage | SA | CSA | Northern SA | Battery Storage | 10 | 10 | 10 | 10 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.9601 | 0 | 0 | 2045
| Lockhart Hybrid Facility - Battery | Battery Storage | NSW | SNSW | Wagga Wagga | Battery Storage | 10 | 9.9 | 9.9 | 9.9 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.8383 | 0 | 0 | 2045
| Melbourne Renewable Energy Hub - Side A | Battery Storage | VIC | VIC | N/A | Battery Storage | 600 | 600 | 600 | 600 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9885 | 0 | 0 | 2050
| Mornington BESS | Battery Storage | VIC | VIC | N/A | Battery Storage | 240 | 240 | 240 | 240 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9885 | 0 | 0 | 2046
| Mortlake Battery | Battery Storage | VIC | VIC | South West Victoria | Battery Storage | 300 | 300 | 300 | 300 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9885 | 0 | 0 | 2047
| Mt Fox BESS | Battery Storage | QLD | NQ | Northern Qld | Battery Storage | 300 | 300 | 300 | 300 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9559 | 0 | 0 | 2046
| New England Solar Farm BESS | Battery Storage | NSW | NNSW | New England | Battery Storage | 200 | 200 | 200 | 200 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.8718 | 0 | 0 | 2046
| Orana BESS | Battery Storage | NSW | CNSW | Central-West Orana | Battery Storage | 408.48 | 368.46 | 408.48 | 408.48 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9439 | 0 | 0 | 2065
| Philip Island BESS | Battery Storage | VIC | VIC | N/A | Battery Storage | 5 | 5 | 5 | 5 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9825 | 0 | 0 | 2038
| Queanbeyan BESS | Battery Storage | NSW | SNSW | Tumut | Battery Storage | 10 | 10 | 10 | 10 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9575 | 0 | 0 | 2042
| Quorn Park BESS | Battery Storage | NSW | CNSW | N/A | Battery Storage | 27.6 | 20 | 20 | 20 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9865 | 0 | 0 | 2045
| Rangebank BESS | Battery Storage | VIC | VIC | N/A | Battery Storage | 200 | 200 | 200 | 200 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9764 | 0 | 0 | 2044
| Richmond Valley BESS | Battery Storage | NSW | NNSW | N/A | Battery Storage | 275 | 275 | 275 | 275 | 0 | 30.6889 | 0 | 0 | 0 | 0 | 0.8718 | 0 | 0 | 2046
| Riverina Energy Storage System 1 | Battery Storage | NSW | SNSW | N/A | Battery Storage | 60 | 60 | 60 | 60 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.8958 | 0 | 0 | 2051
| Riverina Energy Storage System 2 | Battery Storage | NSW | SNSW | N/A | Battery Storage | 65 | 65 | 65 | 65 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.8958 | 0 | 0 | 2051
| Sapphire Wind Farm BESS | Battery Storage | NSW | NNSW | New England | Battery Storage | 30 | 30 | 30 | 30 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.9086 | 0 | 0 | 2033
| Stanwell BESS | Battery Storage | QLD | CQ | Fitzroy | Battery Storage | 150 | 150 | 150 | 150 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9181 | 0 | 0 | 2047
| Swanbank BESS | Battery Storage | QLD | SQ | N/A | Battery Storage | 250 | 250 | 250 | 250 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9987 | 0 | 0 | 2045
| Tailem Bend Battery Project | Battery Storage | SA | CSA | N/A | Battery Storage | 41.5 | 41.5 | 41.5 | 41.5 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.003 | 0 | 0 | 2048
| Tamworth BESS | Battery Storage | NSW | NNSW | N/A | Battery Storage | 200 | 200 | 200 | 200 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9831 | 0 | 0 | 2046
| Tarong BESS | Battery Storage | QLD | SQ | Darling Downs | Battery Storage | 300 | 300 | 300 | 300 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.9751 | 0 | 0 | 2044
| Templers BESS | Battery Storage | SA | CSA | Mid-North SA | Battery Storage | 111 | 111 | 111 | 111 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.0048 | 0 | 0 | 2049
| Terang BESS | Battery Storage | VIC | VIC | South West Victoria | Battery Storage | 101.5 | 101.5 | 101.5 | 101.5 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9756 | 0 | 0 | 2045
| Torrens Island BESS | Battery Storage | SA | CSA | N/A | Battery Storage | 250.7 | 250.7 | 250.7 | 250.7 | 0 | 7.59 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2043
| Ulinda Park BESS | Battery Storage | QLD | SQ | Darling Downs | Battery Storage | 154.96 | 154.96 | 154.96 | 154.96 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9712 | 0 | 0 | 2063
| Victorian Big Battery | Battery Storage | VIC | VIC | N/A | Battery Storage | 300 | 50 | 50 | 300 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9885 | 0 | 0 | 2041
| Wallgrove Grid Battery project | Battery Storage | NSW | SNW | N/A | Battery Storage | 50 | 50 | 50 | 50 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.001 | 0 | 0 | 2036
| Wandoan South BESS | Battery Storage | QLD | SQ | Darling Downs | Battery Storage | 100 | 100 | 100 | 100 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9751 | 0 | 0 | 2051
| Waratah Super Battery | Battery Storage | NSW | SNW | N/A | Battery Storage | 850.18 | 777.6 | 850.17 | 150.04 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9831 | 0 | 0 | 2065
| Western Downs Battery | Battery Storage | QLD | SQ | Darling Downs | Battery Storage | 336 | 254.8 | 254.8 | 254.8 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.9673 | 0 | 0 | 2048
| Wooreen Energy Storage System | Battery Storage | VIC | VIC | Gippsland | Battery Storage | 350 | 350 | 350 | 350 | 0 | 17.32 | 0 | 0 | 0 | 0 | 0.9764 | 0 | 0 | 2046
Additional projects
| Generator | Generator type | Region | ISP sub-region | REZ location | Fuel/technology type | Maximum capacity (MW) | Summer rating (MW) | Summer typical rating (MW) | Winter rating (MW) | Maintenance duration (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate (GJ/MWh HHV s.o.) | Fuel cost ($/GJ) | Emissions (kg/MWh) | MLF | Auxiliary load (%) | SRMC ($/MWh) | Expected retirement year
[15 empty] | Green Energy Exports | Green Energy Exports
[8 empty] | 2030-31 | 2030-31 | 2031 |  |  |  |  | 2023-24 | 2027-28
| Coppabella Wind Farm | Wind | NSW | SNSW | Tumut | Wind | 289.8 | 270.48 | 270.48 | 270.48 | 0 | 26.73 | 0 | 0 | 0 | 0 | 0.9437 | 0.069759 | 0 | 2057
| Derby Solar Project BESS | Battery Storage | VIC | VIC | Murray River | Battery Storage | 85 | 85 | 85 | 85 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.9756 | 0 | 0 | 2045
| Fulham Solar Farm | Large scale Solar PV | VIC | VIC | Gippsland | Solar | 100.8 | 83.28 | 83.28 | 83.28 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.9804 | 0.017458 | 0 | 2055
| Fulham Solar Farm BESS | Battery Storage | VIC | VIC | Gippsland | Battery Storage | 64.8 | 64.8 | 64.8 | 64.8 | 0 | 7.59 | 0 | 0 | 0 | 0 | 0.9804 | 0 | 0 | 2045
| Goulburn River BESS | Battery Storage | NSW | CNSW | N/A | Battery Storage | 49 | 49 | 49 | 49 | 0 | 30.6889 | 0 | 0 | 0 | 0 | 0.9831 | 0 | 0 | 2045
| Horsham Solar Farm BESS | Battery Storage | VIC | VIC | Western Victoria | Battery Storage | 50.01 | 50.01 | 50.01 | 50.01 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.8821 | 0 | 0 | 2045
| Kiamal Solar Farm – Stage 2 | Large scale Solar PV | VIC | VIC | Murray River | Solar | 150.04 | 141.9 | 148.5 | 150.04 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8775 | 0.017458 | 0 | 2056
| Kiamal Solar Farm – Stage 2 BESS | Battery Storage | VIC | VIC | Murray River | Battery Storage | 150.04 | 141.9 | 148.5 | 150.04 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0.8775 | 0 | 0 | 2046
| Kogan Gas | Hydrogen-based gas turbines | QLD | SQ | N/A | Hydrogen-based gas turbines | 200 | 168 | 184 | 200 | 1.37 | 69.5045 | 40.6334 | 12.72 | 0 | 580.9847 | 0.9673 | 1.5 | 40.6334 | 2066
| Limondale BESS | Battery Storage | NSW | SNSW | South West NSW | Battery Storage | 50 | 50 | 50 | 50 | 0 | 30.6889 | 0 | 0 | 0 | 0 | 0.8255 | 0 | 0 | 2045
New England Solar Farm - stage 2 Green Energy Exports | New England Solar Farm - stage 2 | Large scale Solar PV | NSW | NNSW | New England | Solar | 320 | 320 | 320 | 320 | 0 | 18.18 | 0 | 0 | 0 | 0 | 0.8718 | 0.017458 | 0 | 2055
| Silver City Energy Storage | Battery Storage | NSW | SNSW | Broken Hill | Battery Storage | 200 | 200 | 200 | 200 | 0 | 30.6889 | 0 | 0 | 0 | 0 | 0.8324 | 0 | 0 | 2057
| Smithfield BESS | Battery Storage | NSW | SNW | N/A | Battery Storage | 65 | 65 | 65 | 65 | 0 | 10.8 | 0 | 0 | 0 | 0 | 1.001 | 0 | 0 | 2045

## Fuel Price Summary
Go to Assumptions Summary
Fuel Price ($/GJ)
Fuel prices for existing, committed, anticipated and new entrant generators for the selected scenario.
Scenario | Green Energy Exports | [8 empty] | Green Energy Exports |  | Step Change |  | Progressive Change
Gas price scenario | Green Energy Exports | [5 empty] | Gas price scenario |  |  | Green Energy Exports |  | Step Change |  | Progressive Change
Coal price scenario | Low price | [5 empty] | Coal and biomass price scenario |  |  | Low price |  | Central |  | High price
Hydrogen price scenario | Hydrogen Export | [5 empty] | Hydrogen price scenario |  |  | Hydrogen Export |  | - |  | -
Existing generators
Generator | Region | Fuel type | REZ/Sub-region | Fuel cost mapping | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Bayswater | NSW | Black Coal | CNSW | Bayswater | 1.9824 | 2.0062 | 1.9561 | 1.9145 | 3.0484 | 3.0074 | 2.9855 | 2.9817 | 2.9628 | 2.9444 | 2.9237 | 2.8964 | 2.8703 | 2.8159 | 2.7335 | 2.6516 | 2.5702 | 2.5482 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537
Eraring | NSW | Black Coal | SNW | Eraring | 9.5273 | 4.4702 | 4.096 | 3.4804 | 3.3301 | 3.2853 | 3.2614 | 3.2415 | 3.2222 | 3.2035 | 3.1823 | 3.1525 | 3.1227 | 3.0608 | 2.967 | 2.8738 | 2.7811 | 2.6891 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433
Mt Piper | NSW | Black Coal | CNSW | Mt Piper | 3.7259 | 3.6285 | 4.096 | 3.4804 | 3.3301 | 3.2853 | 3.2614 | 3.2415 | 3.2222 | 3.2035 | 3.1823 | 3.1525 | 3.1227 | 3.0608 | 2.967 | 2.8738 | 2.7811 | 2.6891 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433
Vales Point B | NSW | Black Coal | SNW | Vales Point B | 8.8331 | 4.2021 | 3.911 | 3.3632 | 3.2491 | 3.2284 | 3.2186 | 3.2104 | 3.2025 | 3.1949 | 3.1848 | 3.166 | 3.1473 | 3.1082 | 3.0487 | 2.9893 | 2.9298 | 2.8703 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406
Callide B | QLD | Black Coal | CQ | Callide B | 2.3084 | 2.3197 | 2.3264 | 2.3272 | 2.3279 | 2.3287 | 2.3294 | 2.3302 | 2.3309 | 2.3317 | 2.3324 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328
Callide C | QLD | Black Coal | CQ | Callide C | 2.3084 | 2.3197 | 2.3264 | 2.3272 | 2.3279 | 2.3287 | 2.3294 | 2.3302 | 2.3309 | 2.3317 | 2.3324 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328
Gladstone | QLD | Black Coal | GG | Gladstone | 7.6869 | 3.8512 | 3.5675 | 3.1005 | 3.0973 | 3.1306 | 3.1668 | 3.2037 | 3.2119 | 3.1908 | 3.1698 | 3.1488 | 3.1278 | 3.0839 | 3.0172 | 2.9505 | 2.8837 | 2.817 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836
Kogan Creek | QLD | Black Coal | SQ | Kogan Creek | 1.566 | 1.5702 | 1.5775 | 1.5863 | 1.5951 | 1.6092 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188
Millmerran | QLD | Black Coal | SQ | Millmerran | 1.4327 | 1.4316 | 1.4408 | 1.4524 | 1.4643 | 1.4801 | 1.4794 | 1.4704 | 1.4717 | 1.4723 | 1.4727 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726
Stanwell | QLD | Black Coal | CQ | Stanwell | 6.4249 | 3.5099 | 3.2942 | 2.9394 | 2.753 | 2.6569 | 2.6093 | 2.5772 | 2.5541 | 2.5387 | 2.527 | 2.5155 | 2.5042 | 2.493 | 2.4819 | 2.471 | 2.4602 | 2.4495 | 2.4393 | 2.4296 | 2.4205 | 2.412 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057
Tarong | QLD | Black Coal | SQ | Tarong | 3.0141 | 3.0269 | 3.0366 | 3.0367 | 3.0367 | 3.0413 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441
Tarong North | QLD | Black Coal | SQ | Tarong North | 3.0141 | 3.0269 | 3.0366 | 3.0367 | 3.0367 | 3.0413 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441
Loy Yang A Power Station | VIC | Brown Coal | VIC | Loy Yang A | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934
Loy Yang B | VIC | Brown Coal | VIC | Loy Yang B | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934
Yallourn W | VIC | Brown Coal | VIC | Yallourn W | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182
Tallawarra | NSW | Gas | SNW | Tallawarra | 14.5406 | 14.2715 | 13.863 | 12.2304 | 12.0551 | 13.3403 | 13.7322 | 14.0761 | 14.7086 | 15.3492 | 15.8834 | 16.0111 | 15.8256 | 15.5747 | 15.7448 | 16.0425 | 16.0461 | 15.8475 | 15.8423 | 15.9331 | 15.9612 | 16.0121 | 16.0044 | 15.9725 | 16.1058 | 16.1932 | 16.7131 | 17.1279 | 17.3101 | 17.6691 | 18.3662 | 18.4295
Condamine A | QLD | Gas | SQ | Condamine A | 12.8717 | 12.6786 | 12.3826 | 11.0883 | 11.0696 | 12.344 | 12.8839 | 13.314 | 14.0701 | 14.9397 | 15.7101 | 15.9027 | 15.6569 | 15.3342 | 15.4787 | 15.8226 | 15.8326 | 15.6121 | 15.6399 | 15.7308 | 15.6989 | 15.7092 | 15.677 | 15.5933 | 15.6583 | 15.6901 | 16.2143 | 16.6527 | 16.8205 | 17.1552 | 17.8605 | 17.8834
Darling Downs | QLD | Gas | SQ | Darling Downs | 12.8717 | 12.6786 | 12.3826 | 11.0883 | 11.0696 | 12.344 | 12.8839 | 13.314 | 14.0701 | 14.9397 | 15.7101 | 15.9027 | 15.6569 | 15.3342 | 15.4787 | 15.8226 | 15.8326 | 15.6121 | 15.6399 | 15.7308 | 15.6989 | 15.7092 | 15.677 | 15.5933 | 15.6583 | 15.6901 | 16.2143 | 16.6527 | 16.8205 | 17.1552 | 17.8605 | 17.8834
Swanbank E GT | QLD | Gas | SQ | Swanbank E GT | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 11.1466 | 12.4383 | 12.8525 | 13.2291 | 13.9874 | 14.8607 | 15.6347 | 15.8293 | 15.5848 | 15.2634 | 15.4101 | 15.7568 | 15.7682 | 15.5483 | 15.577 | 15.6691 | 15.6379 | 15.6491 | 15.6174 | 15.5339 | 15.5994 | 15.6315 | 16.1593 | 16.6004 | 16.7678 | 17.1045 | 17.8144 | 17.8371
Townsville Power Station | QLD | Gas | NQ | Townsville Power Station | 12.8717 | 12.6786 | 12.3826 | 11.0795 | 11.0442 | 12.3185 | 12.8591 | 13.2853 | 14.0379 | 14.8857 | 15.6377 | 15.8298 | 15.5901 | 15.2736 | 15.4381 | 15.7844 | 15.7945 | 15.5939 | 15.6332 | 15.7305 | 15.6986 | 15.7089 | 15.6767 | 15.593 | 15.658 | 15.6898 | 16.2141 | 16.6525 | 16.8203 | 17.155 | 17.8603 | 17.8832
Yarwun Cogen | QLD | Gas | GG | Yarwun Cogen | 12.9828 | 12.7896 | 12.4937 | 11.1994 | 11.1725 | 12.4386 | 12.9756 | 13.4043 | 14.1579 | 15.0236 | 15.7902 | 15.9806 | 15.7335 | 15.4093 | 15.5515 | 15.8925 | 15.9011 | 15.6799 | 15.7066 | 15.7963 | 15.7636 | 15.773 | 15.7402 | 15.6563 | 15.7204 | 15.7511 | 16.2709 | 16.7165 | 16.9055 | 17.2567 | 17.9705 | 18.0114
Osborne | SA | Gas | CSA | Osborne | 14.4364 | 14.0726 | 13.4204 | 11.7995 | 11.8177 | 13.1342 | 13.5366 | 13.8718 | 14.4775 | 15.0772 | 15.5825 | 15.7125 | 15.522 | 15.2657 | 15.4437 | 15.7525 | 15.7678 | 15.5828 | 15.5902 | 15.6937 | 15.7333 | 15.8022 | 15.8121 | 15.788 | 15.9179 | 15.9975 | 16.5355 | 16.9696 | 17.1541 | 17.5215 | 18.2343 | 18.2994
Pelican Point | SA | Gas | CSA | Pelican Point | 14.4364 | 14.0726 | 13.4204 | 11.7995 | 11.8177 | 13.1342 | 13.5366 | 13.8718 | 14.4775 | 15.0772 | 15.5825 | 15.7125 | 15.522 | 15.2657 | 15.4437 | 15.7525 | 15.7678 | 15.5828 | 15.5902 | 15.6937 | 15.7333 | 15.8022 | 15.8121 | 15.788 | 15.9179 | 15.9975 | 16.5355 | 16.9696 | 17.1541 | 17.5215 | 18.2343 | 18.2994
Tamar Valley Combined Cycle | TAS | Gas | TAS | Tamar Valley Combined Cycle | 14.6287 | 14.322 | 13.9092 | 12.2752 | 11.938 | 13.0964 | 13.4943 | 13.8481 | 14.4696 | 15.1092 | 15.6407 | 15.7691 | 15.5777 | 15.3203 | 15.4967 | 15.8032 | 15.8176 | 15.6315 | 15.6375 | 15.7402 | 15.7812 | 15.8778 | 15.9133 | 15.8888 | 15.9909 | 16.0301 | 16.5534 | 16.9791 | 17.1491 | 17.5026 | 18.2043 | 18.2564
Colongra | NSW | Gas | SNW | Colongra | 19.106 | 18.3755 | 17.7374 | 15.4965 | 14.3587 | 15.508 | 15.8313 | 16.1395 | 16.7145 | 17.2646 | 17.7103 | 17.7868 | 17.57 | 17.2844 | 17.4015 | 17.6294 | 17.6003 | 17.366 | 17.3186 | 17.3809 | 17.3899 | 17.4201 | 17.3987 | 17.3611 | 17.4718 | 17.5291 | 17.948 | 18.2779 | 18.4498 | 18.7548 | 19.3427 | 19.3991
Smithfield Energy Facility | NSW | Gas | SNW | Smithfield Energy Facility | 18.674 | 17.9445 | 17.3085 | 15.0697 | 13.9553 | 15.1299 | 15.4667 | 15.7825 | 16.3688 | 16.9358 | 17.398 | 17.4844 | 17.2742 | 16.9957 | 17.1229 | 17.3636 | 17.341 | 17.1137 | 17.0743 | 17.1423 | 17.1555 | 17.19 | 17.1718 | 17.136 | 17.253 | 17.3196 | 17.7584 | 18.1045 | 18.2806 | 18.5963 | 19.2025 | 19.2624
Uranquinty | NSW | Gas | SNSW | Uranquinty | 17.0029 | 16.4536 | 15.9275 | 14.0109 | 13.3088 | 14.4982 | 14.8516 | 15.1831 | 15.7816 | 16.3662 | 16.8407 | 16.9364 | 16.7254 | 16.446 | 16.5884 | 16.8498 | 16.8435 | 16.6346 | 16.6136 | 16.6981 | 16.7273 | 16.7901 | 16.7968 | 16.7695 | 16.8838 | 16.9385 | 17.4035 | 17.779 | 17.9557 | 18.2846 | 18.9201 | 18.9798
Barcaldine Power Station | QLD | Gas | CQ | Barcaldine Power Station | 16.3028 | 15.4529 | 14.1699 | 12.808 | 13.1265 | 14.4432 | 14.9184 | 15.3111 | 16.0087 | 16.768 | 17.4381 | 17.5853 | 17.3164 | 16.9671 | 17.0814 | 17.3637 | 17.3464 | 17.0515 | 16.9931 | 17.0671 | 17.0188 | 17.011 | 16.9671 | 16.8792 | 16.9263 | 16.9349 | 17.3695 | 17.7018 | 17.8328 | 18.1227 | 18.7336 | 18.7534
Braemar | QLD | Gas | SQ | Braemar | 16.1516 | 15.2956 | 14.0161 | 12.7409 | 12.9181 | 14.0462 | 14.5332 | 14.9351 | 15.6473 | 16.447 | 17.1477 | 17.3006 | 17.0323 | 16.6832 | 16.7861 | 17.0748 | 17.0608 | 16.8288 | 16.8377 | 16.9064 | 16.86 | 16.854 | 16.8105 | 16.722 | 16.7709 | 16.782 | 17.2283 | 17.6076 | 17.7767 | 18.0688 | 18.6848 | 18.7045
Braemar 2 Power Station | QLD | Gas | SQ | Braemar 2 Power Station | 16.1516 | 15.2956 | 14.0161 | 12.7409 | 12.9181 | 14.0462 | 14.5332 | 14.9351 | 15.6473 | 16.447 | 17.1477 | 17.3006 | 17.0323 | 16.6832 | 16.7861 | 17.0748 | 17.0608 | 16.8288 | 16.8377 | 16.9064 | 16.86 | 16.854 | 16.8105 | 16.722 | 16.7709 | 16.782 | 17.2283 | 17.6076 | 17.7767 | 18.0688 | 18.6848 | 18.7045
Mt Stuart | QLD | Liquid Fuel | NQ | Liquid Fuel | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Oakey Power Station | QLD | Gas | SQ | Oakey Power Station | 16.3028 | 15.4529 | 14.1699 | 12.8168 | 12.9234 | 14.0483 | 14.5358 | 14.9392 | 15.6513 | 16.4508 | 17.1527 | 17.3059 | 17.0366 | 16.6875 | 16.7911 | 17.0808 | 17.0659 | 16.8326 | 16.8418 | 16.9105 | 16.864 | 16.8583 | 16.8158 | 16.7284 | 16.7776 | 16.7889 | 17.2341 | 17.6126 | 17.7819 | 18.074 | 18.6897 | 18.7096
Roma | QLD | Gas | SQ | Roma | 15.0086 | 14.4088 | 13.4876 | 12.2815 | 12.4599 | 13.6222 | 14.1228 | 14.5329 | 15.256 | 16.073 | 16.792 | 16.9551 | 16.6917 | 16.3491 | 16.463 | 16.7662 | 16.7576 | 16.5275 | 16.5414 | 16.6156 | 16.5727 | 16.571 | 16.5311 | 16.4446 | 16.4978 | 16.5142 | 16.9791 | 17.3726 | 17.5415 | 17.8443 | 18.4824 | 18.5031
Bolivar Power Station | SA | Gas | CSA | Bolivar Power Station | 18.547 | 17.6224 | 16.1073 | 13.9919 | 13.7178 | 14.9237 | 15.2711 | 15.5782 | 16.1377 | 16.6639 | 17.0972 | 17.1859 | 16.9707 | 16.6867 | 16.8217 | 17.0735 | 17.0627 | 16.8491 | 16.8222 | 16.9028 | 16.9276 | 16.9801 | 16.9795 | 16.9515 | 17.0652 | 17.1238 | 17.5807 | 17.9461 | 18.1246 | 18.4486 | 19.0705 | 19.1321
Dry Creek GT | SA | Gas | CSA | Dry Creek GT | 18.547 | 17.6224 | 16.1073 | 13.9919 | 13.7178 | 14.9237 | 15.2711 | 15.5782 | 16.1377 | 16.6639 | 17.0972 | 17.1859 | 16.9707 | 16.6867 | 16.8217 | 17.0735 | 17.0627 | 16.8491 | 16.8222 | 16.9028 | 16.9276 | 16.9801 | 16.9795 | 16.9515 | 17.0652 | 17.1238 | 17.5807 | 17.9461 | 18.1246 | 18.4486 | 19.0705 | 19.1321
Hallett GT | SA | Gas | CSA | Hallett GT | 16.966 | 16.2571 | 15.0739 | 13.2833 | 13.2428 | 14.4763 | 14.8375 | 15.1516 | 15.7227 | 16.2672 | 16.7185 | 16.8175 | 16.6085 | 16.3314 | 16.4772 | 16.7433 | 16.739 | 16.5325 | 16.5142 | 16.6006 | 16.6291 | 16.6856 | 16.6876 | 16.6606 | 16.7784 | 16.8422 | 17.3194 | 17.702 | 17.882 | 18.2168 | 18.8614 | 18.9239
Ladbroke Grove | SA | Gas | SESA | Ladbroke Grove | 17.5682 | 17.0267 | 16.5277 | 14.2686 | 13.2428 | 14.4763 | 14.8375 | 15.1516 | 15.7227 | 16.2672 | 16.7185 | 16.8175 | 16.6085 | 16.3314 | 16.4772 | 16.7433 | 16.739 | 16.5325 | 16.5142 | 16.6006 | 16.6291 | 16.6856 | 16.6876 | 16.6606 | 16.7784 | 16.8422 | 17.3194 | 17.702 | 17.882 | 18.2168 | 18.8614 | 18.9239
Mintaro GT | SA | Gas | CSA | Mintaro GT | 18.547 | 17.6224 | 16.1073 | 13.9919 | 13.7178 | 14.9237 | 15.2711 | 15.5782 | 16.1377 | 16.6639 | 17.0972 | 17.1859 | 16.9707 | 16.6867 | 16.8217 | 17.0735 | 17.0627 | 16.8491 | 16.8222 | 16.9028 | 16.9276 | 16.9801 | 16.9795 | 16.9515 | 17.0652 | 17.1238 | 17.5807 | 17.9461 | 18.1246 | 18.4486 | 19.0705 | 19.1321
Port Lincoln GT | SA | Liquid Fuel | CSA | Liquid Fuel | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Quarantine | SA | Gas | CSA | Quarantine | 16.966 | 16.2571 | 15.0739 | 13.5333 | 13.7178 | 14.9237 | 15.2711 | 15.5782 | 16.1377 | 16.6639 | 17.0972 | 17.1859 | 16.9707 | 16.6867 | 16.8217 | 17.0735 | 17.0627 | 16.8491 | 16.8222 | 16.9028 | 16.9276 | 16.9801 | 16.9795 | 16.9515 | 17.0652 | 17.1238 | 17.5807 | 17.9461 | 18.1246 | 18.4486 | 19.0705 | 19.1321
Snapper Point Power Station | SA | Gas | CSA | SA new OCGT | 18.0576 | 17.3245 | 16.3175 | 14.1302 | 13.4803 | 14.7 | 15.0543 | 15.3649 | 15.9302 | 16.4655 | 16.9079 | 17.0017 | 16.7896 | 16.509 | 16.6495 | 16.9084 | 16.9009 | 16.6908 | 16.6682 | 16.7517 | 16.7784 | 16.8329 | 16.8336 | 16.8061 | 16.9218 | 16.983 | 17.4501 | 17.824 | 18.0033 | 18.3327 | 18.9659 | 19.028
Snuggery | SA | Liquid Fuel | SESA | Liquid Fuel | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Bell Bay Three | TAS | Gas | TAS | Bell Bay Three | 19.1668 | 18.4725 | 17.9049 | 15.3896 | 13.8381 | 14.886 | 15.2288 | 15.5544 | 16.1299 | 16.6958 | 17.1554 | 17.2425 | 17.0264 | 16.7413 | 16.8747 | 17.1243 | 17.1125 | 16.8977 | 16.8696 | 16.9493 | 16.9755 | 17.0556 | 17.0806 | 17.0523 | 17.1382 | 17.1564 | 17.5986 | 17.9557 | 18.1198 | 18.4301 | 19.0411 | 19.09
Tamar Valley Peaking | TAS | Gas | TAS | Tamar Valley Peaking | 14.6287 | 14.322 | 13.9092 | 12.2752 | 11.938 | 13.0964 | 13.4943 | 13.8481 | 14.4696 | 15.1092 | 15.6407 | 15.7691 | 15.5777 | 15.3203 | 15.4967 | 15.8032 | 15.8176 | 15.6315 | 15.6375 | 15.7402 | 15.7812 | 15.8778 | 15.9133 | 15.8888 | 15.9909 | 16.0301 | 16.5534 | 16.9791 | 17.1491 | 17.5026 | 18.2043 | 18.2564
Bairnsdale | VIC | Gas | VIC | Bairnsdale | 18.3191 | 17.6319 | 17.0673 | 14.7717 | 13.5827 | 14.772 | 15.1198 | 15.4412 | 16.0368 | 16.6185 | 17.0667 | 17.1345 | 16.9302 | 16.6316 | 16.7181 | 16.9508 | 16.9364 | 16.718 | 16.62 | 16.5724 | 16.5412 | 16.6161 | 16.6362 | 16.6094 | 16.7124 | 16.7572 | 17.2371 | 17.6228 | 17.7963 | 18.1282 | 18.7753 | 18.8318
Jeeralang A | VIC | Gas | VIC | Jeeralang A | 16.5869 | 16.0416 | 15.5336 | 13.6402 | 12.8522 | 13.9574 | 14.3289 | 14.6691 | 15.2685 | 15.8726 | 16.3695 | 16.478 | 16.2747 | 16.004 | 16.1597 | 16.4389 | 16.4406 | 16.2407 | 16.2303 | 16.3219 | 16.3558 | 16.4445 | 16.4749 | 16.4487 | 16.5495 | 16.5904 | 17.0849 | 17.4851 | 17.6589 | 17.9964 | 18.6559 | 18.7125
Jeeralang B | VIC | Gas | VIC | Jeeralang B | 16.5869 | 16.0416 | 15.5336 | 13.6402 | 12.8522 | 13.9574 | 14.3289 | 14.6691 | 15.2685 | 15.8726 | 16.3695 | 16.478 | 16.2747 | 16.004 | 16.1597 | 16.4389 | 16.4406 | 16.2407 | 16.2303 | 16.3219 | 16.3558 | 16.4445 | 16.4749 | 16.4487 | 16.5495 | 16.5904 | 17.0849 | 17.4851 | 17.6589 | 17.9964 | 18.6559 | 18.7125
Laverton North | VIC | Gas | VIC | Laverton North | 18.6291 | 17.9348 | 17.3672 | 14.8519 | 13.3273 | 14.4048 | 14.7625 | 15.0957 | 15.6835 | 16.2693 | 16.7482 | 16.8464 | 16.6369 | 16.3592 | 16.5042 | 16.7691 | 16.7644 | 16.5573 | 16.5383 | 16.6242 | 16.6544 | 16.739 | 16.7668 | 16.7395 | 16.8363 | 16.872 | 17.3462 | 17.7292 | 17.9016 | 18.2283 | 18.8651 | 18.9208
Mortlake | VIC | Gas | VIC | Mortlake | 18.8944 | 18.1945 | 17.6225 | 15.1632 | 13.693 | 14.9407 | 15.3933 | 15.5383 | 15.9736 | 16.4802 | 16.9073 | 16.9997 | 16.7862 | 16.5043 | 16.6436 | 16.9014 | 16.8927 | 16.6816 | 16.6581 | 16.7406 | 16.7682 | 16.8501 | 16.8758 | 16.8471 | 16.9392 | 16.9678 | 17.4304 | 17.8041 | 17.9728 | 18.2932 | 18.9209 | 18.9735
Somerton | VIC | Gas | VIC | Somerton | 16.5869 | 16.0416 | 15.5336 | 13.6402 | 12.8522 | 13.9574 | 14.3289 | 14.6691 | 15.2685 | 15.8726 | 16.3695 | 16.478 | 16.2747 | 16.004 | 16.1597 | 16.4389 | 16.4406 | 16.2407 | 16.2303 | 16.3219 | 16.3558 | 16.4445 | 16.4749 | 16.4487 | 16.5495 | 16.5904 | 17.0849 | 17.4851 | 17.6589 | 17.9964 | 18.6559 | 18.7125
Valley Power | VIC | Gas | VIC | Valley Power | 18.6291 | 17.9348 | 17.3672 | 14.8519 | 13.3273 | 14.4048 | 14.7625 | 15.0957 | 15.6835 | 16.2693 | 16.7482 | 16.8464 | 16.6369 | 16.3592 | 16.5042 | 16.7691 | 16.7644 | 16.5573 | 16.5383 | 16.6242 | 16.6544 | 16.739 | 16.7668 | 16.7395 | 16.8363 | 16.872 | 17.3462 | 17.7292 | 17.9016 | 18.2283 | 18.8651 | 18.9208
Torrens Island B | SA | Gas | CSA | Torrens Island B | 16.966 | 16.2571 | 15.0739 | 13.5333 | 13.7178 | 14.9237 | 15.2711 | 15.5782 | 16.1377 | 16.6639 | 17.0972 | 17.1859 | 16.9707 | 16.6867 | 16.8217 | 17.0735 | 17.0627 | 16.8491 | 16.8222 | 16.9028 | 16.9276 | 16.9801 | 16.9795 | 16.9515 | 17.0652 | 17.1238 | 17.5807 | 17.9461 | 18.1246 | 18.4486 | 19.0705 | 19.1321
Newport | VIC | Gas | VIC | Newport | 16.5869 | 16.0416 | 15.5336 | 13.6402 | 12.8522 | 13.9574 | 14.3289 | 14.6691 | 15.2685 | 15.8726 | 16.3695 | 16.478 | 16.2747 | 16.004 | 16.1597 | 16.4389 | 16.4406 | 16.2407 | 16.2303 | 16.3219 | 16.3558 | 16.4445 | 16.4749 | 16.4487 | 16.5495 | 16.5904 | 17.0849 | 17.4851 | 17.6589 | 17.9964 | 18.6559 | 18.7125
Angaston | SA | Liquid Fuel | CSA | Liquid Fuel | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Barker Inlet Power Station | SA | Gas | CSA | Barker Inlet Power Station | 16.966 | 16.2571 | 15.0739 | 13.2833 | 13.2428 | 14.4763 | 14.8375 | 15.1516 | 15.7227 | 16.2672 | 16.7185 | 16.8175 | 16.6085 | 16.3314 | 16.4772 | 16.7433 | 16.739 | 16.5325 | 16.5142 | 16.6006 | 16.6291 | 16.6856 | 16.6876 | 16.6606 | 16.7784 | 16.8422 | 17.3194 | 17.702 | 17.882 | 18.2168 | 18.8614 | 18.9239
Lonsdale | SA | Liquid Fuel | CSA | Liquid Fuel | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Port Stanvac 1 | SA | Liquid Fuel | CSA | Liquid Fuel | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Blowering | NSW | Water | SNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Guthega | NSW | Water | SNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hume Dam NSW | NSW | Water | SNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shoalhaven | NSW | Water | CNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tumut 3 | NSW | Water | SNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Upper Tumut | NSW | Water | SNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Barron Gorge | QLD | Water | NQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kareeya | QLD | Water | NQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wivenhoe | QLD | Water | SQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bastyan | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Catagunya / Liapootah / Wayatinah | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cethana | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Devils Gate | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fisher | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gordon | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
John Butters | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lake Echo | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lemonthyme / Wilmot | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mackintosh | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meadowbank | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Poatina | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Reece | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tarraleah | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Trevallyn | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tribute | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tungatinah | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bogong / MacKay | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dartmouth | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Eildon | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hume Dam VIC | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Murray 1 | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Murray 2 | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Kiewa | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avonlie Solar Farm | NSW | Solar | Wagga Wagga | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Beryl Solar Farm | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bomen Solar Farm | NSW | Solar | Wagga Wagga | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Broken Hill Solar Farm | NSW | Solar | Broken Hill | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coleambally Solar Farm | NSW | Solar | SNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Corowa Solar Farm | NSW | Solar | South West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Darlington Point Solar Farm | NSW | Solar | SNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Finley Solar Farm | NSW | Solar | SNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goonumbla Solar Farm | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gullen Range Solar Farm | NSW | Solar | SNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gunnedah Solar Farm | NSW | Solar | North West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hillston Sun Farm | NSW | Solar | SNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Jemalong Solar | NSW | Solar | CNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Junee Solar Farm | NSW | Solar | Wagga Wagga | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Limondale Solar Farm 1 | NSW | Solar | South West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Limondale Solar Farm 2 | NSW | Solar | South West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Manildra Solar Farm | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Molong Solar Farm | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Moree Solar Farm | NSW | Solar | North West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nevertire Solar Farm | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New England Solar Farm | NSW | Solar | New England | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Nyngan Solar Plant | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Parkes Solar Farm | NSW | Solar | CNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sunraysia Solar Farm | NSW | Solar | South West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Suntop Solar Farm | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wagga North Solar Farm | NSW | Solar | Wagga Wagga | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wellington Solar Farm | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Wyalong Solar Farm | NSW | Solar | SNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
White Rock Solar Farm | NSW | Solar | New England | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bluegrass Solar Farm | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Childers Solar Farm | QLD | Solar | Wide Bay | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Clare Solar Farm | QLD | Solar | Northern Qld | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Clermont Solar Farm | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Collinsville Solar Farm | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Columboola Solar Farm | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Darling Downs Solar Farm | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Daydream Solar Farm | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Edenvale Solar Park | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emerald Solar Farm | QLD | Solar | CQ | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gangarri Solar Farm | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hamilton Solar Farm | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Haughton Solar Farm | QLD | Solar | Northern Qld | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hayman Solar Farm | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hughenden Solar Farm | QLD | Solar | North Qld Clean Energy Hub | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kennedy Energy Park Solar Farm | QLD | Solar | North Qld Clean Energy Hub | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kidston Solar Farm | QLD | Solar | North Qld Clean Energy Hub | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lilyvale Solar Farm | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Longreach Solar Farm | QLD | Solar | Barcaldine | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maryrorough Solar Farm | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Middlemount Solar Farm | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Moura Solar Farm | QLD | Solar | Fitzroy | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oakey 1 Solar Farm | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oakey 2 Solar Farm | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ross River Solar Farm | QLD | Solar | Northern Qld | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rugby Run Solar Farm | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sun Metals Corporation Solar Farm | QLD | Solar | Northern Qld | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Susan River Solar Farm | QLD | Solar | Wide Bay | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warwick Solar Farm | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Western Downs Green Power Hub | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Whitsunday Solar Farm | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yarranlea Solar Farm | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Adelaide Desalination Plant Solar Farm | SA | Solar | CSA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bolivar Waste Water Treatment Solar Farm | SA | Solar | CSA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bungala One Solar Farm | SA | Solar | Northern SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bungala Two Solar Farm | SA | Solar | Northern SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Happy Valley Reservoir | SA | Solar | CSA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | SA | Solar | South East SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mannum Adelaide Pumping Station No 3 - MAPL3 (Tungkillo) | SA | Solar | South East SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | SA | Solar | Riverland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Morgan To Whyalla Pipeline No 2 PS | SA | Solar | Riverland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Morgan To Whyalla Pipeline No 3 PS | SA | Solar | Riverland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Morgan To Whyalla Pipeline No 4 PS | SA | Solar | Riverland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Murray Bridge - Onkaparinga Pipeline Pump 2 | SA | Solar | South East SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Augusta Renewable Energy Park - Solar | SA | Solar | Northern SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tailem Bend Solar Farm | SA | Solar | CSA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tailem Bend Solar Farm - stage 2 | SA | Solar | CSA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bannerton Solar Park | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cohuna Solar Farm | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gannawarra Solar Farm | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Glenrowan West Solar Farm | VIC | Solar | Central North Vic | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Karadoc Solar Farm | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kiamal Solar Farm stage 1 | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Numurkah Solar Farm | VIC | Solar | Central North Vic | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wemen Solar Farm | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Winton Solar Farm | VIC | Solar | Central North Vic | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wyalong Solar Farm | NSW | Solar | SNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yatpool Solar Farm | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bango 973 Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bango 999 Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Boco Rock Wind Farm | NSW | Wind | Cooma-Monaro | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bodangora Wind Farm | NSW | Wind | Central-West Orana | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Collector Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crookwell 2 Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crudine Ridge Wind Farm | NSW | Wind | CNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cullerin Range Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gullen Range Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gullen Range Wind Farm 2 | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gunning Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sapphire Wind Farm | NSW | Wind | New England | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Silverton Wind Farm | NSW | Wind | Broken Hill | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Taralga Wind Farm | NSW | Wind | CNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
White Rock Wind Farm - Stage 1 | NSW | Wind | New England | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Woodlawn Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coopers Gap Wind Farm | QLD | Wind | Darling Downs | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kaban Green Power Hub - Wind Farm | QLD | Wind | Far North QLD | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kennedy Energy Park Wind Farm | QLD | Wind | North Qld Clean Energy Hub | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mount Emerald Wind Farm | QLD | Wind | Far North QLD | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Canunda Wind Farm | SA | Wind | South East SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cathedral Rocks Wind Farm | SA | Wind | Eastern Eyre Peninsula | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Clements Gap Wind Farm | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hallett 4 North Brown Hill Wind Farm | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hallett 5 The Bluff Wind Farm | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hallett Stage 1 Brown Hill Wind Farm | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hallett Stage 2 Hallett Hill Wind Farm | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hornsdale Wind Farm Stage 1 | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hornsdale Wind Farm Stage 2 | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hornsdale Wind Farm Stage 3 | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lake Bonney 1 Wind Farm | SA | Wind | South East SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lake Bonney 2 Wind Farm | SA | Wind | South East SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lake Bonney 3 Wind Farm | SA | Wind | South East SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lincoln Gap Wind Farm - stage 1 | SA | Wind | Northern SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lincoln Gap Wind Farm - stage 2 | SA | Wind | Northern SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mount Millar Wind Farm | SA | Wind | Eastern Eyre Peninsula | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Port Augusta Renewable Energy Park - Wind | SA | Wind | Northern SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Snowtown S2 Wind Farm | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Snowtown Wind Farm | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Starfish Hill Wind Farm | SA | Wind | CSA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waterloo Wind Farm | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wattle Point Wind Farm | SA | Wind | Yorke Peninsula | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willogoleche Wind Farm | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cattle Hill Wind Farm | TAS | Wind | Central Highlands | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Granville Harbour Wind Farm | TAS | Wind | North West Tasmania | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Musselroe Wind Farm | TAS | Wind | TAS | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Woolnorth Wind Farm | TAS | Wind | TAS | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ararat Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bald Hills Wind Farm | VIC | Wind | VIC | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Berrybank Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bulgana Green Power Hub - Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Challicum Hills Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cherry Tree Wind Farm | VIC | Wind | VIC | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crowlands Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dulacca Wind Farm | QLD | Wind | Darling Downs | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dundonnell Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Elaine Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kiata Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Macarthur Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Moorabool Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mortlake South Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mortons Lane Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mt Gellibrand Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mt Mercer Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Murra Warra Wind Farm - stage 1 | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Murra Warra Wind Farm - stage 2 | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Oaklands Hill Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Portland Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Salt Creek Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stockyard Hill Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waubra Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yaloak South Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yambuk Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yendon Wind Farm | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Committed generators
Generator | Region | Fuel type | REZ/Sub-region | Fuel cost mapping | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Kurri Kurri OCGT | NSW | Gas | SNW | Kurri Kurri | 19.106 | 18.3755 | 17.7374 | 15.4965 | 14.3587 | 15.508 | 15.8313 | 16.1395 | 16.7145 | 17.2646 | 17.7103 | 17.7868 | 17.57 | 17.2844 | 17.4015 | 17.6294 | 17.6003 | 17.366 | 17.3186 | 17.3809 | 17.3899 | 17.4201 | 17.3987 | 17.3611 | 17.4718 | 17.5291 | 17.948 | 18.2779 | 18.4498 | 18.7548 | 19.3427 | 19.3991
Tallawarra B* | NSW | Gas | SNW | Tallawarra B | 17.0842 | 16.5318 | 15.9833 | 14.1123 | 13.4803 | 14.6825 | 15.0331 | 15.3559 | 15.9538 | 16.5392 | 17.0194 | 17.1161 | 16.9121 | 16.6404 | 16.7784 | 17.0333 | 17.0173 | 16.7972 | 16.7663 | 16.84 | 16.8569 | 16.8955 | 16.8799 | 16.8451 | 16.9662 | 17.038 | 17.4971 | 17.8604 | 18.0383 | 18.3651 | 18.9943 | 19.0554
Kidston | QLD | Water | NQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Snowy 2.0 | NSW | Water | Tumut | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Girgarre Solar Farm | VIC | Solar | Central North Vic | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Glenrowan Solar Farm | VIC | Solar | Central North Vic | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mannum Solar Farm 2* | SA | Solar | Riverland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Metz Solar Farm | NSW | Solar | New England | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Riverina Solar Farm | NSW | Solar | SNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sebastopol Solar Farm | NSW | Solar | Wagga Wagga | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stubbo Solar Farm | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Walla Walla Solar Farm | NSW | Solar | SNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wandoan South Solar Farm - stage 1 | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wellington North Solar Farm (Lightsource) | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wollar Solar Farm | NSW | Solar | CNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Woolooga Solar Farm | QLD | Solar | Wide Bay | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wunghnu Solar Farm | VIC | Solar | VIC | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Clarke Creek Wind Farm | QLD | Wind | Isaac | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Crookwell 3 Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Flyers Creek Wind Farm | NSW | Wind | Central-West Orana | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Golden Plains Wind Farm East | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goyder South Wind Farm 1A | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goyder South Wind Farm 1B | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hawkesdale Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ryan Corner Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rye Park Wind Farm | NSW | Wind | SNSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wambo Wind Farm | QLD | Wind | Darling Downs | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Anticipated projects
Generator | Region | Fuel type | REZ/Sub-region | Fuel cost mapping | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
SA Hydrogen Turbine | SA | Hyblend | CSA | SA new OCGT | see footnote |  |  | 16.8049 | 18.4834 | 24.3537 | 28.8419 | 31.636 | 31.7228 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Borumba | QLD | Water | Banana | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aramara Solar Farm | QLD | Solar | Wide Bay | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Banksia Solar Farm | QLD | Solar | Wide Bay | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Culcairn Solar Farm | NSW | Solar | Wagga Wagga | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cultana Solar Farm | SA | Solar | Northern SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derby Solar Farm | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Frasers Solar Farm | VIC | Solar | Gippsland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Horsham Solar Farm | VIC | Solar | Western Victoria | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lockhart Hybrid Facility - Solar | NSW | Solar | Wagga Wagga | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Quorn Park Solar Farm | NSW | Solar | CNSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tamworth Solar Farm | NSW | Solar | New England | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tilbuster Solar Farm | NSW | Solar | New England | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MacIntyre Wind Farm | QLD | Wind | Darling Downs | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Uungula Wind Farm | NSW | Wind | Central-West Orana | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Woolsthorpe Wind Farm | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SA Hydrogen Turbine is committed 2025-26
Existing, Committed and Anticipated batteries
Generator | Region | Fuel type | REZ/Sub-region | Fuel cost mapping | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Adelaide Desalination Plant BESS | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aldoga BESS Stage 1 | QLD | Battery | GG | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ballarat Energy Storage System | VIC | Battery | Western Victoria | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Blyth BESS | SA | Battery | Mid-North SA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bolivar Waste Water Treatment BESS | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bouldercombe Battery project | QLD | Battery | Fitzroy | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Broken Hill BESS | NSW | Battery | Broken Hill | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bulgana Green Power Hub BESS | VIC | Battery | Western Victoria | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Bungama Solar BESS | SA | Battery | Mid-North SA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital Battery | NSW | Battery | Tumut | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chinchilla BESS | QLD | Battery | Darling Downs | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Christies Beach Wastewater Treatment Plant BESS | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dalrymple BESS | SA | Battery | Yorke Peninsula | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Darlington Point Energy Storage System | NSW | Battery | SNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Eraring Big Battery | NSW | Battery | Hunter Central Coast | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gannawarra Energy Storage System | VIC | Battery | Murray River | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gnarwarre BESS | VIC | Battery | South West Victoria | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Happy Valley Reservoir BESS | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hazelwood BESS | VIC | Battery | Gippsland | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hornsdale Power Reserve Unit 1 | SA | Battery | Mid-North SA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Koorangie Energy Storage System | VIC | Battery | Murray River | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lake Bonney BESS | SA | Battery | South East SA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Liddell BESS | NSW | Battery | Hunter-Central Coast | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lincoln Gap Wind Farm BESS | SA | Battery | Northern SA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Lockhart Hybrid Facility - Battery | NSW | Battery | Wagga Wagga | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Melbourne Renewable Energy Hub - Side A | VIC | Battery | VIC | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mornington BESS | VIC | Battery | VIC | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mortlake Battery | VIC | Battery | South West Victoria | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mt Fox BESS | QLD | Battery | Northern Qld | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New England Solar Farm BESS | NSW | Battery | New England | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Orana BESS | NSW | Battery | Central-West Orana | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Philip Island BESS | VIC | Battery | VIC | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Queanbeyan BESS | NSW | Battery | Tumut | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Quorn Park BESS | NSW | Battery | CNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Rangebank BESS | VIC | Battery | VIC | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Richmond Valley BESS | NSW | Battery | NNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Riverina Energy Storage System 1 | NSW | Battery | SNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Riverina Energy Storage System 2 | NSW | Battery | SNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Sapphire Wind Farm BESS | NSW | Battery | New England | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stanwell BESS | QLD | Battery | Fitzroy | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swanbank BESS | QLD | Battery | SQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tailem Bend Battery Project | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tamworth BESS | NSW | Battery | NNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tarong BESS | QLD | Battery | Darling Downs | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Templers BESS | SA | Battery | Mid-North SA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Terang BESS | VIC | Battery | South West Victoria | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Torrens Island BESS | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Ulinda Park BESS | QLD | Battery | Darling Downs | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Victorian Big Battery | VIC | Battery | VIC | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wallgrove Grid Battery project | NSW | Battery | SNW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wandoan South BESS | QLD | Battery | Darling Downs | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Waratah Super Battery | NSW | Battery | SNW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Western Downs Battery | QLD | Battery | Darling Downs | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wooreen Energy Storage System | VIC | Battery | Gippsland | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Additional projects
Generator | Region | Fuel type | REZ/Sub-region | Fuel cost mapping | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Coppabella Wind Farm | NSW | Wind | Tumut | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Derby Solar Project BESS | VIC | Battery | Murray River | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fulham Solar Farm | VIC | Solar | Gippsland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fulham Solar Farm BESS | VIC | Battery | Gippsland | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Goulburn River BESS | NSW | Battery | CNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Horsham Solar Farm BESS | VIC | Battery | Western Victoria | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kiamal Solar Farm – Stage 2 | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kiamal Solar Farm – Stage 2 BESS | VIC | Battery | Murray River | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kogan Gas | QLD | Hyblend | SQ | QLD new OCGT | see footnote |  |  |  | 11.1309 | 10.3794 | 13.0103 | 17.877 | 22.2413 | 26.1242 | 29.5697 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Limondale BESS | NSW | Battery | South West NSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
New England Solar Farm - stage 2 | NSW | Solar | New England | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Silver City Energy Storage | NSW | Battery | Broken Hill | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Smithfield BESS | NSW | Battery | SNW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kogan Gas is committed in 2026-27
New Entrant
Generator | Region | Fuel type | REZ/Sub-region | Fuel cost mapping | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
OCGT (small GT) | QLD | Gas | NQ | QLD new OCGT | 16.202 | 15.348 | 14.0674 | 12.7633 | 13.1404 | 14.4596 | 14.934 | 15.3283 | 16.0285 | 16.8031 | 17.4853 | 17.6327 | 17.3602 | 17.0066 | 17.1063 | 17.3863 | 17.3695 | 17.0615 | 16.9948 | 17.0646 | 17.0163 | 17.0082 | 16.9636 | 16.875 | 16.9219 | 16.9304 | 17.3657 | 17.6986 | 17.8295 | 18.1194 | 18.7305 | 18.7501
OCGT (small GT) | QLD | Gas | CQ | QLD new OCGT | 16.202 | 15.348 | 14.0674 | 12.7633 | 13.1404 | 14.4596 | 14.934 | 15.3283 | 16.0285 | 16.8031 | 17.4853 | 17.6327 | 17.3602 | 17.0066 | 17.1063 | 17.3863 | 17.3695 | 17.0615 | 16.9948 | 17.0646 | 17.0163 | 17.0082 | 16.9636 | 16.875 | 16.9219 | 16.9304 | 17.3657 | 17.6986 | 17.8295 | 18.1194 | 18.7305 | 18.7501
OCGT (small GT) | QLD | Gas | GG | QLD new OCGT | 16.202 | 15.348 | 14.0674 | 12.7633 | 13.1404 | 14.4596 | 14.934 | 15.3283 | 16.0285 | 16.8031 | 17.4853 | 17.6327 | 17.3602 | 17.0066 | 17.1063 | 17.3863 | 17.3695 | 17.0615 | 16.9948 | 17.0646 | 17.0163 | 17.0082 | 16.9636 | 16.875 | 16.9219 | 16.9304 | 17.3657 | 17.6986 | 17.8295 | 18.1194 | 18.7305 | 18.7501
OCGT (small GT) | QLD | Gas | SQ | QLD new OCGT | 16.202 | 15.348 | 14.0674 | 12.7633 | 13.1404 | 14.4596 | 14.934 | 15.3283 | 16.0285 | 16.8031 | 17.4853 | 17.6327 | 17.3602 | 17.0066 | 17.1063 | 17.3863 | 17.3695 | 17.0615 | 16.9948 | 17.0646 | 17.0163 | 17.0082 | 16.9636 | 16.875 | 16.9219 | 16.9304 | 17.3657 | 17.6986 | 17.8295 | 18.1194 | 18.7305 | 18.7501
OCGT (small GT) | NSW | Gas | NNSW | NSW new OCGT | 18.962 | 18.2318 | 17.5944 | 15.3542 | 14.2242 | 15.3819 | 15.7098 | 16.0205 | 16.5993 | 17.155 | 17.6062 | 17.686 | 17.4714 | 17.1882 | 17.3086 | 17.5408 | 17.5139 | 17.2819 | 17.2372 | 17.3013 | 17.3118 | 17.3434 | 17.3231 | 17.286 | 17.3989 | 17.4592 | 17.8848 | 18.2201 | 18.3934 | 18.702 | 19.2959 | 19.3535
OCGT (small GT) | NSW | Gas | CNSW | NSW new OCGT | 18.962 | 18.2318 | 17.5944 | 15.3542 | 14.2242 | 15.3819 | 15.7098 | 16.0205 | 16.5993 | 17.155 | 17.6062 | 17.686 | 17.4714 | 17.1882 | 17.3086 | 17.5408 | 17.5139 | 17.2819 | 17.2372 | 17.3013 | 17.3118 | 17.3434 | 17.3231 | 17.286 | 17.3989 | 17.4592 | 17.8848 | 18.2201 | 18.3934 | 18.702 | 19.2959 | 19.3535
OCGT (small GT) | NSW | Gas | SNW | NSW new OCGT | 18.962 | 18.2318 | 17.5944 | 15.3542 | 14.2242 | 15.3819 | 15.7098 | 16.0205 | 16.5993 | 17.155 | 17.6062 | 17.686 | 17.4714 | 17.1882 | 17.3086 | 17.5408 | 17.5139 | 17.2819 | 17.2372 | 17.3013 | 17.3118 | 17.3434 | 17.3231 | 17.286 | 17.3989 | 17.4592 | 17.8848 | 18.2201 | 18.3934 | 18.702 | 19.2959 | 19.3535
OCGT (small GT) | NSW | Gas | SNSW | NSW new OCGT | 18.962 | 18.2318 | 17.5944 | 15.3542 | 14.2242 | 15.3819 | 15.7098 | 16.0205 | 16.5993 | 17.155 | 17.6062 | 17.686 | 17.4714 | 17.1882 | 17.3086 | 17.5408 | 17.5139 | 17.2819 | 17.2372 | 17.3013 | 17.3118 | 17.3434 | 17.3231 | 17.286 | 17.3989 | 17.4592 | 17.8848 | 18.2201 | 18.3934 | 18.702 | 19.2959 | 19.3535
OCGT (small GT) | VIC | Gas | VIC | VIC new OCGT | 17.608 | 16.9882 | 16.4504 | 14.246 | 13.0897 | 14.1811 | 14.5457 | 14.8824 | 15.476 | 16.0709 | 16.5588 | 16.6622 | 16.4558 | 16.1816 | 16.332 | 16.604 | 16.6025 | 16.399 | 16.3843 | 16.4731 | 16.5051 | 16.5917 | 16.6209 | 16.5941 | 16.6929 | 16.7312 | 17.2155 | 17.6071 | 17.7802 | 18.1123 | 18.7605 | 18.8166
OCGT (small GT) | SA | Gas | CSA | SA new OCGT | 18.0576 | 17.3245 | 16.3175 | 14.1302 | 13.4803 | 14.7 | 15.0543 | 15.3649 | 15.9302 | 16.4655 | 16.9079 | 17.0017 | 16.7896 | 16.509 | 16.6495 | 16.9084 | 16.9009 | 16.6908 | 16.6682 | 16.7517 | 16.7784 | 16.8329 | 16.8336 | 16.8061 | 16.9218 | 16.983 | 17.4501 | 17.824 | 18.0033 | 18.3327 | 18.9659 | 19.028
OCGT (small GT) | SA | Gas | SESA | SA new OCGT | 18.0576 | 17.3245 | 16.3175 | 14.1302 | 13.4803 | 14.7 | 15.0543 | 15.3649 | 15.9302 | 16.4655 | 16.9079 | 17.0017 | 16.7896 | 16.509 | 16.6495 | 16.9084 | 16.9009 | 16.6908 | 16.6682 | 16.7517 | 16.7784 | 16.8329 | 16.8336 | 16.8061 | 16.9218 | 16.983 | 17.4501 | 17.824 | 18.0033 | 18.3327 | 18.9659 | 19.028
OCGT (small GT) | TAS | Gas | TAS | TAS new OCGT | 19.1668 | 18.4725 | 17.9049 | 15.3896 | 13.8381 | 14.886 | 15.2288 | 15.5544 | 16.1299 | 16.6958 | 17.1554 | 17.2425 | 17.0264 | 16.7413 | 16.8747 | 17.1243 | 17.1125 | 16.8977 | 16.8696 | 16.9493 | 16.9755 | 17.0556 | 17.0806 | 17.0523 | 17.1382 | 17.1564 | 17.5986 | 17.9557 | 18.1198 | 18.4301 | 19.0411 | 19.09
OCGT (large GT) | QLD | Gas | NQ | QLD new OCGT | 16.202 | 15.348 | 14.0674 | 12.7633 | 13.1404 | 14.4596 | 14.934 | 15.3283 | 16.0285 | 16.8031 | 17.4853 | 17.6327 | 17.3602 | 17.0066 | 17.1063 | 17.3863 | 17.3695 | 17.0615 | 16.9948 | 17.0646 | 17.0163 | 17.0082 | 16.9636 | 16.875 | 16.9219 | 16.9304 | 17.3657 | 17.6986 | 17.8295 | 18.1194 | 18.7305 | 18.7501
OCGT (large GT) | QLD | Gas | CQ | QLD new OCGT | 16.202 | 15.348 | 14.0674 | 12.7633 | 13.1404 | 14.4596 | 14.934 | 15.3283 | 16.0285 | 16.8031 | 17.4853 | 17.6327 | 17.3602 | 17.0066 | 17.1063 | 17.3863 | 17.3695 | 17.0615 | 16.9948 | 17.0646 | 17.0163 | 17.0082 | 16.9636 | 16.875 | 16.9219 | 16.9304 | 17.3657 | 17.6986 | 17.8295 | 18.1194 | 18.7305 | 18.7501
OCGT (large GT) | QLD | Gas | GG | QLD new OCGT | 16.202 | 15.348 | 14.0674 | 12.7633 | 13.1404 | 14.4596 | 14.934 | 15.3283 | 16.0285 | 16.8031 | 17.4853 | 17.6327 | 17.3602 | 17.0066 | 17.1063 | 17.3863 | 17.3695 | 17.0615 | 16.9948 | 17.0646 | 17.0163 | 17.0082 | 16.9636 | 16.875 | 16.9219 | 16.9304 | 17.3657 | 17.6986 | 17.8295 | 18.1194 | 18.7305 | 18.7501
OCGT (large GT) | QLD | Gas | SQ | QLD new OCGT | 16.202 | 15.348 | 14.0674 | 12.7633 | 13.1404 | 14.4596 | 14.934 | 15.3283 | 16.0285 | 16.8031 | 17.4853 | 17.6327 | 17.3602 | 17.0066 | 17.1063 | 17.3863 | 17.3695 | 17.0615 | 16.9948 | 17.0646 | 17.0163 | 17.0082 | 16.9636 | 16.875 | 16.9219 | 16.9304 | 17.3657 | 17.6986 | 17.8295 | 18.1194 | 18.7305 | 18.7501
OCGT (large GT) | NSW | Gas | NNSW | NSW new OCGT | 18.962 | 18.2318 | 17.5944 | 15.3542 | 14.2242 | 15.3819 | 15.7098 | 16.0205 | 16.5993 | 17.155 | 17.6062 | 17.686 | 17.4714 | 17.1882 | 17.3086 | 17.5408 | 17.5139 | 17.2819 | 17.2372 | 17.3013 | 17.3118 | 17.3434 | 17.3231 | 17.286 | 17.3989 | 17.4592 | 17.8848 | 18.2201 | 18.3934 | 18.702 | 19.2959 | 19.3535
OCGT (large GT) | NSW | Gas | CNSW | NSW new OCGT | 18.962 | 18.2318 | 17.5944 | 15.3542 | 14.2242 | 15.3819 | 15.7098 | 16.0205 | 16.5993 | 17.155 | 17.6062 | 17.686 | 17.4714 | 17.1882 | 17.3086 | 17.5408 | 17.5139 | 17.2819 | 17.2372 | 17.3013 | 17.3118 | 17.3434 | 17.3231 | 17.286 | 17.3989 | 17.4592 | 17.8848 | 18.2201 | 18.3934 | 18.702 | 19.2959 | 19.3535
OCGT (large GT) | NSW | Gas | SNW | NSW new OCGT | 18.962 | 18.2318 | 17.5944 | 15.3542 | 14.2242 | 15.3819 | 15.7098 | 16.0205 | 16.5993 | 17.155 | 17.6062 | 17.686 | 17.4714 | 17.1882 | 17.3086 | 17.5408 | 17.5139 | 17.2819 | 17.2372 | 17.3013 | 17.3118 | 17.3434 | 17.3231 | 17.286 | 17.3989 | 17.4592 | 17.8848 | 18.2201 | 18.3934 | 18.702 | 19.2959 | 19.3535
OCGT (large GT) | NSW | Gas | SNSW | NSW new OCGT | 18.962 | 18.2318 | 17.5944 | 15.3542 | 14.2242 | 15.3819 | 15.7098 | 16.0205 | 16.5993 | 17.155 | 17.6062 | 17.686 | 17.4714 | 17.1882 | 17.3086 | 17.5408 | 17.5139 | 17.2819 | 17.2372 | 17.3013 | 17.3118 | 17.3434 | 17.3231 | 17.286 | 17.3989 | 17.4592 | 17.8848 | 18.2201 | 18.3934 | 18.702 | 19.2959 | 19.3535
OCGT (large GT) | VIC | Gas | VIC | VIC new OCGT | 17.608 | 16.9882 | 16.4504 | 14.246 | 13.0897 | 14.1811 | 14.5457 | 14.8824 | 15.476 | 16.0709 | 16.5588 | 16.6622 | 16.4558 | 16.1816 | 16.332 | 16.604 | 16.6025 | 16.399 | 16.3843 | 16.4731 | 16.5051 | 16.5917 | 16.6209 | 16.5941 | 16.6929 | 16.7312 | 17.2155 | 17.6071 | 17.7802 | 18.1123 | 18.7605 | 18.8166
OCGT (large GT) | SA | Gas | CSA | SA new OCGT | 18.0576 | 17.3245 | 16.3175 | 14.1302 | 13.4803 | 14.7 | 15.0543 | 15.3649 | 15.9302 | 16.4655 | 16.9079 | 17.0017 | 16.7896 | 16.509 | 16.6495 | 16.9084 | 16.9009 | 16.6908 | 16.6682 | 16.7517 | 16.7784 | 16.8329 | 16.8336 | 16.8061 | 16.9218 | 16.983 | 17.4501 | 17.824 | 18.0033 | 18.3327 | 18.9659 | 19.028
OCGT (large GT) | SA | Gas | SESA | SA new OCGT | 18.0576 | 17.3245 | 16.3175 | 14.1302 | 13.4803 | 14.7 | 15.0543 | 15.3649 | 15.9302 | 16.4655 | 16.9079 | 17.0017 | 16.7896 | 16.509 | 16.6495 | 16.9084 | 16.9009 | 16.6908 | 16.6682 | 16.7517 | 16.7784 | 16.8329 | 16.8336 | 16.8061 | 16.9218 | 16.983 | 17.4501 | 17.824 | 18.0033 | 18.3327 | 18.9659 | 19.028
OCGT (large GT) | TAS | Gas | TAS | TAS new OCGT | 19.1668 | 18.4725 | 17.9049 | 15.3896 | 13.8381 | 14.886 | 15.2288 | 15.5544 | 16.1299 | 16.6958 | 17.1554 | 17.2425 | 17.0264 | 16.7413 | 16.8747 | 17.1243 | 17.1125 | 16.8977 | 16.8696 | 16.9493 | 16.9755 | 17.0556 | 17.0806 | 17.0523 | 17.1382 | 17.1564 | 17.5986 | 17.9557 | 18.1198 | 18.4301 | 19.0411 | 19.09
CCGT | QLD | Gas | NQ | QLD new CCGT | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 11.334 | 12.7795 | 13.177 | 13.5456 | 14.2955 | 15.1551 | 15.9202 | 16.1114 | 15.8622 | 15.5355 | 15.6739 | 16.0137 | 16.0238 | 15.7381 | 15.7035 | 15.7951 | 15.7624 | 15.7718 | 15.739 | 15.6551 | 15.7189 | 15.7488 | 16.2682 | 16.6721 | 16.8089 | 17.1437 | 17.8498 | 17.8723
CCGT | QLD | Gas | CQ | QLD new CCGT | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 11.334 | 12.7795 | 13.177 | 13.5456 | 14.2955 | 15.1551 | 15.9202 | 16.1114 | 15.8622 | 15.5355 | 15.6739 | 16.0137 | 16.0238 | 15.7381 | 15.7035 | 15.7951 | 15.7624 | 15.7718 | 15.739 | 15.6551 | 15.7189 | 15.7488 | 16.2682 | 16.6721 | 16.8089 | 17.1437 | 17.8498 | 17.8723
CCGT | QLD | Gas | GG | QLD new CCGT | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 11.334 | 12.7795 | 13.177 | 13.5456 | 14.2955 | 15.1551 | 15.9202 | 16.1114 | 15.8622 | 15.5355 | 15.6739 | 16.0137 | 16.0238 | 15.7381 | 15.7035 | 15.7951 | 15.7624 | 15.7718 | 15.739 | 15.6551 | 15.7189 | 15.7488 | 16.2682 | 16.6721 | 16.8089 | 17.1437 | 17.8498 | 17.8723
CCGT | QLD | Gas | SQ | QLD new CCGT | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 11.334 | 12.7795 | 13.177 | 13.5456 | 14.2955 | 15.1551 | 15.9202 | 16.1114 | 15.8622 | 15.5355 | 15.6739 | 16.0137 | 16.0238 | 15.7381 | 15.7035 | 15.7951 | 15.7624 | 15.7718 | 15.739 | 15.6551 | 15.7189 | 15.7488 | 16.2682 | 16.6721 | 16.8089 | 17.1437 | 17.8498 | 17.8723
CCGT | NSW | Gas | NNSW | NSW new CCGT | 14.5406 | 14.2715 | 13.863 | 12.2304 | 12.0551 | 13.3403 | 13.7322 | 14.0761 | 14.7086 | 15.3492 | 15.8834 | 16.0111 | 15.8256 | 15.5747 | 15.7448 | 16.0425 | 16.0461 | 15.8475 | 15.8423 | 15.9331 | 15.9612 | 16.0121 | 16.0044 | 15.9725 | 16.1058 | 16.1932 | 16.7131 | 17.1279 | 17.3101 | 17.6691 | 18.3662 | 18.4295
CCGT | NSW | Gas | CNSW | NSW new CCGT | 14.5406 | 14.2715 | 13.863 | 12.2304 | 12.0551 | 13.3403 | 13.7322 | 14.0761 | 14.7086 | 15.3492 | 15.8834 | 16.0111 | 15.8256 | 15.5747 | 15.7448 | 16.0425 | 16.0461 | 15.8475 | 15.8423 | 15.9331 | 15.9612 | 16.0121 | 16.0044 | 15.9725 | 16.1058 | 16.1932 | 16.7131 | 17.1279 | 17.3101 | 17.6691 | 18.3662 | 18.4295
CCGT | NSW | Gas | SNW | NSW new CCGT | 14.5406 | 14.2715 | 13.863 | 12.2304 | 12.0551 | 13.3403 | 13.7322 | 14.0761 | 14.7086 | 15.3492 | 15.8834 | 16.0111 | 15.8256 | 15.5747 | 15.7448 | 16.0425 | 16.0461 | 15.8475 | 15.8423 | 15.9331 | 15.9612 | 16.0121 | 16.0044 | 15.9725 | 16.1058 | 16.1932 | 16.7131 | 17.1279 | 17.3101 | 17.6691 | 18.3662 | 18.4295
CCGT | NSW | Gas | SNSW | NSW new CCGT | 14.5406 | 14.2715 | 13.863 | 12.2304 | 12.0551 | 13.3403 | 13.7322 | 14.0761 | 14.7086 | 15.3492 | 15.8834 | 16.0111 | 15.8256 | 15.5747 | 15.7448 | 16.0425 | 16.0461 | 15.8475 | 15.8423 | 15.9331 | 15.9612 | 16.0121 | 16.0044 | 15.9725 | 16.1058 | 16.1932 | 16.7131 | 17.1279 | 17.3101 | 17.6691 | 18.3662 | 18.4295
CCGT | VIC | Gas | VIC | VIC new CCGT | 15.608 | 14.9882 | 14.4504 | 12.246 | 11.1896 | 12.3916 | 12.8112 | 13.176 | 13.8158 | 14.4843 | 15.0442 | 15.1888 | 15.0072 | 14.7607 | 14.9539 | 15.2829 | 15.3076 | 15.1328 | 15.1523 | 15.2639 | 15.3108 | 15.4139 | 15.4535 | 15.4306 | 15.5456 | 15.6048 | 16.1703 | 16.6306 | 16.8097 | 17.1851 | 17.9241 | 17.9836
CCGT | SA | Gas | CSA | SA new CCGT | 14.4364 | 14.0726 | 13.4204 | 11.7995 | 11.8177 | 13.1342 | 13.5366 | 13.8718 | 14.4775 | 15.0772 | 15.5825 | 15.7125 | 15.522 | 15.2657 | 15.4437 | 15.7525 | 15.7678 | 15.5828 | 15.5902 | 15.6937 | 15.7333 | 15.8022 | 15.8121 | 15.788 | 15.9179 | 15.9975 | 16.5355 | 16.9696 | 17.1541 | 17.5215 | 18.2343 | 18.2994
CCGT | SA | Gas | SESA | SA new CCGT | 14.4364 | 14.0726 | 13.4204 | 11.7995 | 11.8177 | 13.1342 | 13.5366 | 13.8718 | 14.4775 | 15.0772 | 15.5825 | 15.7125 | 15.522 | 15.2657 | 15.4437 | 15.7525 | 15.7678 | 15.5828 | 15.5902 | 15.6937 | 15.7333 | 15.8022 | 15.8121 | 15.788 | 15.9179 | 15.9975 | 16.5355 | 16.9696 | 17.1541 | 17.5215 | 18.2343 | 18.2994
CCGT | TAS | Gas | TAS | TAS new CCGT | 14.6287 | 14.322 | 13.9092 | 12.2752 | 11.938 | 13.0964 | 13.4943 | 13.8481 | 14.4696 | 15.1092 | 15.6407 | 15.7691 | 15.5777 | 15.3203 | 15.4967 | 15.8032 | 15.8176 | 15.6315 | 15.6375 | 15.7402 | 15.7812 | 15.8778 | 15.9133 | 15.8888 | 15.9909 | 16.0301 | 16.5534 | 16.9791 | 17.1491 | 17.5026 | 18.2043 | 18.2564
CCGT with CCS | QLD | Gas | NQ | QLD new CCGT | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 11.334 | 12.7795 | 13.177 | 13.5456 | 14.2955 | 15.1551 | 15.9202 | 16.1114 | 15.8622 | 15.5355 | 15.6739 | 16.0137 | 16.0238 | 15.7381 | 15.7035 | 15.7951 | 15.7624 | 15.7718 | 15.739 | 15.6551 | 15.7189 | 15.7488 | 16.2682 | 16.6721 | 16.8089 | 17.1437 | 17.8498 | 17.8723
CCGT with CCS | QLD | Gas | CQ | QLD new CCGT | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 11.334 | 12.7795 | 13.177 | 13.5456 | 14.2955 | 15.1551 | 15.9202 | 16.1114 | 15.8622 | 15.5355 | 15.6739 | 16.0137 | 16.0238 | 15.7381 | 15.7035 | 15.7951 | 15.7624 | 15.7718 | 15.739 | 15.6551 | 15.7189 | 15.7488 | 16.2682 | 16.6721 | 16.8089 | 17.1437 | 17.8498 | 17.8723
CCGT with CCS | QLD | Gas | GG | QLD new CCGT | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 11.334 | 12.7795 | 13.177 | 13.5456 | 14.2955 | 15.1551 | 15.9202 | 16.1114 | 15.8622 | 15.5355 | 15.6739 | 16.0137 | 16.0238 | 15.7381 | 15.7035 | 15.7951 | 15.7624 | 15.7718 | 15.739 | 15.6551 | 15.7189 | 15.7488 | 16.2682 | 16.6721 | 16.8089 | 17.1437 | 17.8498 | 17.8723
CCGT with CCS | QLD | Gas | SQ | QLD new CCGT | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 11.334 | 12.7795 | 13.177 | 13.5456 | 14.2955 | 15.1551 | 15.9202 | 16.1114 | 15.8622 | 15.5355 | 15.6739 | 16.0137 | 16.0238 | 15.7381 | 15.7035 | 15.7951 | 15.7624 | 15.7718 | 15.739 | 15.6551 | 15.7189 | 15.7488 | 16.2682 | 16.6721 | 16.8089 | 17.1437 | 17.8498 | 17.8723
CCGT with CCS | NSW | Gas | NNSW | NSW new CCGT | 14.5406 | 14.2715 | 13.863 | 12.2304 | 12.0551 | 13.3403 | 13.7322 | 14.0761 | 14.7086 | 15.3492 | 15.8834 | 16.0111 | 15.8256 | 15.5747 | 15.7448 | 16.0425 | 16.0461 | 15.8475 | 15.8423 | 15.9331 | 15.9612 | 16.0121 | 16.0044 | 15.9725 | 16.1058 | 16.1932 | 16.7131 | 17.1279 | 17.3101 | 17.6691 | 18.3662 | 18.4295
CCGT with CCS | NSW | Gas | CNSW | NSW new CCGT | 14.5406 | 14.2715 | 13.863 | 12.2304 | 12.0551 | 13.3403 | 13.7322 | 14.0761 | 14.7086 | 15.3492 | 15.8834 | 16.0111 | 15.8256 | 15.5747 | 15.7448 | 16.0425 | 16.0461 | 15.8475 | 15.8423 | 15.9331 | 15.9612 | 16.0121 | 16.0044 | 15.9725 | 16.1058 | 16.1932 | 16.7131 | 17.1279 | 17.3101 | 17.6691 | 18.3662 | 18.4295
CCGT with CCS | NSW | Gas | SNW | NSW new CCGT | 14.5406 | 14.2715 | 13.863 | 12.2304 | 12.0551 | 13.3403 | 13.7322 | 14.0761 | 14.7086 | 15.3492 | 15.8834 | 16.0111 | 15.8256 | 15.5747 | 15.7448 | 16.0425 | 16.0461 | 15.8475 | 15.8423 | 15.9331 | 15.9612 | 16.0121 | 16.0044 | 15.9725 | 16.1058 | 16.1932 | 16.7131 | 17.1279 | 17.3101 | 17.6691 | 18.3662 | 18.4295
CCGT with CCS | NSW | Gas | SNSW | NSW new CCGT | 14.5406 | 14.2715 | 13.863 | 12.2304 | 12.0551 | 13.3403 | 13.7322 | 14.0761 | 14.7086 | 15.3492 | 15.8834 | 16.0111 | 15.8256 | 15.5747 | 15.7448 | 16.0425 | 16.0461 | 15.8475 | 15.8423 | 15.9331 | 15.9612 | 16.0121 | 16.0044 | 15.9725 | 16.1058 | 16.1932 | 16.7131 | 17.1279 | 17.3101 | 17.6691 | 18.3662 | 18.4295
CCGT with CCS | VIC | Gas | VIC | VIC new CCGT | 15.608 | 14.9882 | 14.4504 | 12.246 | 11.1896 | 12.3916 | 12.8112 | 13.176 | 13.8158 | 14.4843 | 15.0442 | 15.1888 | 15.0072 | 14.7607 | 14.9539 | 15.2829 | 15.3076 | 15.1328 | 15.1523 | 15.2639 | 15.3108 | 15.4139 | 15.4535 | 15.4306 | 15.5456 | 15.6048 | 16.1703 | 16.6306 | 16.8097 | 17.1851 | 17.9241 | 17.9836
CCGT with CCS | SA | Gas | CSA | SA new CCGT | 14.4364 | 14.0726 | 13.4204 | 11.7995 | 11.8177 | 13.1342 | 13.5366 | 13.8718 | 14.4775 | 15.0772 | 15.5825 | 15.7125 | 15.522 | 15.2657 | 15.4437 | 15.7525 | 15.7678 | 15.5828 | 15.5902 | 15.6937 | 15.7333 | 15.8022 | 15.8121 | 15.788 | 15.9179 | 15.9975 | 16.5355 | 16.9696 | 17.1541 | 17.5215 | 18.2343 | 18.2994
CCGT with CCS | SA | Gas | SESA | SA new CCGT | 14.4364 | 14.0726 | 13.4204 | 11.7995 | 11.8177 | 13.1342 | 13.5366 | 13.8718 | 14.4775 | 15.0772 | 15.5825 | 15.7125 | 15.522 | 15.2657 | 15.4437 | 15.7525 | 15.7678 | 15.5828 | 15.5902 | 15.6937 | 15.7333 | 15.8022 | 15.8121 | 15.788 | 15.9179 | 15.9975 | 16.5355 | 16.9696 | 17.1541 | 17.5215 | 18.2343 | 18.2994
CCGT with CCS | TAS | Gas | TAS | TAS new CCGT | 14.6287 | 14.322 | 13.9092 | 12.2752 | 11.938 | 13.0964 | 13.4943 | 13.8481 | 14.4696 | 15.1092 | 15.6407 | 15.7691 | 15.5777 | 15.3203 | 15.4967 | 15.8032 | 15.8176 | 15.6315 | 15.6375 | 15.7402 | 15.7812 | 15.8778 | 15.9133 | 15.8888 | 15.9909 | 16.0301 | 16.5534 | 16.9791 | 17.1491 | 17.5026 | 18.2043 | 18.2564
Biomass | QLD | Biomass | NQ | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | QLD | Biomass | CQ | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | QLD | Biomass | GG | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | QLD | Biomass | SQ | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | NSW | Biomass | NNSW | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | NSW | Biomass | CNSW | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | NSW | Biomass | SNW | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | NSW | Biomass | SNSW | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | VIC | Biomass | VIC | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | SA | Biomass | CSA | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | SA | Biomass | SESA | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Biomass | TAS | Biomass | TAS | Biomass | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
Large scale Solar PV | QLD | Solar | Far North QLD | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | QLD | Solar | North Qld Clean Energy Hub | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | QLD | Solar | Northern Qld | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | QLD | Solar | Barcaldine | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | QLD | Solar | Fitzroy | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | QLD | Solar | Wide Bay | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | QLD | Solar | Banana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | North West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | New England | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | Broken Hill | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | South West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | Wagga Wagga | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | Tumut | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | Cooma-Monaro | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | Hunter-Central Coast | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | Illawarra | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | VIC | Solar | Ovens Murray | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | VIC | Solar | Western Victoria | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | VIC | Solar | South West Victoria | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | VIC | Solar | Gippsland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | VIC | Solar | Central North Vic | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | SA | Solar | South East SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | SA | Solar | Riverland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | SA | Solar | Mid-North SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | SA | Solar | Yorke Peninsula | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | SA | Solar | Northern SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | SA | Solar | Leigh Creek | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | SA | Solar | Roxby Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | SA | Solar | Eastern Eyre Peninsula | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | SA | Solar | Western Eyre Peninsula | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | TAS | Solar | North East Tasmania | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | TAS | Solar | North West Tasmania | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | TAS | Solar | Central Highlands | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | NSW | Solar | New South Wales Non-REZ | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Large scale Solar PV | VIC | Solar | Victoria Non-REZ | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | QLD | Solar | Far North QLD | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | QLD | Solar | North Qld Clean Energy Hub | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | QLD | Solar | Northern Qld | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | QLD | Solar | Isaac | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | QLD | Solar | Barcaldine | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | QLD | Solar | Fitzroy | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | QLD | Solar | Wide Bay | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | QLD | Solar | Darling Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | QLD | Solar | Banana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | North West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | New England | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | Central-West Orana | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | Broken Hill | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | South West NSW | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | Wagga Wagga | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | Tumut | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | Cooma-Monaro | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | Hunter-Central Coast | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | Illawarra | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | VIC | Solar | Ovens Murray | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | VIC | Solar | Murray River | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | VIC | Solar | Western Victoria | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | VIC | Solar | South West Victoria | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | VIC | Solar | Gippsland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | VIC | Solar | Central North Vic | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | SA | Solar | South East SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | SA | Solar | Riverland | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | SA | Solar | Mid-North SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | SA | Solar | Yorke Peninsula | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | SA | Solar | Northern SA | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | SA | Solar | Leigh Creek | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | SA | Solar | Roxby Downs | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | SA | Solar | Eastern Eyre Peninsula | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | SA | Solar | Western Eyre Peninsula | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | TAS | Solar | North East Tasmania | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | TAS | Solar | North West Tasmania | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | TAS | Solar | Central Highlands | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | NSW | Solar | New South Wales Non-REZ | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal (15hrs storage) | VIC | Solar | Victoria Non-REZ | Solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | QLD | Battery | NQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | QLD | Battery | CQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | QLD | Battery | GG | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | QLD | Battery | SQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | NSW | Battery | NNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | NSW | Battery | CNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | NSW | Battery | SNW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | NSW | Battery | SNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | VIC | Battery | VIC | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | SA | Battery | SESA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (1hr storage) | TAS | Battery | TAS | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | QLD | Battery | NQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | QLD | Battery | CQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | QLD | Battery | GG | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | QLD | Battery | SQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | NSW | Battery | NNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | NSW | Battery | CNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | NSW | Battery | SNW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | NSW | Battery | SNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery storage (2hrs storage) | VIC | Battery | VIC | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | SA | Battery | SESA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (2hrs storage) | TAS | Battery | TAS | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | QLD | Battery | NQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | QLD | Battery | CQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | QLD | Battery | GG | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | QLD | Battery | SQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | NSW | Battery | NNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | NSW | Battery | CNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | NSW | Battery | SNW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | NSW | Battery | SNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | VIC | Battery | VIC | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | SA | Battery | SESA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (4hrs storage) | TAS | Battery | TAS | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | QLD | Battery | NQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | QLD | Battery | CQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | QLD | Battery | GG | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | QLD | Battery | SQ | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | NSW | Battery | NNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | NSW | Battery | CNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | NSW | Battery | SNW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | NSW | Battery | SNSW | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | VIC | Battery | VIC | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | SA | Battery | CSA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | SA | Battery | SESA | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Battery Storage (8hrs storage) | TAS | Battery | TAS | Battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | QLD | Wind | Far North QLD | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | QLD | Wind | North Qld Clean Energy Hub | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | QLD | Wind | Northern Qld | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | QLD | Wind | Isaac | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | QLD | Wind | Barcaldine | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | QLD | Wind | Fitzroy | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | QLD | Wind | Wide Bay | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | QLD | Wind | Darling Downs | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | QLD | Wind | Banana | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | North West NSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | New England | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | Central-West Orana | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | Broken Hill | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | South West NSW | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | Wagga Wagga | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | Tumut | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | Cooma-Monaro | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | Hunter-Central Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | Illawarra | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | VIC | Wind | Ovens Murray | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | VIC | Wind | Murray River | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | VIC | Wind | Western Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | VIC | Wind | South West Victoria | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | VIC | Wind | Gippsland | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | VIC | Wind | Central North Vic | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | SA | Wind | South East SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | SA | Wind | Riverland | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | SA | Wind | Mid-North SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | SA | Wind | Yorke Peninsula | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | SA | Wind | Northern SA | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | SA | Wind | Leigh Creek | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | SA | Wind | Roxby Downs | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | SA | Wind | Eastern Eyre Peninsula | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | SA | Wind | Western Eyre Peninsula | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | TAS | Wind | North East Tasmania | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | TAS | Wind | North West Tasmania | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | TAS | Wind | Central Highlands | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | NSW | Wind | New South Wales Non-REZ | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | VIC | Wind | Victoria Non-REZ | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (fixed) | NSW | Wind | Hunter Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (fixed) | NSW | Wind | Illawarra Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (fixed) | VIC | Wind | Gippsland Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (fixed) | VIC | Wind | Portland Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (fixed) | SA | Wind | South East SA Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (fixed) | TAS | Wind | North West Tasmania Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (fixed) | TAS | Wind | North East Tasmania Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (floating) | NSW | Wind | Hunter Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (floating) | NSW | Wind | Illawarra Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (floating) | VIC | Wind | Gippsland Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (floating) | VIC | Wind | Portland Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (floating) | SA | Wind | South East SA Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (floating) | TAS | Wind | North West Tasmania Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind - offshore (floating) | TAS | Wind | North East Tasmania Coast | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | QLD | Water | NQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | QLD | Water | CQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | QLD | Water | GG | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | QLD | Water | SQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | NSW | Water | NNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | NSW | Water | CNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | NSW | Water | SNW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | NSW | Water | SNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | SA | Water | CSA | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | SA | Water | SESA | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | QLD | Water | NQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | QLD | Water | CQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | QLD | Water | GG | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | QLD | Water | SQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | NSW | Water | NNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | NSW | Water | CNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | NSW | Water | SNW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | NSW | Water | SNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | SA | Water | CSA | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | SA | Water | SESA | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (24hrs storage) | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | QLD | Water | NQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | QLD | Water | CQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | QLD | Water | GG | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | QLD | Water | SQ | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | NSW | Water | NNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | NSW | Water | CNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | NSW | Water | SNW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | NSW | Water | SNSW | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | VIC | Water | VIC | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | SA | Water | CSA | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | SA | Water | SESA | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (48hrs storage) | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BOTN - Cethana | TAS | Water | TAS | Hydro | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hydrogen reciprocating engines | QLD | Hydrogen | NQ | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | QLD | Hydrogen | CQ | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | QLD | Hydrogen | GG | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | QLD | Hydrogen | SQ | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | NSW | Hydrogen | NNSW | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | NSW | Hydrogen | CNSW | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | NSW | Hydrogen | SNW | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | NSW | Hydrogen | SNSW | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | VIC | Hydrogen | VIC | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | SA | Hydrogen | CSA | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | SA | Hydrogen | SESA | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen reciprocating engines | TAS | Hydrogen | TAS | Hydrogen | 0 | 0 | 0 | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659

## Regional Build Costs Summary
Go to Assumptions Summary
Generator build costs, after application of locational cost factors ($/kW, real 2023 dollars)
Build costs for new entrant generators by location for the selected scenario and technology. Does not include connection costs.
Cost trajectories calculated by applying locational cost factors to baseline provided for a region-specific cost estimate, as developed by CSIRO and Aurecon.
Technology and scenario choices are available through the drop down menus.
Large-scale renewables
Technology: | Scenario:
Solar Thermal (15hrs Storage) | Green Energy Exports
Technology type | Cost scenario | Candidate REZ | Sub-region | Cost zone | Locational cost factor | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Solar Thermal (15hrs Storage) | Green Energy Exports | Far North QLD | NQ | QLD Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | North Qld Clean Energy Hub | NQ | QLD Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Northern Qld | NQ | QLD Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Isaac | CQ | QLD Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Barcaldine | CQ | QLD Medium | 106.9% | 7461.399 | 7281.868 | 7039.444 | 6747.8491 | 6480.2679 | 6274.4362 | 6076.6091 | 5850.1942 | 5622.6358 | 5427.0957 | 5283.0135 | 5146.9359 | 5032.585 | 4914.8035 | 4815.3182 | 4714.6893 | 4620.9216 | 4503.1401 | 4385.3586 | 4253.855 | 4141.7911 | 4025.1532 | 3932.5289 | 3844.4787 | 3773.5811 | 3706.114 | 3643.221 | 3581.4715 | 3530.0136 | 3479.6992 | 3429.3848 | 3380.2138
Solar Thermal (15hrs Storage) | Green Energy Exports | Fitzroy | CQ | QLD Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508 | Do not delete
Solar Thermal (15hrs Storage) | Green Energy Exports | Wide Bay | SQ | QLD Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508 | OCGT (small GT)
Solar Thermal (15hrs Storage) | Green Energy Exports | Darling Downs | SQ | QLD Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508 | OCGT (large GT)
Solar Thermal (15hrs Storage) | Green Energy Exports | Banana | CQ | QLD Medium | 106.9% | 7461.399 | 7281.868 | 7039.444 | 6747.8491 | 6480.2679 | 6274.4362 | 6076.6091 | 5850.1942 | 5622.6358 | 5427.0957 | 5283.0135 | 5146.9359 | 5032.585 | 4914.8035 | 4815.3182 | 4714.6893 | 4620.9216 | 4503.1401 | 4385.3586 | 4253.855 | 4141.7911 | 4025.1532 | 3932.5289 | 3844.4787 | 3773.5811 | 3706.114 | 3643.221 | 3581.4715 | 3530.0136 | 3479.6992 | 3429.3848 | 3380.2138 | CCGT
Solar Thermal (15hrs Storage) | Green Energy Exports | North West NSW | NNSW | NSW Medium | 106% | 7395.1157 | 7217.1796 | 6976.9092 | 6687.9047 | 6422.7005 | 6218.6973 | 6022.6276 | 5798.2241 | 5572.6872 | 5378.8842 | 5236.0819 | 5101.2132 | 4987.8781 | 4871.1429 | 4772.5414 | 4672.8065 | 4579.8717 | 4463.1365 | 4346.4014 | 4216.066 | 4104.9976 | 3989.3958 | 3897.5943 | 3810.3263 | 3740.0585 | 3673.1908 | 3610.8565 | 3549.6556 | 3498.6548 | 3448.7873 | 3398.9199 | 3350.1858 | CCGT with CCS
Solar Thermal (15hrs Storage) | Green Energy Exports | New England | NNSW | NSW Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508 | Biomass
Solar Thermal (15hrs Storage) | Green Energy Exports | Central-West Orana | CNSW | NSW Medium | 106% | 7395.1157 | 7217.1796 | 6976.9092 | 6687.9047 | 6422.7005 | 6218.6973 | 6022.6276 | 5798.2241 | 5572.6872 | 5378.8842 | 5236.0819 | 5101.2132 | 4987.8781 | 4871.1429 | 4772.5414 | 4672.8065 | 4579.8717 | 4463.1365 | 4346.4014 | 4216.066 | 4104.9976 | 3989.3958 | 3897.5943 | 3810.3263 | 3740.0585 | 3673.1908 | 3610.8565 | 3549.6556 | 3498.6548 | 3448.7873 | 3398.9199 | 3350.1858 | Battery storage (1hr storage)
Solar Thermal (15hrs Storage) | Green Energy Exports | Broken Hill | SNSW | NSW High | 111.6% | 7787.2334 | 7599.8624 | 7346.8519 | 7042.5233 | 6763.257 | 6548.4367 | 6341.9706 | 6105.6684 | 5868.1727 | 5664.0934 | 5513.7193 | 5371.6992 | 5252.3547 | 5129.4297 | 5025.6 | 4920.5767 | 4822.7142 | 4699.7893 | 4576.8644 | 4439.6181 | 4322.6604 | 4200.929 | 4104.2599 | 4012.3645 | 3938.3709 | 3867.9576 | 3802.3181 | 3737.872 | 3684.167 | 3631.6554 | 3579.1437 | 3527.8256 | Battery storage (2hrs storage)
Solar Thermal (15hrs Storage) | Green Energy Exports | South West NSW | SNSW | NSW High | 111.6% | 7787.2334 | 7599.8624 | 7346.8519 | 7042.5233 | 6763.257 | 6548.4367 | 6341.9706 | 6105.6684 | 5868.1727 | 5664.0934 | 5513.7193 | 5371.6992 | 5252.3547 | 5129.4297 | 5025.6 | 4920.5767 | 4822.7142 | 4699.7893 | 4576.8644 | 4439.6181 | 4322.6604 | 4200.929 | 4104.2599 | 4012.3645 | 3938.3709 | 3867.9576 | 3802.3181 | 3737.872 | 3684.167 | 3631.6554 | 3579.1437 | 3527.8256 | Battery storage (4hrs storage)
Solar Thermal (15hrs Storage) | Green Energy Exports | Wagga Wagga | SNSW | NSW Medium | 106% | 7395.1157 | 7217.1796 | 6976.9092 | 6687.9047 | 6422.7005 | 6218.6973 | 6022.6276 | 5798.2241 | 5572.6872 | 5378.8842 | 5236.0819 | 5101.2132 | 4987.8781 | 4871.1429 | 4772.5414 | 4672.8065 | 4579.8717 | 4463.1365 | 4346.4014 | 4216.066 | 4104.9976 | 3989.3958 | 3897.5943 | 3810.3263 | 3740.0585 | 3673.1908 | 3610.8565 | 3549.6556 | 3498.6548 | 3448.7873 | 3398.9199 | 3350.1858 | Battery storage (8hrs storage)
Solar Thermal (15hrs Storage) | Green Energy Exports | Tumut | SNSW | NSW Medium | 106% | 7395.1157 | 7217.1796 | 6976.9092 | 6687.9047 | 6422.7005 | 6218.6973 | 6022.6276 | 5798.2241 | 5572.6872 | 5378.8842 | 5236.0819 | 5101.2132 | 4987.8781 | 4871.1429 | 4772.5414 | 4672.8065 | 4579.8717 | 4463.1365 | 4346.4014 | 4216.066 | 4104.9976 | 3989.3958 | 3897.5943 | 3810.3263 | 3740.0585 | 3673.1908 | 3610.8565 | 3549.6556 | 3498.6548 | 3448.7873 | 3398.9199 | 3350.1858 | Hydrogen reciprocating engines
Solar Thermal (15hrs Storage) | Green Energy Exports | Cooma-Monaro | SNSW | NSW Medium | 106% | 7395.1157 | 7217.1796 | 6976.9092 | 6687.9047 | 6422.7005 | 6218.6973 | 6022.6276 | 5798.2241 | 5572.6872 | 5378.8842 | 5236.0819 | 5101.2132 | 4987.8781 | 4871.1429 | 4772.5414 | 4672.8065 | 4579.8717 | 4463.1365 | 4346.4014 | 4216.066 | 4104.9976 | 3989.3958 | 3897.5943 | 3810.3263 | 3740.0585 | 3673.1908 | 3610.8565 | 3549.6556 | 3498.6548 | 3448.7873 | 3398.9199 | 3350.1858 | Pumped Hydro (8hrs storage)
Solar Thermal (15hrs Storage) | Green Energy Exports | Hunter-Central Coast | CNSW | NSW Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508 | Pumped Hydro (24hrs storage)
Solar Thermal (15hrs Storage) | Green Energy Exports | Hunter Coast | SNW | NSW Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508 | Pumped Hydro (48hrs storage)
Solar Thermal (15hrs Storage) | Green Energy Exports | Illawarra Coast | SNW | NSW Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Illawarra | SNW | NSW Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Ovens Murray | VIC | VIC Medium | 102.7% | 7162.7756 | 6990.4298 | 6757.7082 | 6477.7837 | 6220.9117 | 6023.3179 | 5833.4083 | 5616.0551 | 5397.6042 | 5209.8901 | 5071.5744 | 4940.943 | 4831.1686 | 4718.101 | 4622.5974 | 4525.996 | 4435.981 | 4322.9134 | 4209.8459 | 4083.6054 | 3976.0265 | 3864.0567 | 3775.1395 | 3690.6132 | 3622.5532 | 3557.7863 | 3497.4104 | 3438.1323 | 3388.7338 | 3340.4331 | 3292.1324 | 3244.9294
Solar Thermal (15hrs Storage) | Green Energy Exports | Murray River | VIC | VIC Medium | 102.7% | 7162.7756 | 6990.4298 | 6757.7082 | 6477.7837 | 6220.9117 | 6023.3179 | 5833.4083 | 5616.0551 | 5397.6042 | 5209.8901 | 5071.5744 | 4940.943 | 4831.1686 | 4718.101 | 4622.5974 | 4525.996 | 4435.981 | 4322.9134 | 4209.8459 | 4083.6054 | 3976.0265 | 3864.0567 | 3775.1395 | 3690.6132 | 3622.5532 | 3557.7863 | 3497.4104 | 3438.1323 | 3388.7338 | 3340.4331 | 3292.1324 | 3244.9294 | Large scale Solar PV
Solar Thermal (15hrs Storage) | Green Energy Exports | Western Victoria | VIC | VIC Medium | 102.7% | 7162.7756 | 6990.4298 | 6757.7082 | 6477.7837 | 6220.9117 | 6023.3179 | 5833.4083 | 5616.0551 | 5397.6042 | 5209.8901 | 5071.5744 | 4940.943 | 4831.1686 | 4718.101 | 4622.5974 | 4525.996 | 4435.981 | 4322.9134 | 4209.8459 | 4083.6054 | 3976.0265 | 3864.0567 | 3775.1395 | 3690.6132 | 3622.5532 | 3557.7863 | 3497.4104 | 3438.1323 | 3388.7338 | 3340.4331 | 3292.1324 | 3244.9294 | Solar Thermal (15hrs Storage)
Solar Thermal (15hrs Storage) | Green Energy Exports | South West Victoria | VIC | VIC Medium | 102.7% | 7162.7756 | 6990.4298 | 6757.7082 | 6477.7837 | 6220.9117 | 6023.3179 | 5833.4083 | 5616.0551 | 5397.6042 | 5209.8901 | 5071.5744 | 4940.943 | 4831.1686 | 4718.101 | 4622.5974 | 4525.996 | 4435.981 | 4322.9134 | 4209.8459 | 4083.6054 | 3976.0265 | 3864.0567 | 3775.1395 | 3690.6132 | 3622.5532 | 3557.7863 | 3497.4104 | 3438.1323 | 3388.7338 | 3340.4331 | 3292.1324 | 3244.9294 | Wind
Solar Thermal (15hrs Storage) | Green Energy Exports | Gippsland | VIC | VIC Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508 | Wind - offshore (fixed)
Solar Thermal (15hrs Storage) | Green Energy Exports | Central North Vic | VIC | VIC High | 104.3% | 7277.8991 | 7102.7833 | 6866.3213 | 6581.8977 | 6320.8972 | 6120.1275 | 5927.1656 | 5706.319 | 5484.357 | 5293.6259 | 5153.0872 | 5020.3561 | 4908.8174 | 4793.9326 | 4696.8939 | 4598.7399 | 4507.2782 | 4392.3933 | 4277.5085 | 4149.239 | 4039.9311 | 3926.1616 | 3835.8153 | 3749.9305 | 3680.7765 | 3614.9687 | 3553.6224 | 3493.3916 | 3443.1991 | 3394.1221 | 3345.0451 | 3297.0835 | Wind - offshore (floating)
Solar Thermal (15hrs Storage) | Green Energy Exports | Gippsland Coast | VIC | VIC Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Southern Ocean | VIC | VIC Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | South East SA | SESA | SA Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Riverland | CSA | SA Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Mid-North SA | CSA | SA Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Yorke Peninsula | CSA | SA Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | Northern SA | CSA | SA Medium | 106.8% | 7450.2355 | 7270.9731 | 7028.9118 | 6737.7532 | 6470.5723 | 6265.0486 | 6067.5174 | 5841.4413 | 5614.2234 | 5418.9759 | 5275.1093 | 5139.2352 | 5025.0554 | 4907.4501 | 4808.1137 | 4707.6354 | 4614.0079 | 4496.4027 | 4378.7974 | 4247.4906 | 4135.5943 | 4019.1309 | 3926.6452 | 3838.7267 | 3767.9352 | 3700.5691 | 3637.7701 | 3576.113 | 3524.7321 | 3474.493 | 3424.2538 | 3375.1565
Solar Thermal (15hrs Storage) | Green Energy Exports | Leigh Creek | CSA | SA Medium | 106.8% | 7450.2355 | 7270.9731 | 7028.9118 | 6737.7532 | 6470.5723 | 6265.0486 | 6067.5174 | 5841.4413 | 5614.2234 | 5418.9759 | 5275.1093 | 5139.2352 | 5025.0554 | 4907.4501 | 4808.1137 | 4707.6354 | 4614.0079 | 4496.4027 | 4378.7974 | 4247.4906 | 4135.5943 | 4019.1309 | 3926.6452 | 3838.7267 | 3767.9352 | 3700.5691 | 3637.7701 | 3576.113 | 3524.7321 | 3474.493 | 3424.2538 | 3375.1565
Solar Thermal (15hrs Storage) | Green Energy Exports | Roxby Downs | CSA | SA Medium | 106.8% | 7450.2355 | 7270.9731 | 7028.9118 | 6737.7532 | 6470.5723 | 6265.0486 | 6067.5174 | 5841.4413 | 5614.2234 | 5418.9759 | 5275.1093 | 5139.2352 | 5025.0554 | 4907.4501 | 4808.1137 | 4707.6354 | 4614.0079 | 4496.4027 | 4378.7974 | 4247.4906 | 4135.5943 | 4019.1309 | 3926.6452 | 3838.7267 | 3767.9352 | 3700.5691 | 3637.7701 | 3576.113 | 3524.7321 | 3474.493 | 3424.2538 | 3375.1565
Solar Thermal (15hrs Storage) | Green Energy Exports | Eastern Eyre Peninsula | CSA | SA Medium | 106.8% | 7450.2355 | 7270.9731 | 7028.9118 | 6737.7532 | 6470.5723 | 6265.0486 | 6067.5174 | 5841.4413 | 5614.2234 | 5418.9759 | 5275.1093 | 5139.2352 | 5025.0554 | 4907.4501 | 4808.1137 | 4707.6354 | 4614.0079 | 4496.4027 | 4378.7974 | 4247.4906 | 4135.5943 | 4019.1309 | 3926.6452 | 3838.7267 | 3767.9352 | 3700.5691 | 3637.7701 | 3576.113 | 3524.7321 | 3474.493 | 3424.2538 | 3375.1565
Solar Thermal (15hrs Storage) | Green Energy Exports | Western Eyre Peninsula | CSA | SA Medium | 106.8% | 7450.2355 | 7270.9731 | 7028.9118 | 6737.7532 | 6470.5723 | 6265.0486 | 6067.5174 | 5841.4413 | 5614.2234 | 5418.9759 | 5275.1093 | 5139.2352 | 5025.0554 | 4907.4501 | 4808.1137 | 4707.6354 | 4614.0079 | 4496.4027 | 4378.7974 | 4247.4906 | 4135.5943 | 4019.1309 | 3926.6452 | 3838.7267 | 3767.9352 | 3700.5691 | 3637.7701 | 3576.113 | 3524.7321 | 3474.493 | 3424.2538 | 3375.1565
Solar Thermal (15hrs Storage) | Green Energy Exports | South East SA Coast | SESA | SA Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | North East Tasmania | TAS | TAS Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | North West Tasmania | TAS | TAS Medium | 105.9% | 7390.2317 | 7212.4131 | 6972.3014 | 6683.4877 | 6418.4587 | 6214.5902 | 6018.65 | 5794.3947 | 5569.0068 | 5375.3317 | 5232.6238 | 5097.8441 | 4984.5839 | 4867.9258 | 4769.3894 | 4669.7204 | 4576.8469 | 4460.1889 | 4343.5308 | 4213.2815 | 4102.2865 | 3986.761 | 3895.0202 | 3807.8098 | 3737.5884 | 3670.7649 | 3608.4718 | 3547.3112 | 3496.3441 | 3446.5096 | 3396.6751 | 3347.9732
Solar Thermal (15hrs Storage) | Green Energy Exports | Central Highlands | TAS | TAS Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Solar Thermal (15hrs Storage) | Green Energy Exports | North Tasmania Coast | TAS | TAS Low | 100% | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Thermal generation and storage
Technology: | Scenario:
Pumped Hydro (8hrs storage) | Progressive Change
Technology type | Cost scenario | REZ | Sub-region | Cost zone | Locational cost factor | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Pumped Hydro (8hrs storage) | Progressive Change | - | NQ | QLD Low | 101% | 3389.018 | 3323.1385 | 3259.4189 | 3195.6993 | 3131.9797 | 3066.1001 | 3000.2206 | 2933.261 | 2867.3814 | 2864.1414 | 2859.8215 | 2856.5815 | 2853.3415 | 2850.1015 | 2846.8615 | 2843.6216 | 2840.3816 | 2837.1416 | 2833.9016 | 2829.5817 | 2825.2617 | 2820.9417 | 2816.6217 | 2812.3018 | 2807.9818 | 2803.6618 | 2799.3419 | 2796.1019 | 2791.7819 | 2786.3819 | 2782.062 | 2776.662
Pumped Hydro (8hrs storage) | Progressive Change | - | CQ | QLD Low | 101% | 3389.018 | 3323.1385 | 3259.4189 | 3195.6993 | 3131.9797 | 3066.1001 | 3000.2206 | 2933.261 | 2867.3814 | 2864.1414 | 2859.8215 | 2856.5815 | 2853.3415 | 2850.1015 | 2846.8615 | 2843.6216 | 2840.3816 | 2837.1416 | 2833.9016 | 2829.5817 | 2825.2617 | 2820.9417 | 2816.6217 | 2812.3018 | 2807.9818 | 2803.6618 | 2799.3419 | 2796.1019 | 2791.7819 | 2786.3819 | 2782.062 | 2776.662
Pumped Hydro (8hrs storage) | Progressive Change | - | SQ | QLD Low | 111.4% | 3737.9862 | 3665.323 | 3595.0422 | 3524.7614 | 3454.4806 | 3381.8174 | 3309.1542 | 3235.2997 | 3162.6365 | 3159.0629 | 3154.2981 | 3150.7245 | 3147.1509 | 3143.5773 | 3140.0037 | 3136.4301 | 3132.8565 | 3129.2829 | 3125.7093 | 3120.9445 | 3116.1797 | 3111.4149 | 3106.6501 | 3101.8853 | 3097.1205 | 3092.3557 | 3087.5909 | 3084.0173 | 3079.2525 | 3073.2965 | 3068.5317 | 3062.5757
Pumped Hydro (8hrs storage) | Progressive Change | - | GG | QLD Low | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | Progressive Change | - | NNSW | NSW Low | 88.1% | 2956.1633 | 2898.698 | 2843.1169 | 2787.5357 | 2731.9546 | 2674.4893 | 2617.0241 | 2558.6168 | 2501.1515 | 2498.3254 | 2494.5571 | 2491.731 | 2488.9048 | 2486.0787 | 2483.2525 | 2480.4263 | 2477.6002 | 2474.774 | 2471.9479 | 2468.1796 | 2464.4114 | 2460.6432 | 2456.875 | 2453.1068 | 2449.3386 | 2445.5704 | 2441.8022 | 2438.976 | 2435.2078 | 2430.4975 | 2426.7293 | 2422.019
Pumped Hydro (8hrs storage) | Progressive Change | - | CNSW | NSW Low | 102.5% | 3439.35 | 3372.492 | 3307.8261 | 3243.1602 | 3178.4942 | 3111.6363 | 3044.7783 | 2976.8243 | 2909.9663 | 2906.6782 | 2902.2941 | 2899.006 | 2895.7179 | 2892.4298 | 2889.1417 | 2885.8536 | 2882.5655 | 2879.2774 | 2875.9893 | 2871.6051 | 2867.221 | 2862.8369 | 2858.4528 | 2854.0686 | 2849.6845 | 2845.3004 | 2840.9162 | 2837.6281 | 2833.244 | 2827.7638 | 2823.3797 | 2817.8996
Pumped Hydro (8hrs storage) | Progressive Change | - | SNSW | NSW Medium | 104.4% | 3503.1038 | 3435.0065 | 3369.1419 | 3303.2773 | 3237.4127 | 3169.3154 | 3101.2181 | 3032.0044 | 2963.9071 | 2960.5581 | 2956.0927 | 2952.7436 | 2949.3946 | 2946.0455 | 2942.6965 | 2939.3474 | 2935.9984 | 2932.6493 | 2929.3003 | 2924.8349 | 2920.3695 | 2915.9041 | 2911.4387 | 2906.9733 | 2902.5079 | 2898.0425 | 2893.5771 | 2890.2281 | 2885.7627 | 2880.1809 | 2875.7155 | 2870.1338
Pumped Hydro (8hrs storage) | Progressive Change | - | SNW | NSW Low | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | Progressive Change | - | VIC | VIC Low | 100% | 3355.4634 | 3290.2361 | 3227.1474 | 3164.0587 | 3100.97 | 3035.7427 | 2970.5154 | 2904.2188 | 2838.9915 | 2835.7836 | 2831.5064 | 2828.2985 | 2825.0906 | 2821.8827 | 2818.6748 | 2815.4669 | 2812.259 | 2809.0511 | 2805.8432 | 2801.566 | 2797.2888 | 2793.0116 | 2788.7344 | 2784.4572 | 2780.18 | 2775.9028 | 2771.6256 | 2768.4177 | 2764.1405 | 2758.794 | 2754.5168 | 2749.1703
Pumped Hydro (8hrs storage) | Progressive Change | - | CSA | SA Low | 135.1% | 4533.2311 | 4445.109 | 4359.8761 | 4274.6433 | 4189.4105 | 4101.2884 | 4013.1663 | 3923.5996 | 3835.4775 | 3831.1436 | 3825.3651 | 3821.0313 | 3816.6974 | 3812.3635 | 3808.0297 | 3803.6958 | 3799.3619 | 3795.028 | 3790.6942 | 3784.9157 | 3779.1372 | 3773.3587 | 3767.5802 | 3761.8017 | 3756.0232 | 3750.2447 | 3744.4662 | 3740.1323 | 3734.3538 | 3727.1307 | 3721.3522 | 3714.1291
Pumped Hydro (8hrs storage) | Progressive Change | - | SESA | SA Medium | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Pumped Hydro (8hrs storage) | Progressive Change | - | TAS | TAS Low | 74.8% | 2509.8866 | 2461.0966 | 2413.9063 | 2366.7159 | 2319.5256 | 2270.7355 | 2221.9455 | 2172.3557 | 2123.5656 | 2121.1661 | 2117.9668 | 2115.5673 | 2113.1678 | 2110.7683 | 2108.3688 | 2105.9692 | 2103.5697 | 2101.1702 | 2098.7707 | 2095.5714 | 2092.372 | 2089.1727 | 2085.9733 | 2082.774 | 2079.5746 | 2076.3753 | 2073.1759 | 2070.7764 | 2067.5771 | 2063.5779 | 2060.3786 | 2056.3794

## Energy Policy Targets
Go to Assumptions Summary
Energy policies
Note: When targets are set for a given calendar year, AEMO assumes they will be met by the end of the financial year ending on that given year.
Constraints will be applied subject to technology lead times.
Emission targets
As further discussed in the 2023 IASR, AEMO will model in the ISP emission targets for Australia as legislated in the Climate Change Act 2022.
ISP modelling will also incorporate state-level emission reduction ambtitions in New South Wales, South Australia, and Victoria.
Further detail on emission reduction ambitions and their incorporation into the modelling can be found in the 2023 IASR report. The Carbon Budgets tab presents the set of emission constraints that will be applied in the 2024 ISP.
Australia
Powering Australia Plan 2030 target
Announced in the Powering Australia Plan, the Federal Government has committed to achieving an 82% share of renewable generation by 2030.
Assumed to be a financial year target.
AEMO interpolates the required developments to meet the objective of the Powering Australia Plan, smoothing out the trajectory to meet 82%. The starting point in the 2024 ISP for Progressive Change and Step Change are from intermediate model runs without an 82% constraint applied for those years, but all other Energy Policy Targets.
In Green Energy Export, the annual targets are the result of a linear interpolation from historicals in 2023, unchanged from the Draft 2024 ISP. The constraint is extended forward by an additional year in Progressive Change to limit significant year on year growth.
Financial year | All scenarios
2029-30 | 82%
Formulation
This policy has been formulated as an annual trajectory, as follows:
where:
Large-scale renewable includes existing and new hydro, solar PV, Concentrated Solar Thermal, onshore wind, offshore wind, and biomass technologies.
Trajectory of minimum VRE share of generation to 2029-30
Financial year | 2027-28 | 2028-29 | 2029-30
Step Change |  | 71% | 82%
Progressive Change | 63% | 66% | 82%
Green Energy Exports |  | 75.57% | 82%
Notes |  |  | Target year
Capacity Investment Scheme - Renewable capacity target
Announced in the Capacity Investment Scheme (CIS), the Federal Government has committed to deliver 32GW of new renewable capacity nation-wide, including 23GW of renewable capacity by 2030.
Assumed to be a financial year target.
NEM share is assumed to be 80% of target, scaling the target down to 18,400 MW.
To ensure an appropiate year-on-year level of growth in the period to 2030, the constraint is formulated such that builds are less or equal than the target. To avoid infeasibilities with other RETs, the constraint is modelled as a soft constraint with a penalty price of 100,000.
Formulation
The constraint on renewable generation capacity in NEM is formulated as follows:
where:
CIS eligible renewables includes new solar PV, onshore wind, and offshore wind in NEM.
Trajectory of minimum renewable capacity target
Financial year | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
Renewable capacity target (MW) | 0 | 0 | 4000 | 8400 | 13240 | 18400
Capacity Investment Scheme - Clean dispatchable capacity target
Announced in the Capacity Investment Scheme, the Federal Government has committed to deliver 32GW of renewable capacity national-wide, including 9GW of dispatchable storage capacity by 2030.
Assumed to be a financial year target.
As reported by DCCEEW, the CIS Stage 1 tender includes 1,075MW of anticipated projects which contribute to the target.
The share of NEM is assumed 80% of target. It is also assumed that there is a 9% share from Virtual Power Plants (VPPs), aligned with the share of VPP in the CIS stage 1 tender.
Formulation
The constraint on renewable generation capacity in NEM is formulated as follows:
where:
CIS clean dispatchable capacity includes new Concentrated Solar Thermal, Pumped Hydro, Battery, Hydrogen Reciprocating Engines, and Biomass.
Trajectory of minimum storage capacity target
Financial year | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
Storage target (MW) | 0 | 0 | 1531 | 3062.5 | 4593.75 | 6125
New South Wales
New South Wales Electricity Infrastructure Roadmap
The Act sets out minimum objective of construction of renewable generation infrastructure that produces at least the same amount of electricity in a year as 8 GW in New England, 3 GW in Central-West Orana and 1 GW of additional capacity by the end of 31 December 2029. The NSW Consumer Trustee, with AEMO, determined this to be approximately 33,600 GWh per year.
The Act also includes a minimum target of the construction of 2 GW of long-duration (8 hours or more) storage infrastructure by 31 December 2029 in addition to Snowy 2.0.
The annual construction trajectory of energy generating capability that is specified in the Consumer Trustee's 2023 Draft Infrastructure Investment Opportunities Report over the period until the minimum objective is met will be applied as a modelling input (providing a development floor that the model can exceed if appropriate). That trajectory outlines 33,600 GWh of equivalent generating capacity by the 31 December 2029.
Formulation of renewable constraint
The constraint on renewable generation capacity in New South Wales is formulated as follows:
where:
Eligible large-scale renewables includes new and existing, committed and anticipated (so long as they were not identified as committed or anticipated in Generation Information as of November 2019) solar PV, Concentrated Solar Thermal, onshore wind, offshore wind, and biomass in NSW. It also includes eligible projects from Tender Round 1.
The constraint is defined on installed capacity rather than generation, as specified in the Act. The coefficients for each generator are defined based on average generator-specific capacity factors.
Trajectory of minimum VRE generation
Financial year | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
NSW EIR Generation (GWh) | 5547 | 12898 | 16623 | 22018 | 27344 | 33237 | 33600
The trajectory for 2029-30 is set to 33,600 GWh instead of what is in the Draft IIO of 35,662 GWh.
Formulation of storage constraint
where:
Eligible large-scale storage includes new 8hr batteries, and 8hr, 24hr, and 48hr PHES in New South Wales.
Trajectory of minimum storage capacity target
Financial year | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30
Storage target (MW) | 0 | 0 | 0 | 0 | 325 | 325 | 2000
Formulation of firming constraint
where:
Eligible installed capacity includes CCGT, CCGT with CCS, OCGTs, Batteries and Biomass in SNW.
The firming target is 930 MW in 2025-26 and zero all other financial year. It reflects the NSW Consumer Trustee announced competitive tender for long-term energy services agreements (LTESAs) for firming infrastructure which targets 380 MW of firming, as well as an additional 550 MW under the Capacity Investment Scheme as announced by the Federal government.
Source: | Firming Infrastructure (aemoservices.com.au)
Capacity Investment Scheme ¦ energy.gov.au
Long-term energy services agreements (LTESAs)
AEMO Services Limited has concluded its first round of LTESA tenders. The awarded projects will be incorporated into the model.
Additionally, the second competitive tender round targetting 380 MW of firming, expected to be operational by summer 2025-26 will also be incorporated via a constraint.
Source: | 010523-asl-mr-aemo-services-nation-leading-tender-and-contract-design-delivers-for-nsw.pdf (aemoservices.com.au)
New South Wales Renewable Fuels Scheme
This is legislated to produce 8 PJ per annum of renewable enrgy by 2030. Its impact is included in hydrogen production trajectories for each scenario.
Source: | Renewable Fuel Scheme ¦ NSW Climate and Energy Action
Queensland
Updated Queensland Renewable Energy Target (QRET)
In 2015, QRET was announced establishing a 50% renewable energy target.
The Queensland Energy and Jobs Plan announced an updated QRET, setting out a 2030, 2032 and 2035 target. This target is expected to be legislated.
QRET uses underlying electricity consumption as the denominator for its relevant 2030, 2032 and 2035 targets.
AEMO linearly interpolates the required developments to meet the objective of the QRET. The starting point includes historical levels of renewable energy (including distributed PV) linearly interpolated to the 2030, 2032 and 2035 target.
Source: | https://www.epw.qld.gov.au/energyandjobsplan/about
Financial year | All scenarios
2029-30 | 50%
2031-32 | 70%
2034-35 | 80%
Formulation
The constraint on generation in Queensland is formulated as follows:
where:
Large-scale renewable includes existing and new hydro, solar PV, Concentrated Solar Thermal, onshore wind, and biomass technologies.
Trajectory of minimum VRE share of generation
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
QRET share | 25% | 28.57% | 32.14% | 35.71% | 39.29% | 42.86% | 46.43% | 50% | 60% | 70% | 73.33% | 76.67% | 80%
Notes | 2022-23: Historical renewable penetration for 2022-23; 2029-30: Target year; 2031-32: Target year; 2034-35: Target year
South Australia
Hydrogen Jobs Plan
Seeks to establish hydrogen production and power generation in South Australia. The output from a 250 MWe electrolyser project is included in the hydrogen production forecasts for each scenario. A 200 MW hydrogen fuelled generator is also incorporated into the model.
Source: | 2022-23: About the project ¦ Office of Hydrogen Power South Australia (ohpsa.sa.gov.au)
Tasmania
Tasmania Renewable Energy Target (TRET)
Renewable generation targets (in GWh) for NEM-connected equipment in Tasmania (including CER and non-scheduled generation) on or before 31 December 2030, and on or before 31 December 2040.
AEMO linearly interpolates the required developments to meet the objective of the TRET. The starting point includes historical levels of renewable energy generation (including distributed PV and non-scheduled generation). The trajectory is then linearly interporlated to the 2030 and 2040 targets.
Source: | 2022-23: Tasmanian Renewable Energy Target
GWh of renewable generation
Calendar year | 2022-23: All scenarios
2030 | 2022-23: 15750
2040 | 2022-23: 21000
Formulation of renewable constraint
Where:
Large-scale renewables includes hydro, solar PV, CST, onshore wind and offshore wind.
Financial year | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Generation target (GWh) | 10775 | 11485.7143 | 12196.4286 | 12907.1429 | 13617.8571 | 14328.5714 | 15039.2857 | 15750 | 16275 | 16800 | 17325 | 17850 | 18375 | 18900 | 19425 | 19950 | 20475 | 21000
Notes | 2022-23: Historical renewable generation for 2022-23; 2029-30: Target year; 2039-40: Target year
Victoria
Updated Victorian Renewable Energy Target (VRET)
The updated VRET is expected to be enshrined in legislation. It sets out a target for new entry renewable capacity required to meet 40% renewable energy generation as a percentage of total Victorian generation by 2025, 65% by 2030, and 95% by 2035.
The currently legislated VRET mandates 40% renewable energy generation as a percentage of total Victorian Genration by 2025, and 50% by 2030.
The targets accounts for the contribution of CER. AEMO linearly interpolates the required developments to meet the objective of the VRET as seen below.
Source: | 2022-23: https://www.energy.vic.gov.au/renewable-energy/victorian-renewable-energy-and-storage-targets
Calendar year | 2022-23: All scenarios
2025 | 2022-23: 40%
2030 | 2022-23: 65%
2035 | 2022-23: 95%
Formulation of renewable constraint
where:
Large–scale renewables include hydro, solar PV, Concentrated Solar Thermal, onshore wind, offshore wind, and biomass.
Trajectory of minimum VRE share of generation
Financial year | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
VRET share | 40% | 45% | 50% | 55% | 60% | 65% | 71% | 77% | 83% | 89% | 95%
Notes | 2024-25: Target year; 2029-30: Target year; 2034-35: Target year
VRET Auctions
VRET1 and VRET2 announced a number of successful projects contributing to VRET.
Announced projects under VRET1 and VRET2 will be incorporated to ensure the outcomes of the auctions are delivered.
Source: | 2024-25: https://www.energy.vic.gov.au/renewable-energy/victorian-renewable-energy-and-storage-targets/victorian-renewable-energy-target-auction-vret2
Victorian Renewable Energy Target auction (VRET1)
Victorian Energy Storage Target
Target including shallow, medium and deep duration energy storage systems.
AEMO will linearly interpolate these targets to create a trajectory to 2035. Targets are assumed to be calendar year.
Source: | 2024-25: https://www.energy.vic.gov.au/renewable-energy/victorian-renewable-energy-and-storage-targets
Calendar year | 2024-25: All scenarios
2030 | 2024-25: 2.6 GW
2035 | 2024-25: 6.3 GW
Formulation of storage constraint
where:
Eligible large-scale storage includes existing, anticipated, committed and new entrant batteries of 1hr - 8hr, as well as pumped hydro of 8hr - 48 hr.
Financial year | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35
Storage target (MW) | 0 | 0 | 650 | 1300 | 1950 | 2600 | 3120 | 3640 | 4160 | 4680 | 6300
Notes | 2029-30: Target year; 2034-35: Target year
Victorian Offshore Wind Target
Targeting Victorian offshore wind generation capacity. Assumed to be calendar years.
AEMO will linearly interpolate these targets to create a trajectory between the target years as shown below. The starting year for the trajectory is 2028, the year in which first power from offshore wind is expected. This is then linearly interpolated to the 2032, 2035 and 2040 targets.
Source: | 2024-25: https://www.energy.vic.gov.au/renewable-energy/offshore-wind-energy
Calendar year | 2024-25: All scenarios
2032 | 2024-25: 2.0 GW
2035 | 2024-25: 4.0 GW
2040 | 2024-25: 9.0 GW
Formulation of offshore wind constraint
where:
Offshore wind refers to fixed and floating offshore wind in Gippsland Coast and Portland Coast.
Financial year | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
Offshore Wind capacity target (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 2000 | 2667 | 3333 | 4000 | 5000 | 6000 | 7000 | 8000 | 9000
Notes | 2028-29: Expected first power; 2031-32: Target year; 2034-35: Target year; 2039-40: Target year
("Large−scale renewables" +"Distributed PV generation" )/("Large−scale renewables" +"Distributed PV" +"Thermal generation" )≥"minimum renewable energy generation share"
"Large–scale renewables"+"Distributed PV generation"≥"Underlying electricity consumption"×"minimum renewable generation share"
∑_"Eligible large−scale renewables" ▒〖"(Installed " 〖"capacity" 〗_𝑖×"Generator " 〖"coefficient" 〗_𝑖)〗≥"NSW EIR generation target"
"Eligible large–scale storage capacity "≥"NSW EIR storage target"
"Eligible large–scale storage capacity"≥"minimum storage target"
"Offshore wind installed capacity "≥"minimum Offshore Wind capacity target"
"Large−scale renewables"+"Distributed PV"+"renewable non−scheduled generation"≥"Generation target"
("Large-scale renewables" +"Distributed PV generation" )/("Large−scale renewables" +"Distributed PV" +"Thermal generation" )≥"minimum renewable energy generation share"
"Eligible installed capacity "≥"Firming target"
∑_"CIS eligilble renewables" ▒〖"Installed " 〖"capacity" 〗_𝑖 〗≤"CIS Renewable capacity target"
∑_"CIS clean dispatchale capacity " ▒〖"Installed " 〖"capacity" 〗_𝑖 〗≥"CIS clean dispatchable capacity target"

## Carbon Budgets
Go to Assumptions Summary
Cumulative NEM-wide carbon budgets
To model emissions reductions, cumulative carbon budgets have been determined using multi-sectoral modelling commissioned from the CSIRO and ClimateWorks Centre to reflect the emissions reduction requirements consistent with each scenario's Representative Concentration Pathway (RCP). The carbon budget below applies to the NEM only.
Addionally, AEMO will incorporate a carbon budget consistent with the Federal Government's Climate Change Act, limiting emissions to 43% below 2005 levels by 2030 and Net Zero by 2050
More information on the derivation of these budgets can be found in the 2023 IASR.
| Green Energy Exports | Step Change | Progressive Change
Global mean temperature increase by 2100 (ºC) | 1.5°C | 1.8°C | 2.6°C
Federal government’s 2030 carbon budget - NEM carbon budget for FYE 2025-2030 (Mt CO2-e)2 | 630 | 630 | 630
Long-term temperature-linked carbon budget - NEM carbon budget for FYE 2025-52 (Mt CO2-e) | 357 | 681 | 1203
Source: Cumulative carbon budgets determined from multi-sectoral modelling commissioned from the CSIRO and ClimateWorks Centre
Notes:
1. Carbon budgets start from FY2025 to be consistent with the ISP 2024 modelling horizon (2025 - 2052 FYE).
2. The carbon budget to 2030 has been derived to meet the emission budget as stipulated in the Climate Change Act (2022). The commensurate NEM carbon budget proposed in the table has been calculated based on the Progressive Change scenario’s forecast NEM emissions from the multi-sectoral modelling conducted by CSIRO and ClimateWorks Centre. For further details please see the IASR report.
Cumulative state-based carbon budgets
AEMO will incorporate carbon budgets to reflect economy-wide state government emission reduction targets. In particular, emission reduction targets in NSW in 2030 (50% reduction from 2005 levels), in 2035 (70% reduction from 2005 levels) and 2050 (net zero); in Queensland in 2030 (30% reduction from 2005 level), in 2035 (75% reduction from 2005 level), and 2050 (net zero) targets; South Australia's currently legislated target for 2050 (60% reduction compared to 1990 levels); and Victoria's 2025 (28-33% reduction from 2005 levels), 2030 (45-50% reduction from 2005 levels) and 2035 (net zero) targets have been converted to state-level, NEM-only carbon budgets.
AEMO derived states' carbon budgets using a similar approach to the NEM-wide carbon budget. The states’ economy-wide emission reduction point targets are scaled down to a states’ electricity target using pro-rata factors based on state emissions data from the Clean Energy Regulator and the economy-wide emission figures from the Department of Climate Change, Energy, the Environment and Water. Linear trajectories to those electricity-wide emission reduction point targets are then aggregated to produce the cumulative carbon budgets shown below.
More information on the derivation of these budgets can be found in the 2023 IASR.
State | 2024-25 to 2029-30 | 2030-31 to 2051-52 | 2024-25 to 2051-52
NSW | 212 | 241 | Not Applicable
QLD | 269 | 252 | Not Applicable
SA | Not Applicable | Not Applicable | 65
VIC1 | 212 | 151 | Not Applicable
Notes:
1. Carbon budgets for Victoria have been re-calculated to use a consistent approach to mapping calendar to financial years. This has resulted in a slight adjustment downwards of the two carbon budgets.

## Demand and Energy Forecasts
Go to Assumptions Summary
Demand and Energy Forecasts
Final energy consumption and seasonal maximum demand forecasts for all scenarios will be published on the AEMO National Electricity and Gas Forecasting portal.
The most recently published forecast is the 2023 ESOO publication and the draft forecast for the 2024 ISP.
The Forecasting Portal can be accessed at | https://forecasting.aemo.com.au/
Example method of extracting the correct dataset shown below. Instructions for how to use the Forecasting Portal are available via More Information >> Forecast portal user guide

## DSP
Go to Assumptions Summary
Demand Side Participation (MW)
Expected voluntary consumer demand management representing the most likely amount of operational demand reduction, in MW, as a result of DSP, including wholesale demand response (WDR). The Reliability Response value reflects responses to both price and network reliability programs combined, as expected during actual LOR2 or LOR3 events. Forecast maximum demand is 'gross' of this demand response. | [12 empty] | See AEMO’s reserve level declaration guidelines for more detail about LOR2 and LOR3.
For example, users assessing forecast DSP demand reductions for Green Energy Exports in New South Wales, summer, 2023-24 would find no response for prices lower than $1000/MWh, a reduction of 94 MW forecast when prices are between $1000/MWh and $7500/MWh and a total reduction of 95 MW for prices above $7500/MWh. In case of a reliability event, the combined response would be 337 MW. | [12 empty] | https://www.aemo.com.au/-/media/files/electricity/nem/security_and_reliability/power_system_ops/ reserve-level-declaration-guidelines.pdf
The NSW Peak Demand Reduction Scheme (PDRS) is accounted for in the summer DSP forecast for New South Wales. It's assumed that the scheme would impact the demand response in summer to the reliability triggers as well as the highest price trigger, $7500/ MWh. Further details on the PDRS assumptions are in the IASR.
Green Energy Exports
New South Wales
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 93.74 | 105.33 | 117.55 | 130.37 | 142.99 | 193.32 | 240.22 | 278.9 | 317.6 | 356.3 | 363.21 | 369.54 | 374.3 | 380.21 | 386.1 | 389.85 | 393.18 | 397.6 | 399.67 | 402.24 | 405.35 | 404.66 | 415.82 | 426.96 | 436.15 | 446.87 | 457.18 | 459.5 | 467 | 475.64 | 485.41
$7,500 + | 94.74 | 106.46 | 118.8 | 131.76 | 144.51 | 195.38 | 242.78 | 281.88 | 320.99 | 360.1 | 367.08 | 373.48 | 378.3 | 384.27 | 390.22 | 394.01 | 397.37 | 401.84 | 403.94 | 406.53 | 409.67 | 408.97 | 420.25 | 431.51 | 440.81 | 451.63 | 462.06 | 464.4 | 471.99 | 480.72 | 490.59
Reliability Response | 336.75 | 378.39 | 422.28 | 468.34 | 513.66 | 694.47 | 862.96 | 1001.92 | 1140.94 | 1279.96 | 1304.76 | 1327.51 | 1344.63 | 1365.85 | 1387 | 1400.47 | 1412.44 | 1428.32 | 1435.77 | 1444.99 | 1456.14 | 1453.66 | 1493.76 | 1533.78 | 1566.81 | 1605.3 | 1642.35 | 1650.67 | 1677.64 | 1708.67 | 1743.76
Reliability response in % of peak demand* | 2.4% | 2.64% | 2.87% | 3.11% | 3.34% | 4.41% | 5.34% | 6.03% | 6.7% | 7.36% | 7.36% | 7.36% | 7.36% | 7.36% | 7.36% | 7.36% | 7.36% | 7.36% | 7.36% | 7.36% | 7.36% | 7.36% | 7.56% | 7.8% | 8.03% | 8.27% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
* The estimated percentage is in most years set by the NSW PDRS, adjusted to account for the target being only for the state of NSW (i.e. excluding ACT) and removing contributions likely from energy efficiency and coordinated EV and battery storage load, which are modelled separately.
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 93.74 | 104.7 | 116.51 | 128.06 | 140.2 | 153.27 | 167.39 | 182.18 | 196.4 | 210.79 | 224.47 | 238.83 | 253.84 | 268.4 | 282.9 | 296.01 | 310.07 | 324.93 | 339.81 | 353.43 | 365.3 | 376.19 | 386.49 | 396.55 | 405.91 | 413.32 | 422.26 | 424.36 | 429.7 | 437.44 | 445.27
$7,500 + | 94.74 | 105.82 | 117.75 | 129.43 | 141.69 | 154.9 | 169.18 | 184.12 | 198.49 | 213.04 | 226.86 | 241.38 | 256.55 | 271.26 | 285.92 | 299.17 | 313.38 | 328.39 | 343.43 | 357.2 | 369.2 | 380.2 | 390.61 | 400.78 | 410.24 | 417.73 | 426.77 | 428.89 | 434.28 | 442.11 | 450.02
Reliability Response | 336.74 | 376.13 | 418.52 | 460.03 | 503.62 | 550.57 | 601.32 | 654.44 | 705.51 | 757.21 | 806.35 | 857.94 | 911.86 | 964.15 | 1016.27 | 1063.36 | 1113.86 | 1167.23 | 1220.68 | 1269.61 | 1312.26 | 1351.36 | 1388.37 | 1424.53 | 1458.13 | 1484.76 | 1516.89 | 1524.42 | 1543.6 | 1571.42 | 1599.54
Reliability response in % of peak demand | 2.57% | 2.8% | 3.03% | 3.25% | 3.48% | 3.71% | 3.94% | 4.17% | 4.39% | 4.62% | 4.85% | 5.08% | 5.31% | 5.53% | 5.76% | 5.99% | 6.22% | 6.45% | 6.68% | 6.9% | 7.13% | 7.36% | 7.59% | 7.82% | 8.04% | 8.27% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
Queensland
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 22.02 | 24.65 | 27.44 | 30.25 | 33.18 | 36.62 | 40.55 | 44.72 | 48.82 | 52.65 | 56.53 | 60.62 | 65.01 | 69.37 | 73.72 | 77.91 | 82 | 86.44 | 90.92 | 95.38 | 99.67 | 103.33 | 107.15 | 111.11 | 114.96 | 118.63 | 122.41 | 123.47 | 125.75 | 128.71 | 131.56
$500 - $1,000 | 54.15 | 60.61 | 67.47 | 74.38 | 81.6 | 90.04 | 99.72 | 109.98 | 120.05 | 129.48 | 139.02 | 149.07 | 159.87 | 170.6 | 181.3 | 191.59 | 201.64 | 212.56 | 223.58 | 234.56 | 245.1 | 254.1 | 263.5 | 273.25 | 282.71 | 291.72 | 301.03 | 303.63 | 309.24 | 316.52 | 323.51
$1,000 - $7,500 | 151.86 | 169.98 | 189.21 | 208.6 | 228.84 | 252.52 | 279.67 | 308.44 | 336.67 | 363.11 | 389.88 | 418.05 | 448.36 | 478.43 | 508.43 | 537.3 | 565.49 | 596.1 | 627 | 657.81 | 687.36 | 712.61 | 738.96 | 766.3 | 792.83 | 818.1 | 844.21 | 851.51 | 867.25 | 887.65 | 907.27
$7,500 + | 189.12 | 211.69 | 235.63 | 259.78 | 284.99 | 314.48 | 348.29 | 384.12 | 419.27 | 452.2 | 485.55 | 520.63 | 558.36 | 595.82 | 633.18 | 669.13 | 704.24 | 742.36 | 780.84 | 819.21 | 856.01 | 887.46 | 920.27 | 954.32 | 987.36 | 1018.83 | 1051.34 | 1060.43 | 1080.04 | 1105.44 | 1129.87
Reliability Response | 261.52 | 292.73 | 325.84 | 359.23 | 394.09 | 434.86 | 481.62 | 531.16 | 579.78 | 625.31 | 671.42 | 719.93 | 772.12 | 823.91 | 875.57 | 925.29 | 973.83 | 1026.55 | 1079.76 | 1132.81 | 1183.71 | 1227.19 | 1272.56 | 1319.64 | 1365.34 | 1408.85 | 1453.81 | 1466.39 | 1493.5 | 1528.62 | 1562.41
Reliability response in % of peak demand | 2.51% | 2.74% | 2.97% | 3.2% | 3.43% | 3.66% | 3.89% | 4.12% | 4.35% | 4.58% | 4.81% | 5.04% | 5.28% | 5.51% | 5.74% | 5.97% | 6.2% | 6.43% | 6.66% | 6.89% | 7.12% | 7.35% | 7.58% | 7.81% | 8.04% | 8.27% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 22.02 | 25.09 | 28.32 | 31.46 | 34.99 | 39.14 | 43.9 | 48.98 | 53.93 | 58.43 | 62.77 | 67.68 | 73.18 | 78.41 | 83.53 | 88.31 | 93.04 | 98.36 | 103.87 | 109.31 | 114.07 | 118.08 | 122.43 | 127.12 | 131.79 | 136.53 | 141 | 141.96 | 144.86 | 148.22 | 151.59
$500 - $1,000 | 54.15 | 61.7 | 69.63 | 77.38 | 86.05 | 96.24 | 107.95 | 120.44 | 132.63 | 143.7 | 154.35 | 166.44 | 179.96 | 192.82 | 205.42 | 217.16 | 228.79 | 241.88 | 255.42 | 268.81 | 280.52 | 290.37 | 301.07 | 312.62 | 324.09 | 335.74 | 346.75 | 349.09 | 356.24 | 364.5 | 372.78
$1,000 - $7,500 | 151.86 | 173.04 | 195.27 | 216.99 | 241.32 | 269.91 | 302.73 | 337.77 | 371.95 | 402.99 | 432.87 | 466.78 | 504.68 | 540.74 | 576.08 | 609.01 | 641.63 | 678.35 | 716.32 | 753.85 | 786.71 | 814.33 | 844.33 | 876.71 | 908.89 | 941.57 | 972.43 | 978.99 | 999.04 | 1022.22 | 1045.44
$7,500 + | 189.12 | 215.5 | 243.19 | 270.23 | 300.52 | 336.13 | 377.01 | 420.65 | 463.21 | 501.87 | 539.08 | 581.31 | 628.51 | 673.41 | 717.43 | 758.43 | 799.06 | 844.78 | 892.07 | 938.81 | 979.74 | 1014.13 | 1051.49 | 1091.82 | 1131.89 | 1172.59 | 1211.02 | 1219.19 | 1244.16 | 1273.04 | 1301.95
Reliability Response | 189.12 | 215.5 | 243.18 | 270.23 | 300.52 | 336.12 | 377.01 | 420.64 | 463.2 | 501.86 | 539.07 | 581.3 | 628.49 | 673.4 | 717.41 | 758.42 | 799.05 | 844.77 | 892.06 | 938.79 | 979.72 | 1014.11 | 1051.47 | 1091.8 | 1131.87 | 1172.57 | 1211 | 1219.17 | 1244.14 | 1273.01 | 1301.92
Reliability response in % of peak demand | 2.2% | 2.44% | 2.69% | 2.93% | 3.17% | 3.41% | 3.65% | 3.9% | 4.14% | 4.38% | 4.62% | 4.87% | 5.11% | 5.35% | 5.59% | 5.84% | 6.08% | 6.32% | 6.56% | 6.8% | 7.05% | 7.29% | 7.53% | 7.77% | 8.02% | 8.26% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
South Australia
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 25.57 | 31.38 | 38.23 | 45.27 | 51.85 | 58.04 | 65.07 | 73.4 | 82.01 | 90.87 | 99.92 | 108.76 | 117.63 | 127.22 | 137.11 | 146.76 | 156.77 | 166.86 | 177.11 | 186.34 | 195.44 | 204.33 | 212.43 | 220.55 | 227.99 | 234.83 | 243.35 | 245.19 | 247.19 | 249.48 | 252.03
$500 - $1,000 | 40 | 49.1 | 59.8 | 70.81 | 81.11 | 90.79 | 101.79 | 114.82 | 128.29 | 142.15 | 156.31 | 170.14 | 184.02 | 199.01 | 214.49 | 229.58 | 245.24 | 261.03 | 277.06 | 291.5 | 305.74 | 319.64 | 332.32 | 345.01 | 356.65 | 367.36 | 380.69 | 383.56 | 386.68 | 390.27 | 394.25
$1,000 - $7,500 | 43.63 | 53.55 | 65.22 | 77.24 | 88.47 | 99.03 | 111.03 | 125.24 | 139.94 | 155.05 | 170.49 | 185.58 | 200.72 | 217.08 | 233.95 | 250.42 | 267.49 | 284.72 | 302.2 | 317.96 | 333.49 | 348.65 | 362.47 | 376.32 | 389.01 | 400.7 | 415.24 | 418.37 | 421.77 | 425.68 | 430.03
$7,500 + | 48.57 | 59.61 | 72.61 | 85.98 | 98.48 | 110.24 | 123.6 | 139.42 | 155.78 | 172.61 | 189.79 | 206.59 | 223.44 | 241.65 | 260.44 | 278.77 | 297.78 | 316.96 | 336.42 | 353.96 | 371.24 | 388.12 | 403.52 | 418.93 | 433.06 | 446.07 | 462.25 | 465.74 | 469.53 | 473.88 | 478.72
Reliability Response | 48.57 | 59.62 | 72.61 | 85.98 | 98.49 | 110.25 | 123.6 | 139.42 | 155.78 | 172.61 | 189.8 | 206.59 | 223.45 | 241.66 | 260.44 | 278.77 | 297.78 | 316.96 | 336.42 | 353.96 | 371.25 | 388.13 | 403.52 | 418.93 | 433.07 | 446.07 | 462.26 | 465.75 | 469.54 | 473.89 | 478.73
Reliability response in % of peak demand | 1.44% | 1.71% | 1.98% | 2.25% | 2.52% | 2.79% | 3.07% | 3.34% | 3.61% | 3.88% | 4.15% | 4.42% | 4.7% | 4.97% | 5.24% | 5.51% | 5.78% | 6.05% | 6.33% | 6.6% | 6.87% | 7.14% | 7.41% | 7.68% | 7.96% | 8.23% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 25.57 | 30.75 | 36.23 | 42.15 | 47.31 | 52.54 | 58.43 | 65.74 | 72.99 | 80.56 | 87.9 | 95.57 | 103.16 | 111.19 | 119.13 | 126.84 | 135.52 | 144.33 | 152.95 | 160.49 | 167.55 | 174.3 | 181.5 | 187.98 | 193.28 | 199.41 | 206.23 | 207.2 | 208.73 | 209.96 | 211.66
$500 - $1,000 | 40 | 48.1 | 56.67 | 65.94 | 74.01 | 82.19 | 91.41 | 102.83 | 114.18 | 126.03 | 137.5 | 149.5 | 161.37 | 173.94 | 186.36 | 198.42 | 211.99 | 225.79 | 239.26 | 251.06 | 262.1 | 272.66 | 283.93 | 294.06 | 302.35 | 311.94 | 322.61 | 324.13 | 326.52 | 328.44 | 331.11
$1,000 - $7,500 | 43.63 | 52.46 | 61.82 | 71.92 | 80.73 | 89.65 | 99.7 | 112.17 | 124.54 | 137.47 | 149.98 | 163.07 | 176.02 | 189.73 | 203.28 | 216.43 | 231.23 | 246.28 | 260.98 | 273.84 | 285.89 | 297.4 | 309.7 | 320.74 | 329.79 | 340.25 | 351.89 | 353.54 | 356.15 | 358.25 | 361.15
$7,500 + | 48.57 | 58.4 | 68.82 | 80.06 | 89.87 | 99.8 | 110.99 | 124.86 | 138.64 | 153.03 | 166.96 | 181.54 | 195.95 | 211.21 | 226.29 | 240.93 | 257.41 | 274.16 | 290.52 | 304.85 | 318.26 | 331.08 | 344.76 | 357.06 | 367.13 | 378.77 | 391.73 | 393.57 | 396.48 | 398.81 | 402.05
Reliability Response | 48.57 | 58.4 | 68.82 | 80.07 | 89.87 | 99.8 | 110.99 | 124.87 | 138.64 | 153.03 | 166.97 | 181.54 | 195.95 | 211.21 | 226.29 | 240.94 | 257.41 | 274.17 | 290.53 | 304.85 | 318.26 | 331.08 | 344.77 | 357.06 | 367.14 | 378.78 | 391.74 | 393.58 | 396.48 | 398.82 | 402.05
Reliability response in % of peak demand | 1.78% | 2.04% | 2.29% | 2.55% | 2.81% | 3.07% | 3.33% | 3.59% | 3.85% | 4.1% | 4.36% | 4.62% | 4.88% | 5.14% | 5.4% | 5.66% | 5.91% | 6.17% | 6.43% | 6.69% | 6.95% | 7.21% | 7.47% | 7.72% | 7.98% | 8.24% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
Tasmania
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 0.36 | 0.65 | 0.97 | 1.32 | 1.69 | 2.02 | 2.35 | 2.71 | 3.12 | 3.54 | 3.95 | 4.33 | 4.69 | 5.08 | 5.49 | 5.89 | 6.28 | 6.7 | 7.11 | 7.51 | 7.9 | 8.22 | 8.59 | 8.94 | 9.26 | 9.48 | 9.67 | 9.48 | 9.35 | 9.23 | 9.16
$500 - $1,000 | 5.95 | 10.77 | 15.97 | 21.8 | 27.87 | 33.34 | 38.89 | 44.75 | 51.48 | 58.53 | 65.32 | 71.51 | 77.45 | 84.02 | 90.78 | 97.42 | 103.81 | 110.78 | 117.45 | 124.08 | 130.5 | 135.9 | 141.91 | 147.8 | 153.02 | 156.64 | 159.76 | 156.66 | 154.58 | 152.59 | 151.38
$1,000 - $7,500 | 5.95 | 10.77 | 15.97 | 21.8 | 27.87 | 33.34 | 38.89 | 44.75 | 51.48 | 58.53 | 65.32 | 71.51 | 77.45 | 84.02 | 90.78 | 97.42 | 103.81 | 110.78 | 117.45 | 124.08 | 130.5 | 135.9 | 141.91 | 147.8 | 153.02 | 156.64 | 159.76 | 156.66 | 154.58 | 152.59 | 151.38
$7,500 + | 5.95 | 10.77 | 15.97 | 21.8 | 27.87 | 33.34 | 38.89 | 44.75 | 51.48 | 58.53 | 65.32 | 71.51 | 77.45 | 84.02 | 90.78 | 97.42 | 103.81 | 110.78 | 117.45 | 124.08 | 130.5 | 135.9 | 141.91 | 147.8 | 153.02 | 156.64 | 159.76 | 156.66 | 154.58 | 152.59 | 151.38
Reliability Response | 5.95 | 10.77 | 15.97 | 21.8 | 27.87 | 33.34 | 38.89 | 44.75 | 51.49 | 58.53 | 65.33 | 71.51 | 77.45 | 84.03 | 90.78 | 97.42 | 103.82 | 110.79 | 117.46 | 124.09 | 130.5 | 135.91 | 141.92 | 147.8 | 153.02 | 156.65 | 159.77 | 156.67 | 154.59 | 152.59 | 151.38
Reliability response in % of peak demand | 0.41% | 0.72% | 1.03% | 1.34% | 1.65% | 1.96% | 2.28% | 2.59% | 2.9% | 3.21% | 3.52% | 3.83% | 4.14% | 4.45% | 4.77% | 5.08% | 5.39% | 5.7% | 6.01% | 6.32% | 6.63% | 6.94% | 7.26% | 7.57% | 7.88% | 8.19% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 0.36 | 0.72 | 1.12 | 1.54 | 1.97 | 2.38 | 2.79 | 3.22 | 3.71 | 4.22 | 4.73 | 5.17 | 5.63 | 6.11 | 6.6 | 7.08 | 7.56 | 8.05 | 8.54 | 9.03 | 9.49 | 9.9 | 10.32 | 10.74 | 11.05 | 11.34 | 11.65 | 11.55 | 11.43 | 11.31 | 11.24
$500 - $1,000 | 5.95 | 11.95 | 18.54 | 25.52 | 32.55 | 39.29 | 46.1 | 53.28 | 61.4 | 69.73 | 78.14 | 85.49 | 92.99 | 100.91 | 109.04 | 116.98 | 124.94 | 133.05 | 141.2 | 149.22 | 156.81 | 163.59 | 170.62 | 177.45 | 182.56 | 187.48 | 192.49 | 190.82 | 188.97 | 186.91 | 185.81
$1,000 - $7,500 | 5.95 | 11.95 | 18.54 | 25.52 | 32.55 | 39.29 | 46.1 | 53.28 | 61.4 | 69.73 | 78.14 | 85.49 | 92.99 | 100.91 | 109.04 | 116.98 | 124.94 | 133.05 | 141.2 | 149.22 | 156.81 | 163.59 | 170.62 | 177.45 | 182.56 | 187.48 | 192.49 | 190.82 | 188.97 | 186.91 | 185.81
$7,500 + | 5.95 | 11.95 | 18.54 | 25.52 | 32.55 | 39.29 | 46.1 | 53.28 | 61.4 | 69.73 | 78.14 | 85.49 | 92.99 | 100.91 | 109.04 | 116.98 | 124.94 | 133.05 | 141.2 | 149.22 | 156.81 | 163.59 | 170.62 | 177.45 | 182.56 | 187.48 | 192.49 | 190.82 | 188.97 | 186.91 | 185.81
Reliability Response | 5.95 | 11.94 | 18.53 | 25.52 | 32.55 | 39.28 | 46.09 | 53.28 | 61.39 | 69.72 | 78.13 | 85.48 | 92.98 | 100.89 | 109.03 | 116.96 | 124.92 | 133.03 | 141.18 | 149.2 | 156.79 | 163.57 | 170.6 | 177.42 | 182.53 | 187.46 | 192.46 | 190.8 | 188.94 | 186.88 | 185.79
Reliability response in % of peak demand | 0.33% | 0.64% | 0.96% | 1.27% | 1.58% | 1.9% | 2.21% | 2.53% | 2.84% | 3.16% | 3.47% | 3.79% | 4.1% | 4.41% | 4.73% | 5.04% | 5.36% | 5.67% | 5.99% | 6.3% | 6.61% | 6.93% | 7.24% | 7.56% | 7.87% | 8.19% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
Victoria
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 63.18 | 70.47 | 79.1 | 89.12 | 99.34 | 110.15 | 120.84 | 131.61 | 143.32 | 155.3 | 167.81 | 178.89 | 189.14 | 199.48 | 210.6 | 221.24 | 232.33 | 243.45 | 253.38 | 263.1 | 272.61 | 281.22 | 288.95 | 295.15 | 299.66 | 304.69 | 311.22 | 310.74 | 309.75 | 309.04 | 309.79
$7,500 + | 63.18 | 70.47 | 79.1 | 89.12 | 99.34 | 110.15 | 120.84 | 131.61 | 143.32 | 155.3 | 167.81 | 178.89 | 189.14 | 199.48 | 210.6 | 221.24 | 232.33 | 243.45 | 253.38 | 263.1 | 272.61 | 281.22 | 288.95 | 295.15 | 299.66 | 304.69 | 311.22 | 310.74 | 309.75 | 309.04 | 309.79
Reliability Response | 257.18 | 286.85 | 321.97 | 362.79 | 404.36 | 448.37 | 491.9 | 535.75 | 583.42 | 632.18 | 683.09 | 728.21 | 769.93 | 812.01 | 857.28 | 900.58 | 945.74 | 991.02 | 1031.42 | 1070.97 | 1109.68 | 1144.74 | 1176.22 | 1201.44 | 1219.79 | 1240.26 | 1266.85 | 1264.92 | 1260.88 | 1257.99 | 1261.03
Reliability response in % of peak demand | 2.48% | 2.71% | 2.94% | 3.18% | 3.41% | 3.64% | 3.87% | 4.1% | 4.33% | 4.56% | 4.8% | 5.03% | 5.26% | 5.49% | 5.72% | 5.95% | 6.19% | 6.42% | 6.65% | 6.88% | 7.11% | 7.34% | 7.57% | 7.81% | 8.04% | 8.27% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 63.18 | 70.93 | 80.58 | 91.28 | 103.8 | 117.15 | 130.2 | 143.2 | 156.88 | 171.02 | 184.43 | 197.13 | 210.07 | 222.39 | 235.6 | 247.58 | 258.73 | 271.69 | 284.23 | 295.99 | 304.77 | 313.07 | 320.03 | 326.68 | 331.76 | 337.71 | 343 | 339.12 | 335.12 | 333.2 | 331.92
$7,500 + | 63.18 | 70.93 | 80.58 | 91.28 | 103.8 | 117.15 | 130.2 | 143.2 | 156.88 | 171.02 | 184.43 | 197.13 | 210.07 | 222.39 | 235.6 | 247.58 | 258.73 | 271.69 | 284.23 | 295.99 | 304.77 | 313.07 | 320.03 | 326.68 | 331.76 | 337.71 | 343 | 339.12 | 335.12 | 333.2 | 331.92
Reliability Response | 212.18 | 238.19 | 270.62 | 306.54 | 348.58 | 393.42 | 437.24 | 480.91 | 526.85 | 574.34 | 619.37 | 662.03 | 705.47 | 746.86 | 791.21 | 831.46 | 868.9 | 912.41 | 954.55 | 994.03 | 1023.5 | 1051.4 | 1074.76 | 1097.09 | 1114.17 | 1134.14 | 1151.89 | 1138.87 | 1125.43 | 1119 | 1114.71
Reliability response in % of peak demand | 2.58% | 2.8% | 3.03% | 3.26% | 3.49% | 3.72% | 3.94% | 4.17% | 4.4% | 4.63% | 4.85% | 5.08% | 5.31% | 5.54% | 5.77% | 5.99% | 6.22% | 6.45% | 6.68% | 6.91% | 7.13% | 7.36% | 7.59% | 7.82% | 8.04% | 8.27% | 8.5% | 8.5% | 8.5% | 8.5% | 8.5%
Progressive Change
New South Wales
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 93.74 | 95.47 | 97.26 | 99.67 | 138.93 | 190.77 | 236.72 | 256.31 | 275.88 | 295.44 | 297.87 | 300.52 | 302.65 | 305.36 | 307.73 | 310.75 | 313.13 | 316.32 | 316.85 | 317.88 | 319.67 | 319.09 | 319.88 | 320.5 | 320.06 | 321.14 | 322.34 | 324.64 | 329.95 | 333.56 | 337.9
$7,500 + | 94.74 | 96.49 | 98.3 | 100.74 | 140.42 | 192.81 | 239.25 | 259.04 | 278.82 | 298.59 | 301.05 | 303.73 | 305.88 | 308.62 | 311.01 | 314.06 | 316.47 | 319.7 | 320.23 | 321.27 | 323.08 | 322.5 | 323.29 | 323.91 | 323.47 | 324.56 | 325.78 | 328.1 | 333.47 | 337.12 | 341.5
Reliability Response | 336.74 | 342.94 | 349.4 | 358.05 | 499.09 | 685.31 | 850.38 | 920.72 | 991.02 | 1061.28 | 1070.04 | 1079.54 | 1087.21 | 1096.93 | 1105.44 | 1116.29 | 1124.85 | 1136.31 | 1138.21 | 1141.89 | 1148.33 | 1146.26 | 1149.08 | 1151.3 | 1149.72 | 1153.61 | 1157.93 | 1166.18 | 1185.25 | 1198.23 | 1213.82
Reliability response in % of peak demand* | 2.44% | 2.44% | 2.44% | 2.44% | 3.35% | 4.55% | 5.96% | 6.39% | 6.82% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26% | 7.26%
* The estimated percentage is in most years set by the NSW PDRS, adjusted to account for the target being only for the state of NSW (i.e. excluding ACT) and removing contributions likely from energy efficiency and coordinated EV and battery storage load, which are modelled separately.
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 93.74 | 95.27 | 97.61 | 99.64 | 101.28 | 97.74 | 96.56 | 97.43 | 98.15 | 98.68 | 99.45 | 100.26 | 101.06 | 101.73 | 102.64 | 103.32 | 104.21 | 104.75 | 105.26 | 105.58 | 105.27 | 104.91 | 104.99 | 105.36 | 105.6 | 105.65 | 106 | 106.6 | 108.2 | 109.53 | 110.75
$7,500 + | 94.74 | 96.28 | 98.65 | 100.71 | 102.36 | 98.78 | 97.59 | 98.47 | 99.19 | 99.73 | 100.51 | 101.33 | 102.14 | 102.81 | 103.73 | 104.42 | 105.32 | 105.86 | 106.39 | 106.71 | 106.39 | 106.03 | 106.11 | 106.48 | 106.73 | 106.78 | 107.14 | 107.73 | 109.36 | 110.7 | 111.93
Reliability Response | 336.75 | 342.23 | 350.63 | 357.95 | 363.83 | 351.1 | 346.89 | 350 | 352.57 | 354.48 | 357.27 | 360.16 | 363.05 | 365.45 | 368.7 | 371.16 | 374.35 | 376.28 | 378.15 | 379.28 | 378.17 | 376.89 | 377.15 | 378.47 | 379.35 | 379.53 | 380.8 | 382.93 | 388.71 | 393.46 | 397.84
Reliability response in % of peak demand | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61%
Queensland
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 22.02 | 22.29 | 22.45 | 22.85 | 23.15 | 23.52 | 22.17 | 22.64 | 22.98 | 23.31 | 23.73 | 24.19 | 24.69 | 25.24 | 25.59 | 25.96 | 26.51 | 26.82 | 27.05 | 27.34 | 27.59 | 27.76 | 27.99 | 28.31 | 28.52 | 29.25 | 29.82 | 30.44 | 30.56 | 30.97 | 31.29
$500 - $1,000 | 54.15 | 54.82 | 55.21 | 56.2 | 56.94 | 57.85 | 54.52 | 55.67 | 56.51 | 57.32 | 58.36 | 59.49 | 60.71 | 62.07 | 62.92 | 63.84 | 65.19 | 65.96 | 66.51 | 67.22 | 67.85 | 68.28 | 68.83 | 69.63 | 70.14 | 71.92 | 73.33 | 74.85 | 75.16 | 76.16 | 76.95
$1,000 - $7,500 | 151.86 | 153.75 | 154.84 | 157.61 | 159.68 | 162.24 | 152.9 | 156.12 | 158.48 | 160.76 | 163.66 | 166.84 | 170.26 | 174.06 | 176.45 | 179.03 | 182.82 | 184.98 | 186.52 | 188.52 | 190.28 | 191.48 | 193.02 | 195.26 | 196.69 | 201.69 | 205.65 | 209.91 | 210.79 | 213.57 | 215.81
$7,500 + | 189.12 | 191.47 | 192.83 | 196.29 | 198.86 | 202.04 | 190.41 | 194.43 | 197.36 | 200.2 | 203.82 | 207.78 | 212.03 | 216.77 | 219.74 | 222.96 | 227.68 | 230.37 | 232.28 | 234.78 | 236.96 | 238.46 | 240.38 | 243.17 | 244.96 | 251.17 | 256.1 | 261.41 | 262.51 | 265.97 | 268.76
Reliability Response | 261.52 | 264.77 | 266.65 | 271.43 | 274.99 | 279.39 | 263.31 | 268.86 | 272.92 | 276.84 | 281.85 | 287.32 | 293.21 | 299.76 | 303.87 | 308.31 | 314.85 | 318.56 | 321.21 | 324.66 | 327.68 | 329.75 | 332.41 | 336.27 | 338.73 | 347.33 | 354.15 | 361.49 | 363.01 | 367.8 | 371.64
Reliability response in % of peak demand | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55% | 2.55%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 22.02 | 22.18 | 22.31 | 22.61 | 22.96 | 21.94 | 21.76 | 22.24 | 22.57 | 22.96 | 23.4 | 23.9 | 24.47 | 25.08 | 25.51 | 25.88 | 26.43 | 26.7 | 26.98 | 27.31 | 27.54 | 27.64 | 27.88 | 28.26 | 28.53 | 29.51 | 30.18 | 30.79 | 31.05 | 31.41 | 31.75
$500 - $1,000 | 54.15 | 54.54 | 54.87 | 55.61 | 56.45 | 53.96 | 53.51 | 54.68 | 55.51 | 56.47 | 57.54 | 58.76 | 60.17 | 61.68 | 62.73 | 63.64 | 64.98 | 65.65 | 66.34 | 67.15 | 67.74 | 67.98 | 68.56 | 69.5 | 70.16 | 72.57 | 74.22 | 75.73 | 76.35 | 77.25 | 78.09
$1,000 - $7,500 | 151.86 | 152.96 | 153.88 | 155.95 | 158.31 | 151.33 | 150.06 | 153.36 | 155.68 | 158.36 | 161.37 | 164.79 | 168.74 | 172.97 | 175.93 | 178.48 | 182.25 | 184.12 | 186.05 | 188.31 | 189.96 | 190.64 | 192.27 | 194.91 | 196.77 | 203.53 | 208.15 | 212.37 | 214.12 | 216.64 | 218.99
$7,500 + | 189.12 | 190.49 | 191.64 | 194.22 | 197.16 | 188.46 | 186.88 | 190.99 | 193.87 | 197.21 | 200.96 | 205.23 | 210.14 | 215.41 | 219.1 | 222.27 | 226.96 | 229.3 | 231.7 | 234.51 | 236.57 | 237.42 | 239.45 | 242.73 | 245.05 | 253.47 | 259.22 | 264.47 | 266.66 | 269.79 | 272.72
Reliability Response | 189.12 | 190.49 | 191.64 | 194.22 | 197.16 | 188.46 | 186.88 | 190.98 | 193.87 | 197.21 | 200.96 | 205.22 | 210.14 | 215.41 | 219.09 | 222.27 | 226.96 | 229.3 | 231.7 | 234.51 | 236.56 | 237.41 | 239.45 | 242.72 | 245.04 | 253.47 | 259.22 | 264.47 | 266.66 | 269.79 | 272.71
Reliability response in % of peak demand | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24% | 2.24%
South Australia
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 25.57 | 25.94 | 26.47 | 27.14 | 27.82 | 28.12 | 28.5 | 28.78 | 29.12 | 29.42 | 29.84 | 30.19 | 30.57 | 30.9 | 31.18 | 31.44 | 31.71 | 32.03 | 32.29 | 32.53 | 32.67 | 32.74 | 32.66 | 32.54 | 32.34 | 32.13 | 32.16 | 32.29 | 32.46 | 32.64 | 32.69
$500 - $1,000 | 40 | 40.58 | 41.41 | 42.46 | 43.52 | 43.99 | 44.58 | 45.01 | 45.56 | 46.02 | 46.68 | 47.23 | 47.82 | 48.33 | 48.77 | 49.18 | 49.61 | 50.11 | 50.51 | 50.89 | 51.11 | 51.22 | 51.09 | 50.9 | 50.59 | 50.26 | 50.31 | 50.51 | 50.77 | 51.06 | 51.14
$1,000 - $7,500 | 43.63 | 44.26 | 45.17 | 46.31 | 47.47 | 47.99 | 48.63 | 49.1 | 49.69 | 50.2 | 50.92 | 51.52 | 52.16 | 52.72 | 53.2 | 53.65 | 54.11 | 54.66 | 55.09 | 55.51 | 55.75 | 55.87 | 55.73 | 55.52 | 55.19 | 54.82 | 54.87 | 55.1 | 55.38 | 55.69 | 55.78
$7,500 + | 48.57 | 49.28 | 50.28 | 51.55 | 52.85 | 53.42 | 54.13 | 54.66 | 55.32 | 55.88 | 56.69 | 57.35 | 58.07 | 58.69 | 59.22 | 59.72 | 60.24 | 60.84 | 61.33 | 61.79 | 62.07 | 62.19 | 62.04 | 61.81 | 61.43 | 61.03 | 61.08 | 61.34 | 61.65 | 62 | 62.1
Reliability Response | 48.57 | 49.28 | 50.28 | 51.56 | 52.85 | 53.42 | 54.14 | 54.66 | 55.32 | 55.88 | 56.69 | 57.36 | 58.07 | 58.69 | 59.22 | 59.72 | 60.24 | 60.85 | 61.33 | 61.79 | 62.07 | 62.2 | 62.04 | 61.81 | 61.44 | 61.03 | 61.09 | 61.34 | 61.65 | 62 | 62.1
Reliability response in % of peak demand | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48% | 1.48%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 25.57 | 26.04 | 26.71 | 27.55 | 28.15 | 28.6 | 28.94 | 29.31 | 29.67 | 30.01 | 30.37 | 30.77 | 31.17 | 31.54 | 31.9 | 32.12 | 32.42 | 32.75 | 33.05 | 33.28 | 33.37 | 33.32 | 33.35 | 33.22 | 32.88 | 32.77 | 32.75 | 32.77 | 33.04 | 33.1 | 33.11
$500 - $1,000 | 40 | 40.73 | 41.78 | 43.09 | 44.03 | 44.74 | 45.28 | 45.85 | 46.41 | 46.95 | 47.52 | 48.13 | 48.76 | 49.33 | 49.9 | 50.24 | 50.72 | 51.23 | 51.7 | 52.07 | 52.2 | 52.12 | 52.17 | 51.96 | 51.44 | 51.27 | 51.23 | 51.26 | 51.69 | 51.78 | 51.8
$1,000 - $7,500 | 43.63 | 44.43 | 45.57 | 47 | 48.03 | 48.8 | 49.39 | 50.01 | 50.62 | 51.21 | 51.83 | 52.5 | 53.19 | 53.81 | 54.43 | 54.8 | 55.32 | 55.88 | 56.39 | 56.79 | 56.94 | 56.85 | 56.91 | 56.68 | 56.11 | 55.92 | 55.88 | 55.91 | 56.38 | 56.48 | 56.5
$7,500 + | 48.57 | 49.46 | 50.73 | 52.33 | 53.47 | 54.33 | 54.98 | 55.67 | 56.35 | 57.01 | 57.7 | 58.44 | 59.21 | 59.9 | 60.59 | 61.01 | 61.59 | 62.21 | 62.78 | 63.22 | 63.39 | 63.29 | 63.35 | 63.1 | 62.46 | 62.25 | 62.2 | 62.24 | 62.76 | 62.87 | 62.89
Reliability Response | 48.57 | 49.46 | 50.73 | 52.33 | 53.47 | 54.33 | 54.98 | 55.67 | 56.35 | 57.01 | 57.7 | 58.45 | 59.21 | 59.9 | 60.59 | 61.01 | 61.59 | 62.21 | 62.78 | 63.22 | 63.39 | 63.29 | 63.35 | 63.1 | 62.46 | 62.25 | 62.2 | 62.25 | 62.76 | 62.87 | 62.9
Reliability response in % of peak demand | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83% | 1.83%
Tasmania
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 0.36 | 0.36 | 0.32 | 0.27 | 0.28 | 0.28 | 0.29 | 0.3 | 0.3 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.32 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.3 | 0.3 | 0.3 | 0.3
$500 - $1,000 | 5.95 | 6 | 5.24 | 4.54 | 4.57 | 4.66 | 4.79 | 4.91 | 5.01 | 5.05 | 5.06 | 5.09 | 5.06 | 5.08 | 5.09 | 5.11 | 5.12 | 5.16 | 5.17 | 5.2 | 5.21 | 5.19 | 5.19 | 5.18 | 5.19 | 5.19 | 5.14 | 5.03 | 4.96 | 4.94 | 4.94
$1,000 - $7,500 | 5.95 | 6 | 5.24 | 4.54 | 4.57 | 4.66 | 4.79 | 4.91 | 5.01 | 5.05 | 5.06 | 5.09 | 5.06 | 5.08 | 5.09 | 5.11 | 5.12 | 5.16 | 5.17 | 5.2 | 5.21 | 5.19 | 5.19 | 5.18 | 5.19 | 5.19 | 5.14 | 5.03 | 4.96 | 4.94 | 4.94
$7,500 + | 5.95 | 6 | 5.24 | 4.54 | 4.57 | 4.66 | 4.79 | 4.91 | 5.01 | 5.05 | 5.06 | 5.09 | 5.06 | 5.08 | 5.09 | 5.11 | 5.12 | 5.16 | 5.17 | 5.2 | 5.21 | 5.19 | 5.19 | 5.18 | 5.19 | 5.19 | 5.14 | 5.03 | 4.96 | 4.94 | 4.94
Reliability Response | 5.95 | 6 | 5.24 | 4.54 | 4.57 | 4.66 | 4.79 | 4.91 | 5.01 | 5.05 | 5.06 | 5.09 | 5.06 | 5.08 | 5.09 | 5.11 | 5.12 | 5.16 | 5.18 | 5.2 | 5.21 | 5.19 | 5.19 | 5.18 | 5.19 | 5.2 | 5.14 | 5.03 | 4.96 | 4.94 | 4.94
Reliability response in % of peak demand | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42% | 0.42%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 0.36 | 0.34 | 0.3 | 0.29 | 0.3 | 0.3 | 0.31 | 0.31 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.33 | 0.33 | 0.33 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.31 | 0.31 | 0.31 | 0.31
$500 - $1,000 | 5.95 | 5.57 | 5.02 | 4.85 | 4.89 | 4.96 | 5.07 | 5.16 | 5.25 | 5.27 | 5.32 | 5.31 | 5.31 | 5.32 | 5.33 | 5.34 | 5.36 | 5.37 | 5.39 | 5.39 | 5.39 | 5.37 | 5.34 | 5.32 | 5.31 | 5.3 | 5.26 | 5.17 | 5.11 | 5.08 | 5.06
$1,000 - $7,500 | 5.95 | 5.57 | 5.02 | 4.85 | 4.89 | 4.96 | 5.07 | 5.16 | 5.25 | 5.27 | 5.32 | 5.31 | 5.31 | 5.32 | 5.33 | 5.34 | 5.36 | 5.37 | 5.39 | 5.39 | 5.39 | 5.37 | 5.34 | 5.32 | 5.31 | 5.3 | 5.26 | 5.17 | 5.11 | 5.08 | 5.06
$7,500 + | 5.95 | 5.57 | 5.02 | 4.85 | 4.89 | 4.96 | 5.07 | 5.16 | 5.25 | 5.27 | 5.32 | 5.31 | 5.31 | 5.32 | 5.33 | 5.34 | 5.36 | 5.37 | 5.39 | 5.39 | 5.39 | 5.37 | 5.34 | 5.32 | 5.31 | 5.3 | 5.26 | 5.17 | 5.11 | 5.08 | 5.06
Reliability Response | 5.95 | 5.57 | 5.02 | 4.85 | 4.89 | 4.96 | 5.07 | 5.16 | 5.25 | 5.27 | 5.32 | 5.31 | 5.31 | 5.32 | 5.33 | 5.34 | 5.36 | 5.37 | 5.39 | 5.39 | 5.39 | 5.37 | 5.34 | 5.32 | 5.31 | 5.3 | 5.26 | 5.17 | 5.11 | 5.08 | 5.06
Reliability response in % of peak demand | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33% | 0.33%
Victoria
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 63.18 | 63.69 | 64.52 | 62.47 | 63.61 | 65.1 | 66.83 | 67.92 | 69.36 | 70.37 | 71.53 | 72.23 | 72.84 | 73.4 | 74.01 | 74.67 | 75.45 | 76.26 | 76.73 | 77.35 | 77.71 | 77.88 | 78.28 | 78.38 | 78.16 | 77.71 | 77.57 | 77.8 | 78.26 | 78.89 | 79.1
$7,500 + | 63.18 | 63.69 | 64.52 | 62.47 | 63.61 | 65.1 | 66.83 | 67.92 | 69.36 | 70.37 | 71.53 | 72.23 | 72.84 | 73.4 | 74.01 | 74.67 | 75.45 | 76.26 | 76.73 | 77.35 | 77.71 | 77.88 | 78.28 | 78.38 | 78.16 | 77.71 | 77.57 | 77.8 | 78.26 | 78.89 | 79.1
Reliability Response | 257.18 | 259.24 | 262.65 | 254.27 | 258.93 | 265 | 272.05 | 276.46 | 282.34 | 286.44 | 291.15 | 294 | 296.52 | 298.78 | 301.25 | 303.94 | 307.11 | 310.41 | 312.34 | 314.87 | 316.32 | 317.01 | 318.65 | 319.05 | 318.14 | 316.32 | 315.74 | 316.68 | 318.56 | 321.12 | 321.98
Reliability response in % of peak demand | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53% | 2.53%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 63.18 | 64.33 | 63.55 | 63.96 | 65.87 | 68.24 | 70.33 | 72.42 | 74.39 | 75.93 | 77.18 | 78.19 | 79.36 | 80.57 | 81.91 | 82.97 | 83.78 | 84.93 | 86.33 | 87.3 | 87.9 | 88.23 | 88.83 | 89.53 | 90.14 | 90.65 | 90.91 | 90.48 | 91.35 | 91.87 | 92.08
$7,500 + | 63.18 | 64.33 | 63.55 | 63.96 | 65.87 | 68.24 | 70.33 | 72.42 | 74.39 | 75.93 | 77.18 | 78.19 | 79.36 | 80.57 | 81.91 | 82.97 | 83.78 | 84.93 | 86.33 | 87.3 | 87.9 | 88.23 | 88.83 | 89.53 | 90.14 | 90.65 | 90.91 | 90.48 | 91.35 | 91.87 | 92.08
Reliability Response | 212.18 | 216.05 | 213.42 | 214.8 | 221.21 | 229.16 | 236.18 | 243.21 | 249.82 | 255.01 | 259.2 | 262.57 | 266.53 | 270.59 | 275.07 | 278.63 | 281.36 | 285.21 | 289.92 | 293.17 | 295.21 | 296.31 | 298.31 | 300.67 | 302.71 | 304.44 | 305.3 | 303.85 | 306.79 | 308.53 | 309.25
Reliability response in % of peak demand | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61% | 2.61%
Step Change
New South Wales
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 93.74 | 97.89 | 102.41 | 107.81 | 139.49 | 191.54 | 238.02 | 269.9 | 301.77 | 333.63 | 337.34 | 341.2 | 344.8 | 349.69 | 354.2 | 357.1 | 359.18 | 362.75 | 364.7 | 367.81 | 370.35 | 369.59 | 370.2 | 369.71 | 369.75 | 371.8 | 372.61 | 375.69 | 382.35 | 387.88 | 393.98
$7,500 + | 94.74 | 98.93 | 103.5 | 108.96 | 140.98 | 193.58 | 240.56 | 272.78 | 304.99 | 337.19 | 340.94 | 344.84 | 348.48 | 353.42 | 357.98 | 360.9 | 363.02 | 366.62 | 368.59 | 371.73 | 374.3 | 373.53 | 374.15 | 373.65 | 373.7 | 375.77 | 376.58 | 379.7 | 386.43 | 392.02 | 398.18
Reliability Response | 336.74 | 351.64 | 367.88 | 387.29 | 501.09 | 688.08 | 855.03 | 969.56 | 1084.06 | 1198.52 | 1211.82 | 1225.69 | 1238.65 | 1256.21 | 1272.4 | 1282.8 | 1290.3 | 1303.1 | 1310.11 | 1321.3 | 1330.43 | 1327.68 | 1329.87 | 1328.1 | 1328.27 | 1335.64 | 1338.53 | 1349.59 | 1373.53 | 1393.41 | 1415.29
Reliability response in % of peak demand* | 2.44% | 2.51% | 2.58% | 2.65% | 3.35% | 4.49% | 5.45% | 6.07% | 6.68% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29% | 7.29%
* The estimated percentage is in most years set by the NSW PDRS, adjusted to account for the target being only for the state of NSW (i.e. excluding ACT) and removing contributions likely from energy efficiency and coordinated EV and battery storage load, which are modelled separately.
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 93.74 | 97.44 | 102.14 | 107.37 | 112.7 | 118.09 | 123.23 | 128.14 | 132.64 | 136.73 | 140.79 | 145.07 | 150.01 | 154.63 | 158.99 | 162.58 | 166.47 | 171.04 | 175.92 | 180.11 | 183.13 | 185.71 | 188.84 | 192.47 | 196.12 | 199.19 | 202.74 | 204.3 | 207.31 | 209.93 | 212.55
$7,500 + | 94.74 | 98.48 | 103.23 | 108.51 | 113.9 | 119.35 | 124.54 | 129.51 | 134.05 | 138.18 | 142.3 | 146.61 | 151.61 | 156.28 | 160.69 | 164.31 | 168.24 | 172.87 | 177.8 | 182.03 | 185.08 | 187.69 | 190.86 | 194.53 | 198.21 | 201.32 | 204.9 | 206.48 | 209.52 | 212.17 | 214.81
Reliability Response | 336.74 | 350.02 | 366.92 | 385.69 | 404.85 | 424.2 | 442.68 | 460.33 | 476.48 | 491.16 | 505.77 | 521.13 | 538.88 | 555.48 | 571.15 | 584.03 | 598 | 614.44 | 631.96 | 647.01 | 657.86 | 667.13 | 678.38 | 691.42 | 704.53 | 715.57 | 728.3 | 733.9 | 744.71 | 754.14 | 763.53
Reliability response in % of peak demand | 2.61% | 2.67% | 2.73% | 2.8% | 2.86% | 2.92% | 2.99% | 3.05% | 3.11% | 3.18% | 3.24% | 3.3% | 3.36% | 3.43% | 3.49% | 3.55% | 3.62% | 3.68% | 3.74% | 3.81% | 3.87% | 3.93% | 4% | 4.06% | 4.12% | 4.19% | 4.25% | 4.25% | 4.25% | 4.25% | 4.25%
Queensland
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 22.02 | 23.17 | 24.26 | 25.51 | 26.62 | 27.94 | 29.38 | 30.81 | 32.18 | 33.57 | 35 | 36.35 | 38.01 | 39.69 | 41.4 | 42.83 | 44.26 | 45.89 | 47.45 | 48.95 | 50.35 | 51.49 | 52.77 | 54.22 | 55.57 | 56.88 | 58.1 | 58.7 | 59.78 | 61.12 | 62.24
$500 - $1,000 | 54.15 | 56.98 | 59.67 | 62.74 | 65.46 | 68.7 | 72.25 | 75.76 | 79.12 | 82.55 | 86.06 | 89.39 | 93.46 | 97.61 | 101.82 | 105.32 | 108.84 | 112.84 | 116.69 | 120.38 | 123.82 | 126.63 | 129.76 | 133.33 | 136.66 | 139.87 | 142.86 | 144.35 | 147.01 | 150.31 | 153.07
$1,000 - $7,500 | 151.86 | 159.81 | 167.33 | 175.94 | 183.58 | 192.67 | 202.63 | 212.46 | 221.9 | 231.51 | 241.36 | 250.68 | 262.11 | 273.74 | 285.55 | 295.38 | 305.24 | 316.45 | 327.24 | 337.59 | 347.24 | 355.11 | 363.91 | 373.92 | 383.26 | 392.27 | 400.65 | 404.83 | 412.27 | 421.53 | 429.27
$7,500 + | 189.12 | 199.02 | 208.39 | 219.11 | 228.63 | 239.94 | 252.34 | 264.59 | 276.34 | 288.32 | 300.57 | 312.18 | 326.43 | 340.91 | 355.61 | 367.85 | 380.14 | 394.1 | 407.53 | 420.42 | 432.43 | 442.24 | 453.2 | 465.66 | 477.29 | 488.52 | 498.95 | 504.15 | 513.43 | 524.95 | 534.59
Reliability Response | 261.52 | 275.21 | 288.16 | 302.99 | 316.15 | 331.79 | 348.94 | 365.88 | 382.13 | 398.69 | 415.64 | 431.69 | 451.39 | 471.41 | 491.74 | 508.67 | 525.66 | 544.97 | 563.54 | 581.36 | 597.97 | 611.54 | 626.69 | 643.93 | 660.01 | 675.53 | 689.96 | 697.15 | 709.98 | 725.91 | 739.24
Reliability response in % of peak demand | 2.52% | 2.59% | 2.65% | 2.72% | 2.79% | 2.85% | 2.92% | 2.99% | 3.05% | 3.12% | 3.19% | 3.25% | 3.32% | 3.39% | 3.45% | 3.52% | 3.59% | 3.65% | 3.72% | 3.78% | 3.85% | 3.92% | 3.98% | 4.05% | 4.12% | 4.18% | 4.25% | 4.25% | 4.25% | 4.25% | 4.25%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 22.02 | 23.39 | 24.74 | 26.2 | 27.63 | 29.27 | 31.07 | 32.85 | 34.58 | 36.29 | 37.96 | 39.62 | 41.85 | 43.94 | 46.09 | 47.7 | 49.44 | 51.5 | 53.62 | 55.55 | 57.15 | 58.57 | 60.2 | 62.16 | 63.96 | 65.65 | 67.15 | 67.67 | 69.13 | 70.59 | 71.95
$500 - $1,000 | 54.15 | 57.53 | 60.85 | 64.43 | 67.95 | 71.99 | 76.41 | 80.79 | 85.04 | 89.23 | 93.35 | 97.42 | 102.9 | 108.06 | 113.33 | 117.29 | 121.59 | 126.65 | 131.87 | 136.6 | 140.54 | 144.03 | 148.04 | 152.87 | 157.29 | 161.44 | 165.13 | 166.4 | 170 | 173.59 | 176.93
$1,000 - $7,500 | 151.86 | 161.33 | 170.64 | 180.68 | 190.57 | 201.89 | 214.28 | 226.57 | 238.48 | 250.25 | 261.8 | 273.22 | 288.59 | 303.05 | 317.83 | 328.93 | 340.99 | 355.19 | 369.81 | 383.09 | 394.13 | 403.92 | 415.17 | 428.7 | 441.12 | 452.76 | 463.1 | 466.66 | 476.75 | 486.81 | 496.18
$7,500 + | 189.12 | 200.91 | 212.5 | 225.01 | 237.33 | 251.42 | 266.86 | 282.16 | 296.99 | 311.65 | 326.04 | 340.25 | 359.4 | 377.4 | 395.81 | 409.64 | 424.66 | 442.33 | 460.55 | 477.08 | 490.83 | 503.02 | 517.04 | 533.88 | 549.35 | 563.85 | 576.73 | 581.16 | 593.72 | 606.25 | 617.93
Reliability Response | 189.12 | 200.92 | 212.51 | 225.01 | 237.34 | 251.43 | 266.86 | 282.16 | 296.99 | 311.66 | 326.04 | 340.26 | 359.4 | 377.41 | 395.82 | 409.65 | 424.67 | 442.34 | 460.56 | 477.09 | 490.84 | 503.03 | 517.05 | 533.9 | 549.36 | 563.86 | 576.74 | 581.17 | 593.73 | 606.26 | 617.94
Reliability response in % of peak demand | 2.21% | 2.29% | 2.37% | 2.45% | 2.52% | 2.6% | 2.68% | 2.76% | 2.84% | 2.92% | 3% | 3.07% | 3.15% | 3.23% | 3.31% | 3.39% | 3.47% | 3.54% | 3.62% | 3.7% | 3.78% | 3.86% | 3.94% | 4.01% | 4.09% | 4.17% | 4.25% | 4.25% | 4.25% | 4.25% | 4.25%
South Australia
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 25.57 | 27.83 | 30.34 | 33.09 | 36.08 | 38.87 | 41.89 | 45.07 | 48.18 | 51.29 | 54.66 | 58.26 | 62.13 | 66.23 | 70.06 | 73.77 | 77.17 | 80.76 | 84.3 | 87.97 | 91.24 | 94.46 | 97.15 | 99.79 | 102.57 | 105.21 | 108.11 | 108.93 | 109.72 | 110.63 | 111.46
$500 - $1,000 | 40 | 43.54 | 47.46 | 51.77 | 56.44 | 60.8 | 65.52 | 70.51 | 75.37 | 80.23 | 85.5 | 91.14 | 97.19 | 103.61 | 109.6 | 115.4 | 120.73 | 126.33 | 131.87 | 137.61 | 142.73 | 147.76 | 151.98 | 156.11 | 160.46 | 164.58 | 169.12 | 170.4 | 171.64 | 173.06 | 174.36
$1,000 - $7,500 | 43.63 | 47.49 | 51.77 | 56.47 | 61.56 | 66.32 | 71.47 | 76.91 | 82.21 | 87.51 | 93.26 | 99.41 | 106.01 | 113.01 | 119.54 | 125.87 | 131.68 | 137.79 | 143.83 | 150.1 | 155.68 | 161.17 | 165.77 | 170.27 | 175.02 | 179.52 | 184.47 | 185.86 | 187.21 | 188.77 | 190.19
$7,500 + | 48.57 | 52.87 | 57.63 | 62.86 | 68.54 | 73.82 | 79.56 | 85.61 | 91.51 | 97.42 | 103.82 | 110.66 | 118.01 | 125.81 | 133.08 | 140.12 | 146.59 | 153.4 | 160.12 | 167.09 | 173.31 | 179.42 | 184.54 | 189.55 | 194.84 | 199.85 | 205.35 | 206.91 | 208.41 | 210.14 | 211.72
Reliability Response | 48.57 | 52.87 | 57.63 | 62.86 | 68.54 | 73.82 | 79.56 | 85.61 | 91.52 | 97.42 | 103.82 | 110.66 | 118.01 | 125.81 | 133.08 | 140.12 | 146.59 | 153.4 | 160.12 | 167.09 | 173.31 | 179.42 | 184.54 | 189.55 | 194.84 | 199.85 | 205.35 | 206.91 | 208.41 | 210.14 | 211.72
Reliability response in % of peak demand | 1.46% | 1.57% | 1.68% | 1.79% | 1.89% | 2% | 2.11% | 2.21% | 2.32% | 2.43% | 2.54% | 2.64% | 2.75% | 2.86% | 2.96% | 3.07% | 3.18% | 3.29% | 3.39% | 3.5% | 3.61% | 3.71% | 3.82% | 3.93% | 4.04% | 4.14% | 4.25% | 4.25% | 4.25% | 4.25% | 4.25%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 25.57 | 27.33 | 29.45 | 31.9 | 34.26 | 36.67 | 39.13 | 41.8 | 44.26 | 46.76 | 49.35 | 52.51 | 55.84 | 59.17 | 62.1 | 64.86 | 67.61 | 70.62 | 73.51 | 76.27 | 78.68 | 80.97 | 83.39 | 85.58 | 87.41 | 89.43 | 91.62 | 91.8 | 92.43 | 92.64 | 93.25
$500 - $1,000 | 40 | 42.75 | 46.06 | 49.89 | 53.59 | 57.37 | 61.22 | 65.39 | 69.24 | 73.14 | 77.2 | 82.14 | 87.36 | 92.56 | 97.14 | 101.47 | 105.76 | 110.48 | 114.99 | 119.31 | 123.09 | 126.67 | 130.45 | 133.88 | 136.73 | 139.9 | 143.32 | 143.6 | 144.59 | 144.92 | 145.88
$1,000 - $7,500 | 43.63 | 46.63 | 50.24 | 54.42 | 58.46 | 62.57 | 66.77 | 71.33 | 75.52 | 79.78 | 84.2 | 89.6 | 95.28 | 100.96 | 105.96 | 110.68 | 115.36 | 120.5 | 125.42 | 130.14 | 134.26 | 138.16 | 142.29 | 146.03 | 149.14 | 152.6 | 156.32 | 156.64 | 157.71 | 158.07 | 159.11
$7,500 + | 48.57 | 51.91 | 55.93 | 60.58 | 65.07 | 69.66 | 74.33 | 79.4 | 84.07 | 88.81 | 93.74 | 99.74 | 106.07 | 112.39 | 117.95 | 123.21 | 128.42 | 134.14 | 139.62 | 144.87 | 149.46 | 153.8 | 158.4 | 162.57 | 166.03 | 169.87 | 174.02 | 174.37 | 175.56 | 175.97 | 177.13
Reliability Response | 48.57 | 51.91 | 55.93 | 60.58 | 65.07 | 69.66 | 74.33 | 79.4 | 84.07 | 88.81 | 93.74 | 99.74 | 106.07 | 112.39 | 117.95 | 123.21 | 128.42 | 134.15 | 139.62 | 144.87 | 149.46 | 153.8 | 158.41 | 162.57 | 166.03 | 169.87 | 174.02 | 174.37 | 175.57 | 175.97 | 177.13
Reliability response in % of peak demand | 1.82% | 1.91% | 2.01% | 2.1% | 2.19% | 2.29% | 2.38% | 2.47% | 2.57% | 2.66% | 2.76% | 2.85% | 2.94% | 3.04% | 3.13% | 3.22% | 3.32% | 3.41% | 3.5% | 3.6% | 3.69% | 3.78% | 3.88% | 3.97% | 4.06% | 4.16% | 4.25% | 4.25% | 4.25% | 4.25% | 4.25%
Tasmania
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 0.36 | 0.5 | 0.63 | 0.78 | 0.91 | 1.05 | 1.18 | 1.34 | 1.52 | 1.71 | 1.88 | 2.05 | 2.21 | 2.38 | 2.55 | 2.7 | 2.83 | 2.98 | 3.14 | 3.32 | 3.49 | 3.64 | 3.79 | 3.92 | 4.05 | 4.2 | 4.31 | 4.25 | 4.16 | 4.09 | 4.07
$500 - $1,000 | 5.95 | 8.19 | 10.4 | 12.81 | 15.07 | 17.32 | 19.55 | 22.07 | 25.09 | 28.22 | 31.15 | 33.85 | 36.49 | 39.28 | 42.09 | 44.55 | 46.83 | 49.24 | 51.94 | 54.9 | 57.76 | 60.2 | 62.61 | 64.85 | 66.92 | 69.38 | 71.27 | 70.17 | 68.82 | 67.67 | 67.33
$1,000 - $7,500 | 5.95 | 8.19 | 10.4 | 12.81 | 15.07 | 17.32 | 19.55 | 22.07 | 25.09 | 28.22 | 31.15 | 33.85 | 36.49 | 39.28 | 42.09 | 44.55 | 46.83 | 49.24 | 51.94 | 54.9 | 57.76 | 60.2 | 62.61 | 64.85 | 66.92 | 69.38 | 71.27 | 70.17 | 68.82 | 67.67 | 67.33
$7,500 + | 5.95 | 8.19 | 10.4 | 12.81 | 15.07 | 17.32 | 19.55 | 22.07 | 25.09 | 28.22 | 31.15 | 33.85 | 36.49 | 39.28 | 42.09 | 44.55 | 46.83 | 49.24 | 51.94 | 54.9 | 57.76 | 60.2 | 62.61 | 64.85 | 66.92 | 69.38 | 71.27 | 70.17 | 68.82 | 67.67 | 67.33
Reliability Response | 5.95 | 8.19 | 10.4 | 12.81 | 15.07 | 17.32 | 19.55 | 22.07 | 25.09 | 28.22 | 31.15 | 33.85 | 36.48 | 39.28 | 42.09 | 44.55 | 46.83 | 49.23 | 51.94 | 54.9 | 57.75 | 60.2 | 62.61 | 64.85 | 66.92 | 69.38 | 71.27 | 70.16 | 68.82 | 67.66 | 67.33
Reliability response in % of peak demand | 0.41% | 0.56% | 0.71% | 0.86% | 1% | 1.15% | 1.3% | 1.45% | 1.59% | 1.74% | 1.89% | 2.04% | 2.18% | 2.33% | 2.48% | 2.63% | 2.77% | 2.92% | 3.07% | 3.22% | 3.36% | 3.51% | 3.66% | 3.81% | 3.95% | 4.1% | 4.25% | 4.25% | 4.25% | 4.25% | 4.25%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 0.36 | 0.53 | 0.7 | 0.88 | 1.05 | 1.23 | 1.4 | 1.59 | 1.81 | 2.04 | 2.26 | 2.46 | 2.66 | 2.87 | 3.06 | 3.25 | 3.43 | 3.62 | 3.83 | 4.04 | 4.25 | 4.43 | 4.6 | 4.77 | 4.95 | 5.13 | 5.3 | 5.22 | 5.15 | 5.07 | 5.05
$500 - $1,000 | 5.95 | 8.73 | 11.64 | 14.56 | 17.43 | 20.29 | 23.17 | 26.28 | 29.92 | 33.65 | 37.35 | 40.6 | 43.98 | 47.39 | 50.65 | 53.66 | 56.65 | 59.84 | 63.22 | 66.76 | 70.17 | 73.2 | 76.03 | 78.91 | 81.84 | 84.78 | 87.62 | 86.33 | 85.05 | 83.86 | 83.53
$1,000 - $7,500 | 5.95 | 8.73 | 11.64 | 14.56 | 17.43 | 20.29 | 23.17 | 26.28 | 29.92 | 33.65 | 37.35 | 40.6 | 43.98 | 47.39 | 50.65 | 53.66 | 56.65 | 59.84 | 63.22 | 66.76 | 70.17 | 73.2 | 76.03 | 78.91 | 81.84 | 84.78 | 87.62 | 86.33 | 85.05 | 83.86 | 83.53
$7,500 + | 5.95 | 8.73 | 11.64 | 14.56 | 17.43 | 20.29 | 23.17 | 26.28 | 29.92 | 33.65 | 37.35 | 40.6 | 43.98 | 47.39 | 50.65 | 53.66 | 56.65 | 59.84 | 63.22 | 66.76 | 70.17 | 73.2 | 76.03 | 78.91 | 81.84 | 84.78 | 87.62 | 86.33 | 85.05 | 83.86 | 83.53
Reliability Response | 5.95 | 8.73 | 11.64 | 14.56 | 17.43 | 20.29 | 23.17 | 26.28 | 29.92 | 33.65 | 37.35 | 40.6 | 43.99 | 47.39 | 50.65 | 53.66 | 56.65 | 59.84 | 63.22 | 66.76 | 70.17 | 73.2 | 76.03 | 78.91 | 81.84 | 84.78 | 87.62 | 86.33 | 85.05 | 83.86 | 83.54
Reliability response in % of peak demand | 0.33% | 0.48% | 0.63% | 0.78% | 0.94% | 1.09% | 1.24% | 1.39% | 1.54% | 1.69% | 1.84% | 1.99% | 2.14% | 2.29% | 2.44% | 2.59% | 2.74% | 2.89% | 3.04% | 3.2% | 3.35% | 3.5% | 3.65% | 3.8% | 3.95% | 4.1% | 4.25% | 4.25% | 4.25% | 4.25% | 4.25%
Victoria
Summer
Price band | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 63.18 | 65.32 | 67.98 | 71.25 | 74.37 | 78.17 | 81.93 | 85.73 | 90.01 | 94 | 98.52 | 102.49 | 106.3 | 110.14 | 113.84 | 117.3 | 120.59 | 124.11 | 127.1 | 130.08 | 133.03 | 135.55 | 138.21 | 140.37 | 142.87 | 145 | 147.09 | 148.08 | 149.07 | 150.13 | 150.76
$7,500 + | 63.18 | 65.32 | 67.98 | 71.25 | 74.37 | 78.17 | 81.93 | 85.73 | 90.01 | 94 | 98.52 | 102.49 | 106.3 | 110.14 | 113.84 | 117.3 | 120.59 | 124.11 | 127.1 | 130.08 | 133.03 | 135.55 | 138.21 | 140.37 | 142.87 | 145 | 147.09 | 148.08 | 149.07 | 150.13 | 150.76
Reliability Response | 257.18 | 265.87 | 276.72 | 290.01 | 302.71 | 318.19 | 333.49 | 348.98 | 366.38 | 382.62 | 401.06 | 417.2 | 432.72 | 448.35 | 463.4 | 477.49 | 490.89 | 505.2 | 517.37 | 529.52 | 541.52 | 551.78 | 562.6 | 571.41 | 581.56 | 590.23 | 598.75 | 602.77 | 606.81 | 611.12 | 613.67
Reliability response in % of peak demand | 2.53% | 2.59% | 2.66% | 2.73% | 2.79% | 2.86% | 2.92% | 2.99% | 3.06% | 3.12% | 3.19% | 3.26% | 3.32% | 3.39% | 3.45% | 3.52% | 3.59% | 3.65% | 3.72% | 3.79% | 3.85% | 3.92% | 3.98% | 4.05% | 4.12% | 4.18% | 4.25% | 4.25% | 4.25% | 4.25% | 4.25%
Winter
Price band | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054
$300 - $500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$500 - $1,000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
$1,000 - $7,500 | 63.18 | 65.62 | 69.29 | 73.26 | 77.87 | 82.73 | 87.52 | 92.43 | 97.69 | 102.5 | 107.28 | 111.96 | 117.49 | 122.58 | 127.45 | 131.63 | 135.4 | 139.94 | 144.63 | 149.23 | 152.69 | 155.54 | 159.1 | 163.06 | 166.82 | 170.11 | 172.86 | 172.18 | 172.79 | 173.05 | 172.97
$7,500 + | 63.18 | 65.62 | 69.29 | 73.26 | 77.87 | 82.73 | 87.52 | 92.43 | 97.69 | 102.5 | 107.28 | 111.96 | 117.49 | 122.58 | 127.45 | 131.63 | 135.4 | 139.94 | 144.63 | 149.23 | 152.69 | 155.54 | 159.1 | 163.06 | 166.82 | 170.11 | 172.86 | 172.18 | 172.79 | 173.05 | 172.97
Reliability Response | 212.18 | 220.36 | 232.69 | 246.02 | 261.52 | 277.85 | 293.92 | 310.4 | 328.07 | 344.22 | 360.27 | 376 | 394.57 | 411.67 | 428.03 | 442.06 | 454.72 | 469.98 | 485.71 | 501.17 | 512.79 | 522.34 | 534.31 | 547.62 | 560.25 | 571.29 | 580.53 | 578.24 | 580.27 | 581.16 | 580.89
Reliability response in % of peak demand | 2.63% | 2.69% | 2.75% | 2.82% | 2.88% | 2.94% | 3% | 3.06% | 3.13% | 3.19% | 3.25% | 3.31% | 3.38% | 3.44% | 3.5% | 3.56% | 3.63% | 3.69% | 3.75% | 3.81% | 3.88% | 3.94% | 4% | 4.06% | 4.13% | 4.19% | 4.25% | 4.25% | 4.25% | 4.25% | 4.25%

## Economic Growth Forecasts
Go to Assumptions Summary
Economic Growth Forecasts | [8 empty] | Note: | Further information is available at https://forecasting.aemo.com.au
Gross State Product and Household Disposable Income forecasts based on Oxford Economics Australia's (previously BIS Oxford Economics) long term macroeconomic forecasts developed for AEMO in July 2022,
and rebased using the financial year 2021-22 Australian Bureau of Statistics (ABS) National Accounts release (available at: https://www.abs.gov.au/statistics/economy/national-accounts/australian-system-national-accounts/2021-22).
Note that forecasts are in real terms (2022-23 prices).
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | Progressive Change | Step Change | Hydrogen Export
Gross State Product ($ millions, real 2022-23)
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 787813.7584 | 796768.0017 | 823512.4063 | 844915.6283 | 870032.4498 | 893238.476 | 914868.3157 | 935687.071 | 956090.1614 | 976225.2995 | 996030.2552 | 1015166.6467 | 1033043.3152 | 1050062.8579 | 1066765.3293 | 1083175.3629 | 1099446.6648 | 1115649.1035 | 1131863.6998 | 1148238.2591 | 1164800.1698 | 1181553.9952 | 1198442.9452 | 1215495.628 | 1232817.1888 | 1250439.5687 | 1267769.427 | 1285126.6493 | 1302749.2029 | 1320613.8414 | 1338723.8973
QLD | 432732.3386 | 438218.0404 | 453081.5285 | 466029.2133 | 481081.1653 | 495086.4846 | 508790.3926 | 522364.9151 | 535368.5058 | 547700.1989 | 559797.0218 | 571700.6055 | 583056.085 | 594005.3908 | 604793.3145 | 615391.6492 | 625933.4806 | 636463.9904 | 646874.6864 | 657205.1733 | 667492.0282 | 677700.2545 | 687826.2367 | 697917.5707 | 707980.0752 | 718034.3374 | 727814.519 | 737449.9154 | 747208.3187 | 757095.8513 | 767114.2221
SA | 131592.9981 | 132157.0082 | 135870.213 | 138504.5445 | 141768.7583 | 144922.3429 | 148144.3532 | 151300.732 | 154299.94 | 157160.0799 | 159889.8434 | 162520.5135 | 164985.592 | 167348.0542 | 169675.5861 | 171934.2686 | 174134.3182 | 176314.2845 | 178472.8108 | 180604.7199 | 182712.0212 | 184796.8555 | 186858.4189 | 188908.4998 | 190956.088 | 193004.5932 | 194974.9935 | 196911.8216 | 198869.1074 | 200845.8484 | 202842.238
TAS | 38447.6268 | 38656.0013 | 39773.0337 | 40467.0088 | 41420.1309 | 42338.3593 | 43205.351 | 44018.5881 | 44805.2703 | 45560.3856 | 46271.7125 | 46957.5008 | 47606.6906 | 48225.5927 | 48841.6402 | 49453.745 | 50058.7044 | 50660.8304 | 51262.838 | 51862.2558 | 52456.6072 | 53050.6538 | 53645.7781 | 54243.3094 | 54848.158 | 55462.6494 | 56066.7661 | 56670.2864 | 57281.2467 | 57898.7938 | 58522.9986
VIC | 567164.3593 | 576957.0158 | 601550.7181 | 621554.7733 | 643684.9794 | 664799.1788 | 684967.4803 | 704555.2659 | 723310.1739 | 740930.2656 | 757722.5645 | 773735.9792 | 788676.8568 | 802941.3675 | 817023.7452 | 830806.1893 | 844222.0314 | 857327.6129 | 870145.451 | 882682.2591 | 894916.0102 | 906871.9116 | 918510.5846 | 929804.0315 | 940780.5679 | 951413.4576 | 961156.9348 | 970238.8451 | 979377.9469 | 988603.1339 | 997915.217
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 803481.4869 | 824670.2169 | 840601.2976 | 857088.4751 | 879825.2198 | 905928.9325 | 933574.5098 | 960684.9497 | 986485.8786 | 1010020.546 | 1033663.2483 | 1056693.2852 | 1077829.725 | 1099045.984 | 1120200.3884 | 1140796.6441 | 1161017.2616 | 1181305.5518 | 1201742.0108 | 1222465.5824 | 1243537.4398 | 1264872.2367 | 1286506.7474 | 1308382.4654 | 1330600.6939 | 1353165.6775 | 1376001.0714 | 1399350.9031 | 1423165.2173 | 1447385.1815 | 1472017.7126
QLD | 444764.0224 | 457499.4348 | 469451.3837 | 481684.8964 | 495432.3706 | 509881.7417 | 524963.0953 | 540302.8139 | 555256.3091 | 569166.4929 | 583105.4899 | 596842.2651 | 609686.1505 | 622587.6622 | 635693.6201 | 648598.0979 | 661108.7253 | 673554.629 | 686035.5959 | 698529.3803 | 711034.7112 | 723525.1058 | 736002.2591 | 748454.2009 | 760924.2569 | 773436.0495 | 785954.7276 | 798577.8062 | 811411.9807 | 824452.4169 | 837702.4297
SA | 136562.4396 | 138815.1654 | 141078.4199 | 143353.2324 | 146219.7144 | 149498.8314 | 153123.7735 | 156976.4644 | 160597.5576 | 163952.5485 | 167307.608 | 170573.6823 | 173569.3832 | 176580.4476 | 179607.1113 | 182570.9403 | 185448.3927 | 188304.3408 | 191149.9655 | 193994.7226 | 196851.3565 | 199711.3801 | 202570.4855 | 205429.8645 | 208296.8848 | 211184.2231 | 214085.3834 | 217010.9544 | 219976.3519 | 222982.2708 | 226029.2648
TAS | 39783.6698 | 40464.4813 | 41259.737 | 42052.8646 | 42988.6366 | 43979.5702 | 45015.4251 | 46051.8159 | 47040.7741 | 47971.9243 | 48903.5993 | 49809.5276 | 50648.7194 | 51488.5314 | 52331.9001 | 53170.5231 | 53999.3455 | 54815.1303 | 55625.0298 | 56437.8885 | 57254.7265 | 58075.9266 | 58900.6128 | 59728.6293 | 60564.014 | 61411.8658 | 62271.65 | 63133.9985 | 64005.135 | 64888.2917 | 65783.6343
VIC | 582807.1121 | 601829.7451 | 620520.0467 | 639772.5366 | 660325.5102 | 681899.5121 | 704249.2813 | 727148.1291 | 749256.1334 | 769166.4032 | 788815.462 | 807646.1468 | 824784.6952 | 841990.868 | 859496.2699 | 876944.7538 | 893814.7716 | 910347.8697 | 926638.0011 | 942773.2194 | 958767.7267 | 974550.0751 | 990111.6341 | 1005354.9548 | 1020311.282 | 1034936.2611 | 1049111.6863 | 1063000.7962 | 1077068.4131 | 1091322.199 | 1105764.6177
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 822811.6849 | 860716.7849 | 891787.3951 | 918095.7187 | 943512.2683 | 968512.3528 | 994662.0581 | 1024170.9153 | 1053054.2659 | 1081759.7797 | 1110852.4669 | 1139566.4534 | 1166904.3353 | 1194502.0963 | 1223011.4214 | 1251655.608 | 1279280.7418 | 1307103.2278 | 1335678.1774 | 1364875.1921 | 1394602.3712 | 1425032.3725 | 1455865.7953 | 1487256.6518 | 1519478.3556 | 1552680.9439 | 1586847.6684 | 1621868.1045 | 1657654.9136 | 1694231.3775 | 1731614.9206
QLD | 453475.0529 | 474526.9366 | 492388.3137 | 508645.7896 | 523931.0995 | 538544.0502 | 553481.5401 | 569773.0745 | 586334.7803 | 602920.6982 | 619481.1398 | 635889.5693 | 651859.115 | 668042.3576 | 684791.6228 | 701693.6939 | 717950.5118 | 734222.7201 | 750756.5929 | 767601.6745 | 784618.3242 | 801775.1105 | 819002.9065 | 836381.7081 | 854028.2512 | 872040.3106 | 890405.2889 | 909042.1687 | 928049.87 | 947455.0145 | 967265.9127
SA | 138449.1059 | 143558.9559 | 147880.8334 | 151789.073 | 155172.9613 | 158381.348 | 161931.1464 | 165797.4426 | 169640.1095 | 173577.5663 | 177549.0257 | 181423.2918 | 185149.3566 | 188961.6152 | 192938.0611 | 196912.3225 | 200661.9502 | 204424.8734 | 208238.394 | 212096.7063 | 215981.6146 | 219905.8113 | 223834.4839 | 227779.4867 | 231781.4478 | 235867.6909 | 240035.7972 | 244265.4596 | 248566.5785 | 252943.4332 | 257397.3572
TAS | 40569.3 | 42045.1522 | 43230.644 | 44288.5181 | 45241.8935 | 46091.5087 | 46962.9948 | 47881.8149 | 48803.5244 | 49765.8902 | 50742.3213 | 51685.7893 | 52589.2352 | 53518.0004 | 54496.174 | 55481.3367 | 56411.8395 | 57353.745 | 58309.6536 | 59278.9061 | 60257.1959 | 61250.3633 | 62251.0685 | 63260.4912 | 64292.8931 | 65355.6619 | 66448.4845 | 67563.5778 | 68697.0121 | 69849.4607 | 71021.2426
VIC | 594648.7659 | 626694.7667 | 655911.0148 | 681922.4146 | 705850.8311 | 729066.0557 | 752647.4248 | 778153.5657 | 803293.0967 | 828105.5984 | 852868.4993 | 877016.129 | 900096.5096 | 923420.56 | 947697.7385 | 972196.7056 | 995622.7885 | 1018810.7143 | 1042204.2885 | 1065767.0599 | 1089362.4144 | 1113094.9829 | 1136703.6005 | 1160205.1089 | 1183783.9987 | 1207540.2328 | 1231374.6295 | 1255168.6104 | 1279369.9481 | 1304037.9201 | 1329181.5238
Household Disposable Income ($ millions, real 2022-23)
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 541838.4907 | 546782.4777 | 561286.8146 | 575727.4653 | 587710.1489 | 600798.7924 | 614504.3776 | 627876.93 | 642112.4632 | 656687.1854 | 671349.6494 | 685767.116 | 699051.9621 | 711972.2215 | 725204.2683 | 738477.9833 | 751280.9874 | 763668.0997 | 776079.5929 | 788703.9889 | 801571.1126 | 814622.2553 | 827835.7784 | 841158.7757 | 854650.3636 | 868426.4793 | 882542.6729 | 897034.9501 | 911779.9611 | 926767.6958 | 942002.156
QLD | 298639.7215 | 299608.5166 | 304144.5599 | 310751.1192 | 317595.0294 | 324726.0582 | 332760.707 | 341905.0261 | 351110.6627 | 359496.7134 | 367705.2913 | 376150.3301 | 384085.6249 | 391714.4879 | 399519.8352 | 407440.5897 | 415132.554 | 422646.4978 | 430146.875 | 437612.9383 | 445039.6655 | 452467.1014 | 459874.5558 | 467229.5994 | 474526.4004 | 481858.711 | 489254.1995 | 496677.5628 | 504206.0774 | 511848.7074 | 519607.1825
SA | 98206.3645 | 99031.964 | 100664.1082 | 102581.7199 | 104394.732 | 106451.41 | 108681.0092 | 111034.7349 | 113432.0306 | 115727.3253 | 117949.1024 | 120110.9294 | 122085.4636 | 124019.4239 | 126013.5652 | 128009.7008 | 129911.778 | 131757.8881 | 133596.5466 | 135426.0453 | 137246.8699 | 139058.8741 | 140864.2208 | 142657.2413 | 144442.2503 | 146239.0761 | 148056.5791 | 149894.3215 | 151754.3818 | 153637.5239 | 155544.0342
TAS | 31553.1714 | 31793.653 | 32243.39 | 32718.7929 | 33229.6346 | 33835.2331 | 34475.8026 | 35142.7038 | 35824.8053 | 36482.3356 | 37108.8769 | 37712.0314 | 38262.6466 | 38800.8839 | 39359.6 | 39926.6694 | 40477.1663 | 41015.2881 | 41553.6583 | 42092.5755 | 42630.4453 | 43168.3568 | 43710.6243 | 44254.7372 | 44801.7812 | 45359.2594 | 45931.362 | 46516.5202 | 47109.6051 | 47710.2519 | 48318.5569
VIC | 374977.7405 | 379118.6527 | 387361.9401 | 396264.7467 | 404510.9822 | 413641.0217 | 424057.8285 | 436289.2916 | 448812.5712 | 460771.8435 | 472330.7783 | 483499.7696 | 493759.6073 | 503715.0807 | 513879.157 | 524088.7024 | 533882.0545 | 543287.5969 | 552538.9753 | 561669.7229 | 570668.8142 | 579529.7376 | 588246.0039 | 596745.8502 | 605037.4425 | 613173.7301 | 621140.8004 | 628945.2474 | 636824.016 | 644801.4815 | 652878.8804
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 550831.6307 | 556864.3769 | 568407.1738 | 582738.3975 | 599933.3807 | 620010.5099 | 639955.4939 | 658840.0204 | 676823.4632 | 693328.0329 | 709529.4352 | 725574.2619 | 740349.6215 | 754678.2883 | 769065.4897 | 783455.0003 | 797600.1369 | 811549.357 | 825577.3335 | 839761.1914 | 854126.7457 | 868669.3662 | 883402.6668 | 898261.7593 | 913289.2289 | 928587.839 | 944190.453 | 960097.1889 | 976276.6072 | 992728.8066 | 1009458.3884
QLD | 303154.16 | 305762.5323 | 311333.1518 | 318877.8539 | 328198.8027 | 338968.1299 | 349920.5367 | 360657.4613 | 370852.5717 | 380353.4809 | 389768.4033 | 399121.5418 | 407751.3632 | 416242.3004 | 424993.3892 | 433825.5876 | 442385.8775 | 450754.3925 | 459131.6583 | 467527.1366 | 475904.339 | 484261.8134 | 492592.523 | 500898.8601 | 509161.8994 | 517434.0824 | 525759.9677 | 534142.5578 | 542652.9448 | 551298.9261 | 560082.6621
SA | 99508.0053 | 100569.1031 | 102436.4696 | 104799.2871 | 107557.1551 | 110682.4776 | 113662.8616 | 116450.7173 | 119078.9497 | 121527.1707 | 123971.6635 | 126385.8923 | 128560.9779 | 130666.0858 | 132825.9337 | 135007.4109 | 137108.78 | 139138.7968 | 141139.0285 | 143129.0621 | 145117.5063 | 147097.0777 | 149065.0755 | 151017.3796 | 152958.0198 | 154900.3108 | 156854.0816 | 158824.705 | 160819.5968 | 162839.5451 | 164884.8647
TAS | 31952.0122 | 32206.8653 | 32714.7197 | 33362.5238 | 34155.4097 | 35066.9112 | 35918.0887 | 36684.2955 | 37398.5164 | 38076.6577 | 38757.7265 | 39427.1859 | 40024.9649 | 40597.5696 | 41188.5223 | 41795.7255 | 42390.9084 | 42966.2657 | 43531.9473 | 44097.0209 | 44664.1013 | 45231.608 | 45801.3472 | 46371.3563 | 46943.1786 | 47521.8117 | 48111.0918 | 48709.773 | 49315.8713 | 49929.5113 | 50550.7869
VIC | 380541.3393 | 386322.2839 | 394821.5867 | 405213.789 | 417545.3281 | 431454.8333 | 445484.4389 | 460251.406 | 474371.0091 | 487352.7048 | 500086.384 | 512525.1059 | 523886.0561 | 534866.2349 | 546032.6894 | 557335.6625 | 568330.2178 | 578937.0939 | 589338.3809 | 599619.829 | 609799.7026 | 619857.8055 | 629777.9303 | 639491.1465 | 648998.991 | 658334.9588 | 667493.0441 | 676506.5484 | 685619.8292 | 694855.8758 | 704216.3421
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 562673.5538 | 576023.207 | 594276.8207 | 613627.6087 | 633137.2086 | 654377.2037 | 674284.3898 | 693176.7396 | 711865.8613 | 730111.3733 | 748592.9393 | 767289.4116 | 784983.7511 | 802241.8166 | 819897.4169 | 837808.5955 | 855330.9515 | 872596.2704 | 890315.6867 | 908251.1364 | 926391.0158 | 944937.0645 | 963802.8268 | 982880.6255 | 1002282.4517 | 1022158.4685 | 1042551.7743 | 1063355.5389 | 1084535.9726 | 1106138.2921 | 1128170.901
QLD | 309555.5188 | 315287.5063 | 323226.4513 | 333142.2795 | 343709.6843 | 354765.3456 | 365513.1772 | 376563.2396 | 387758.3501 | 398623.0259 | 409288.1894 | 420045.5202 | 430421.2233 | 440603.868 | 451065.599 | 461861.2544 | 472486.6244 | 482779.9395 | 493155.346 | 503708.0079 | 514399.3755 | 525170.1215 | 535935.6354 | 546765.7258 | 557706.095 | 568810.6583 | 580112.6142 | 591556.3255 | 603196.7084 | 615066.1455 | 627169.1442
SA | 101527.0714 | 103597.4831 | 106242.2127 | 109284.1506 | 112304.4125 | 115478.5341 | 118341.9192 | 121080.6408 | 123864.0144 | 126641.3056 | 129406.419 | 132137.8256 | 134675.8353 | 137138.5024 | 139694.4462 | 142326.0817 | 144871.1811 | 147313.0784 | 149759.6819 | 152214.5107 | 154685.1004 | 157180.1521 | 159673.5321 | 162156.9721 | 164650.2106 | 167179.8632 | 169755.7347 | 172357.4713 | 174991.4542 | 177665.6898 | 180380.7933
TAS | 32589.9601 | 33153.5181 | 33875.6843 | 34717.9159 | 35583.2087 | 36495.1606 | 37293.0734 | 38024.7446 | 38770.7637 | 39537.261 | 40297.9655 | 41037.5791 | 41717.7116 | 42372.8532 | 43056.2967 | 43770.4012 | 44471.4423 | 45143.7085 | 45814.0515 | 46487.7882 | 47168.8105 | 47859.817 | 48554.533 | 49249.7147 | 49951.9864 | 50670.4063 | 51409.0273 | 52159.0751 | 52917.8069 | 53687.5757 | 54468.5419
VIC | 388628.8848 | 398753.0418 | 410844.4843 | 424217.2345 | 437863.8238 | 452278.9763 | 466171.6832 | 481135.7649 | 496237.6785 | 510932.0692 | 525478.0727 | 539821.9831 | 553288.5609 | 566357.0975 | 579814.8528 | 593659.8382 | 607175.746 | 620206.9118 | 633236.7892 | 646243.9563 | 659231.4149 | 672272.7303 | 685258.9165 | 698096.1772 | 710852.2262 | 723616.2009 | 736381.5701 | 749081.6946 | 761948.6602 | 775036.6415 | 788349.4348

## Energy Efficiency
Go to Assumptions Summary
Energy Efficiency (GWh) | [8 empty] | Note: | Further information is available at https://forecasting.aemo.com.au
Based on 2023 forecasts developed by Strategy Policy Research (SPR).
AEMO has rebased forecasts for both Residential and Business Energy Efficiency forecasts, setting 2022-23 as the base year.
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports | Reduced Energy Efficiency
Consultant's scenario/sensitivity name | Progressive Change | Orchestrated Step Change | Green Energy Exports | Low Energy Efficiency sensitivity
Residential Energy Efficiency (GWh)
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 185.9598 | 387.8925 | 591.3927 | 803.8316 | 1030.3261 | 1256.8357 | 1497.507 | 1755.7966 | 2004.7731 | 2245.286 | 2476.2467 | 2705.882 | 3035.9133 | 3367.1892 | 3703.4592 | 4151.4322 | 4497.763 | 4883.129 | 5262.4175 | 5629.782 | 5987.4595 | 6334.6795 | 6845.5945 | 7353.383 | 7856.554 | 8353.6225 | 8662.77 | 8658.379 | 8657.923 | 8661.044 | 8667.493
QLD | 100.4225 | 201.5157 | 297.6025 | 395.3587 | 493.0916 | 582.9231 | 664.9758 | 756.7353 | 843.0699 | 925.0809 | 1002.6922 | 1077.0789 | 1201.8474 | 1326.1761 | 1451.1344 | 1629.3869 | 1759.5014 | 1923.9354 | 2095.734 | 2275.6588 | 2458.5635 | 2640.724 | 2911.001 | 3182.942 | 3458.507 | 3738.9885 | 3927.1377 | 4117.423 | 4309.458 | 4504.1375 | 4702.127
SA | 51.0521 | 98.5724 | 159.262 | 218.8695 | 270.799 | 329.0515 | 383.6172 | 409.4985 | 432.6481 | 450.6418 | 463.5849 | 473.0761 | 517.8687 | 572.9379 | 628.0416 | 696.7472 | 750.1504 | 815.2882 | 881.3563 | 947.2321 | 1013.3328 | 1079.8156 | 1172.5519 | 1266.0121 | 1360.1649 | 1454.7867 | 1521.9223 | 1589.4407 | 1657.3774 | 1725.8414 | 1794.8595
TAS | 14.4758 | 28.748 | 42.3478 | 63.6096 | 84.3826 | 104.3262 | 122.6881 | 142.6367 | 160.7434 | 177.5802 | 193.3879 | 208.5776 | 230.9701 | 253.1653 | 275.2343 | 300.858 | 318.5438 | 339.3488 | 360.1143 | 380.9975 | 401.9379 | 422.9067 | 456.0992 | 489.4945 | 523.1839 | 557.1184 | 578.2361 | 599.4688 | 620.8948 | 642.4742 | 664.2004
VIC | 269.4895 | 535.9393 | 583.5177 | 705.7526 | 839.4851 | 914.4322 | 971.6494 | 1013.5431 | 1057.9594 | 1225.8277 | 1420.2777 | 1617.1608 | 1872.7101 | 2133.7422 | 2400.2238 | 2759.8083 | 3068.7903 | 3440.9215 | 3813.037 | 4187.639 | 4563.9875 | 4941.7085 | 5414.056 | 5890.788 | 6372.059 | 6856.343 | 7241.119 | 7627.3825 | 8015.5715 | 8406.007 | 8800.274
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 343.1086 | 706.9759 | 1134.01 | 1585.0144 | 2063.0667 | 2551.8652 | 3003.6565 | 3501.6565 | 3999.2218 | 4498.334 | 4998.9 | 5506.6505 | 6003.9455 | 6510.4785 | 7030.6745 | 7682.338 | 8188.274 | 8746.266 | 9290.449 | 9824.399 | 10354.174 | 10878.836 | 11663.136 | 12449.797 | 13235.283 | 14016.605 | 14511.676 | 14553.849 | 14593.863 | 14631.539 | 14666.917
QLD | 182.6043 | 367.5875 | 576.3855 | 785.6916 | 1003.0498 | 1225.1295 | 1417.0551 | 1639.7496 | 1859.6263 | 2077.6435 | 2294.6562 | 2511.1782 | 2716.0135 | 2921.8083 | 3129.2278 | 3395.953 | 3588.706 | 3828.783 | 4067.8052 | 4307.4845 | 4554.155 | 4807.597 | 5202.581 | 5602.752 | 6007.456 | 6416.7185 | 6681.065 | 6947.6985 | 7216.9285 | 7489.238 | 7765.248
SA | 78.2383 | 154.3439 | 253.3883 | 357.1026 | 460.0715 | 574.7756 | 681.5369 | 754.0674 | 824.1902 | 889.5801 | 950.5353 | 1008.0199 | 1058.5219 | 1116.709 | 1199.1634 | 1296.4209 | 1369.304 | 1458.9775 | 1548.0931 | 1638.3582 | 1729.8698 | 1822.3309 | 1955.4316 | 2089.6906 | 2224.9918 | 2361.1505 | 2454.8158 | 2548.7205 | 2642.9975 | 2737.815 | 2833.3958
TAS | 27.7146 | 55.6127 | 87.7094 | 128.5777 | 169.7144 | 210.6391 | 245.9757 | 286.5813 | 325.3232 | 362.9974 | 399.9416 | 436.2443 | 469.4836 | 502.4951 | 535.3177 | 571.7183 | 595.9826 | 624.9777 | 653.9121 | 682.8792 | 711.8099 | 740.7242 | 788.1807 | 835.9043 | 883.9997 | 932.3855 | 961.1007 | 989.8783 | 1018.7841 | 1047.8239 | 1077.0121
VIC | 401.219 | 820.2845 | 1034.1655 | 1331.2462 | 1652.7161 | 1934.4031 | 2183.3765 | 2487.8268 | 2782.8023 | 3120.6303 | 3547.1653 | 3968.5028 | 4379.188 | 4788.7475 | 5197.867 | 5696.891 | 6111.3825 | 6635.0785 | 7159.13 | 7685.3905 | 8213.029 | 8743.478 | 9422.691 | 10109.348 | 10802.947 | 11501.587 | 12044.413 | 12588.324 | 13133.793 | 13681.381 | 14234.196
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 281.8256 | 583.7567 | 950.4482 | 1339.9804 | 1754.4084 | 2179.0055 | 2565.6717 | 3002.6385 | 3441.3812 | 3884.5662 | 4332.363 | 4791.2305 | 5375.951 | 5977.62 | 6601.8145 | 7367.254 | 7938.379 | 8571.688 | 9202.37 | 9827.394 | 10449.648 | 11066.893 | 12033.857 | 13006.15 | 13980.39 | 14953.24 | 15545.244 | 15539.804 | 15527.207 | 15507.049 | 15479.066
QLD | 152.2291 | 305.3799 | 482.6807 | 664.6346 | 853.8173 | 1046.5536 | 1208.9503 | 1407.3408 | 1601.8722 | 1793.4335 | 1983.2818 | 2172.8875 | 2424.607 | 2676.2135 | 2927.369 | 3239.2915 | 3446.0768 | 3707.7625 | 3973.163 | 4243.6825 | 4522.699 | 4809.8335 | 5294.7845 | 5787.998 | 6288.4315 | 6796.356 | 7101.9 | 7414.731 | 7734.7115 | 8056.8875 | 8381.7165
SA | 68.6298 | 135.2769 | 228.0945 | 326.9613 | 425.691 | 537.0471 | 641.3994 | 705.3763 | 766.8956 | 823.7099 | 876.2254 | 925.3578 | 986.8064 | 1044.0335 | 1130.9764 | 1240.267 | 1316.4094 | 1411.3056 | 1506.7129 | 1602.8725 | 1699.9925 | 1797.9523 | 1950.1156 | 2103.866 | 2259.1512 | 2415.751 | 2515.6092 | 2616.01 | 2717.0425 | 2818.892 | 2921.763
TAS | 22.3428 | 44.9152 | 71.6901 | 108.0441 | 144.7264 | 181.2169 | 212.0494 | 248.8837 | 283.7395 | 317.5017 | 350.4868 | 382.8007 | 422.4196 | 461.9008 | 501.2903 | 544.4204 | 571.1571 | 603.4737 | 635.8425 | 668.3112 | 700.8107 | 733.353 | 791.2871 | 849.7017 | 908.7079 | 968.2456 | 1000.9792 | 1033.8371 | 1066.9206 | 1100.2159 | 1133.7386
VIC | 388.9889 | 804.1777 | 994.1344 | 1270.3445 | 1575.7839 | 1852.1215 | 2104.4983 | 2440.862 | 2765.0338 | 3074.4907 | 3524.9535 | 3970.0455 | 4475.8455 | 4981.825 | 5488.781 | 6088.0175 | 6570.249 | 7190.478 | 7814.868 | 8444.191 | 9078.935 | 9720.417 | 10574.646 | 11441.782 | 12320.884 | 13209.661 | 13878.946 | 14552.372 | 15230.482 | 15913.936 | 16606.361
5795.9447
Reduced Energy Efficiency (Sensitivity)
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 339.3894 | 698.7645 | 1061.5025 | 1442.8526 | 1845.9041 | 2254.1083 | 2680.9138 | 3110.5392 | 3534.058 | 3952.6948 | 4365.879 | 4778.61 | 5014.5965 | 5246.865 | 5478.999 | 5828.055 | 6188.4965 | 6570.0585 | 6931.9955 | 7278.6255 | 7616.2775 | 7944.109 | 8266.5835 | 8581.679 | 8886.226 | 9177.587 | 9455.526 | 9407.111 | 9358.36 | 9309.09 | 9259.13
QLD | 180.5738 | 363.0972 | 539.8841 | 714.2489 | 893.6883 | 1074.6929 | 1252.8299 | 1427.4462 | 1598.4279 | 1766.669 | 1932.8647 | 2097.3448 | 2167.9797 | 2235.852 | 2301.437 | 2422.4465 | 2554.629 | 2707.697 | 2857.9223 | 3006.6892 | 3160.3767 | 3318.7645 | 3479.6295 | 3640.2728 | 3799.8545 | 3958.3727 | 4116.4192 | 4274.503 | 4432.826 | 4591.7885 | 4751.4285
SA | 77.4511 | 152.6108 | 238.1848 | 324.3626 | 405.7542 | 494.827 | 581.3747 | 633.3869 | 682.7796 | 727.301 | 767.1955 | 803.3768 | 830.0037 | 865.3885 | 899.7014 | 947.9362 | 997.4474 | 1051.1556 | 1103.9421 | 1157.4444 | 1211.7191 | 1266.4497 | 1321.2255 | 1375.7893 | 1429.9391 | 1483.6265 | 1536.9243 | 1589.9725 | 1642.8555 | 1695.7127 | 1748.4999
TAS | 27.4612 | 55.054 | 82.3207 | 109.28 | 136.2223 | 162.9223 | 188.9388 | 214.2096 | 238.7367 | 262.7012 | 286.2758 | 309.4988 | 318.1908 | 326.5214 | 334.5399 | 346.1126 | 357.9612 | 371.2518 | 384.4061 | 397.5749 | 410.7067 | 423.7112 | 436.5317 | 449.146 | 461.6556 | 474.0597 | 486.3814 | 498.6303 | 510.8367 | 522.9835 | 535.0198
VIC | 398.495 | 814.2461 | 994.1819 | 1254.1395 | 1535.305 | 1773.4068 | 2007.2576 | 2189.7447 | 2361.9075 | 2576.4262 | 2879.4997 | 3176.8708 | 3377.86 | 3573.7917 | 3765.1505 | 4042.9457 | 4326.6365 | 4631.1015 | 4934.886 | 5238.916 | 5542.914 | 5847.944 | 6154.4175 | 6462.87 | 6772.4615 | 7081.6915 | 7390.3935 | 7699.039 | 8007.9835 | 8317.643 | 8628.91
Business Energy Efficiency (GWh)
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 0 | 91.0898 | 237.1691 | 395.802 | 707.9284 | 1106.0305 | 1495.5393 | 1901.9787 | 2305.634 | 2692.824 | 3074.3225 | 3507.1152 | 3923.8618 | 4382.186 | 4767.5685 | 5137.6055 | 5516.616 | 5902.8385 | 6298.241 | 6701.932 | 7116.738 | 7687.1735 | 8267.012 | 8856.345 | 9602.529 | 10360.028 | 10744.097 | 11132.144 | 11523.897 | 11919.075 | 12318.32
QLD | 0 | 65.9529 | 160.5449 | 278.3392 | 530.5191 | 864.4846 | 1188.264 | 1507.1958 | 1824.7771 | 2136.3313 | 2438.1653 | 2781.3985 | 3120.0068 | 3495.398 | 3818.515 | 4137.3915 | 4456.661 | 4772.6925 | 5087.487 | 5400.9025 | 5712.335 | 6128.6315 | 6544.7165 | 6960.1605 | 7481.09 | 8002.1195 | 8312.9215 | 8623.91 | 8935.499 | 9247.925 | 9561.866
SA | 0 | 17.9061 | 36.6935 | 64.0066 | 123.9813 | 226.5521 | 307.738 | 387.1088 | 461.8063 | 533.4156 | 601.8673 | 685.1795 | 766.3495 | 859.0669 | 931.7506 | 1008.0665 | 1104.1517 | 1199.52 | 1293.8426 | 1387.5991 | 1480.8935 | 1614.9881 | 1748.9129 | 1882.8935 | 2058.3656 | 2233.988 | 2327.1055 | 2420.2342 | 2513.3835 | 2606.6737 | 2700.3967
TAS | 0 | 7.2345 | 18.242 | 32.0161 | 57.0479 | 88.9774 | 120.3365 | 152.1078 | 183.5556 | 214.9418 | 246.6001 | 282.6751 | 318.2055 | 356.1274 | 389.3793 | 422.3111 | 455.6667 | 489.2937 | 522.9233 | 556.4892 | 590.2112 | 634.7377 | 679.3499 | 724.1933 | 779.9737 | 836.0051 | 871.2895 | 906.9386 | 942.9267 | 979.2276 | 1015.9004
VIC | 0 | 64.7983 | 133.8739 | 200.9477 | 462.5893 | 770.7977 | 1030.1207 | 1290.1292 | 1517.8889 | 1716.0283 | 1903.0085 | 2349.4637 | 2787.2155 | 3268.9425 | 3692.2945 | 4106.568 | 4522.8405 | 4937.3675 | 5349.5075 | 5759.5425 | 6168.4415 | 6699.462 | 7231.2745 | 7762.7715 | 8419.602 | 9075.748 | 9475.786 | 9874.402 | 10272.672 | 10671.634 | 11073.214
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 0 | 112.4215 | 333.6781 | 643.7824 | 989.4529 | 1395.1453 | 1818.474 | 2246.6318 | 2636.0565 | 3023.6562 | 3378.7427 | 3737.813 | 4102.1095 | 4496.35 | 4934.0595 | 5358.448 | 5794.961 | 6235.523 | 6684.751 | 7143.083 | 7611.9055 | 8281.7055 | 8962.076 | 9651.538 | 10158.2 | 10675.246 | 11075.018 | 11476.478 | 11879.68 | 12284.762 | 12691.637
QLD | 0 | 82.6421 | 229.4345 | 460.4776 | 737.1015 | 1066.7555 | 1406.373 | 1742.9053 | 2044.058 | 2342.668 | 2619.084 | 2903.3502 | 3190.219 | 3508.625 | 3856.0298 | 4196.8475 | 4539.1265 | 4878.833 | 5215.9775 | 5550.12 | 5882.4265 | 6350.836 | 6817.633 | 7282.5715 | 7610.119 | 7936.4395 | 8264.314 | 8591.965 | 8919.87 | 9248.368 | 9577.724
SA | 0 | 22.7689 | 58.293 | 122.6533 | 197.4484 | 312.7426 | 400.7018 | 486.0728 | 557.4338 | 626.081 | 685.6513 | 748.7064 | 810.3564 | 878.429 | 947.5701 | 1017.7289 | 1119.7648 | 1220.5258 | 1319.8802 | 1418.3754 | 1516.1372 | 1666.1569 | 1815.5407 | 1964.1933 | 2059.4074 | 2154.0365 | 2249.5665 | 2344.9995 | 2440.4153 | 2535.9455 | 2631.6645
TAS | 0 | 8.8789 | 25.4513 | 51.0536 | 79.9065 | 113.3178 | 148.2803 | 182.0059 | 210.5062 | 240.0129 | 267.103 | 293.0469 | 320.4123 | 348.3506 | 383.9287 | 419.2856 | 455.2884 | 491.2847 | 527.2171 | 563.2626 | 599.4026 | 649.227 | 699.1589 | 749.2419 | 786.0315 | 823.0322 | 860.6202 | 898.5733 | 936.8932 | 975.6096 | 1014.7209
VIC | 0 | 83.2461 | 219.4517 | 422.3432 | 710.1665 | 1022.4601 | 1314.5719 | 1597.0219 | 1808.9848 | 1997.3465 | 2147.3015 | 2522.2832 | 2904.5445 | 3321.0278 | 3783.4215 | 4238.8605 | 4699.348 | 5156.8705 | 5610.7645 | 6060.85 | 6507.848 | 7122.8565 | 7738.045 | 8352.1025 | 8795.247 | 9235.817 | 9676.432 | 10116.717 | 10557.891 | 11000.944 | 11446.834
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 0 | 128.4977 | 410.6242 | 848.125 | 1295.3222 | 1791.4469 | 2289.5723 | 2781.652 | 3234.0172 | 3695.8958 | 4131.1947 | 4595.032 | 5071.303 | 5580.497 | 6127.965 | 6665.2555 | 7217.522 | 7774.52 | 8339.4255 | 8914.518 | 9502.526 | 10353.573 | 11216.277 | 12086.904 | 13218.668 | 14363.288 | 14865.875 | 15370.988 | 15878.195 | 16387.31 | 16898.074
QLD | 0 | 95.7396 | 289.168 | 618.5966 | 975.2036 | 1371.9143 | 1762.586 | 2144.2252 | 2489.5613 | 2838.2865 | 3169.9605 | 3528.8223 | 3894.2945 | 4294.158 | 4719.986 | 5141.246 | 5566.0825 | 5990.2265 | 6412.594 | 6831.887 | 7250.371 | 7855.44 | 8459.678 | 9062.649 | 9850.251 | 10638.062 | 11061.854 | 11487.106 | 11914.011 | 12342.528 | 12772.839
SA | 0 | 26.823 | 77.6312 | 174.9669 | 277.4592 | 417.7911 | 519.8963 | 616.6548 | 699.2673 | 781.7054 | 856.7857 | 941.0888 | 1024.7586 | 1114.919 | 1203.3296 | 1292.424 | 1418.6185 | 1544.0521 | 1668.2023 | 1791.3856 | 1913.7859 | 2104.419 | 2294.6825 | 2482.6745 | 2735.861 | 2984.9817 | 3107.254 | 3229.5642 | 3352.0057 | 3474.646 | 3597.5023
TAS | 0 | 9.8797 | 30.1781 | 63.799 | 98.8892 | 137.6979 | 177.1209 | 214.2779 | 245.7647 | 279.0285 | 310.1243 | 341.7168 | 375.4778 | 409.947 | 452.1355 | 494.3781 | 537.6337 | 581.0658 | 624.517 | 668.1632 | 712.099 | 774.5296 | 837.259 | 900.1539 | 981.5006 | 1063.0976 | 1109.2828 | 1156.0195 | 1203.263 | 1251.046 | 1299.384
VIC | 0 | 97.7368 | 291.7994 | 617.4411 | 1003.3314 | 1402.6962 | 1765.1345 | 2101.69 | 2365.5925 | 2616.8252 | 2837.4895 | 3299.7922 | 3777.2013 | 4294.139 | 4861.613 | 5425.006 | 5997.034 | 6568.3415 | 7137.8945 | 7705.0095 | 8272.6075 | 9062.36 | 9854.692 | 10648.638 | 11664.736 | 12684.903 | 13267.17 | 13851.875 | 14440.052 | 15032.215 | 15629.22
Reduced Energy Efficiency (Sensitivity)
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 0 | 91.3716 | 270.4413 | 520.2736 | 802.3522 | 1125.2158 | 1456.6805 | 1787.0332 | 2075.6724 | 2360.8173 | 2613.8077 | 2790.084 | 2972.6588 | 3125.7245 | 3408.426 | 3681.4307 | 3965.546 | 4255.7465 | 4555.6405 | 4864.2765 | 5182.295 | 5507.428 | 5840.2195 | 6179.647 | 6525.1435 | 6878.1465 | 7143.964 | 7410.8345 | 7678.798 | 7947.9295 | 8218.23
QLD | 0 | 63.848 | 179.6734 | 360.0114 | 576.8647 | 827.1751 | 1082.231 | 1329.5241 | 1540.3099 | 1750.7769 | 1941.5441 | 2082.8864 | 2229.7555 | 2357.1825 | 2575.6957 | 2790.5482 | 3006.558 | 3220.968 | 3433.7975 | 3644.8733 | 3854.6557 | 4063.2672 | 4270.651 | 4476.799 | 4681.861 | 4885.939 | 5089.171 | 5291.7265 | 5493.732 | 5695.267 | 5896.3895
SA | 0 | 17.5971 | 43.7415 | 90.8293 | 144.3263 | 226.1342 | 294.1476 | 358.7314 | 409.4245 | 458.0598 | 498.5803 | 523.2909 | 549.7065 | 570.3354 | 618.2649 | 669.9543 | 738.1002 | 805.4486 | 871.9589 | 937.8806 | 1003.2637 | 1068.0426 | 1132.3038 | 1196.082 | 1259.3416 | 1322.161 | 1384.7215 | 1447.0114 | 1509.0571 | 1570.8982 | 1632.5538
TAS | 0 | 7.7216 | 22.3141 | 44.7898 | 70.6218 | 99.9594 | 130.4289 | 159.5097 | 183.3404 | 208.1651 | 230.6876 | 246.1849 | 263.2366 | 278.059 | 306.7614 | 335.3788 | 364.4249 | 393.5186 | 422.629 | 451.8574 | 481.1927 | 510.6023 | 540.1458 | 569.855 | 599.7096 | 629.7382 | 660.0262 | 690.5729 | 721.3806 | 752.4674 | 783.8344
VIC | 0 | 65.174 | 168.187 | 325.0864 | 555.3958 | 794.6528 | 1012.4588 | 1217.9376 | 1355.3077 | 1473.1357 | 1556.4474 | 1773.9205 | 1999.5545 | 2200.6095 | 2520.0392 | 2835.8125 | 3155.6045 | 3474.1332 | 3791.0705 | 4106.2115 | 4419.8725 | 4732.922 | 5045.765 | 5357.826 | 5668.851 | 5978.975 | 6288.1415 | 6597.4645 | 6907.4665 | 7218.558 | 7531.123

## Rooftop PV
Go to Assumptions Summary
Distributed Energy Resources: Rooftop PV | [8 empty] | Note: | Further information is available at https://forecasting.aemo.com.au
Rooftop PV forecasts based on CSIRO and Green Energy Markets (GEM) trajectories that were developed for AEMO in 2022.
AEMO has rebased the Rooftop PV forecasts in March 2023 using data from the Clean Energy Regulator (CER).
The Capacity values (MW) represent the installed capacity at the end of the financial year i.e. as at 30th June. Energy values (GWh) present the total production across the year of interest, which captures Rooftop PV growth throughout the financial year.
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | CSIRO Progressive Change | Average CSIRO/GEM Step Change | GEM Hydrogen Export
Rooftop PV (Capacity, MW)
Capacity of behind-the-meter rooftop PV
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 5954.0151 | 6157.6245 | 6361.2344 | 6624.5088 | 7122.3032 | 7629.103 | 8161.1011 | 8574.4834 | 8975.1318 | 9330.5068 | 9659.2139 | 9936.667 | 10150.4932 | 10298.3076 | 10432.1211 | 10566.1348 | 10698.501 | 10830.668 | 10964.7559 | 11100.7949 | 11238.0195 | 11376.7012 | 11517.3184 | 11659.8184 | 11804.4219 | 11951.8398 | 12105.0898 | 12261.3232 | 12429.082 | 12641.5186 | 12896.3057
QLD | 5624.8779 | 5812.7236 | 6000.5698 | 6209.6782 | 6503.8789 | 6798.5752 | 7100.7119 | 7378.3662 | 7642.0571 | 7873.2202 | 8090.897 | 8281.5029 | 8444.2979 | 8586.5244 | 8729.9971 | 8879.2412 | 9030.4834 | 9184.332 | 9340.5693 | 9499.1885 | 9659.8916 | 9822.7891 | 9988.165 | 10156.1465 | 10326.7637 | 10506.207 | 10702.6475 | 10909.752 | 11121.2764 | 11339.7227 | 11563.6816
SA | 2220.105 | 2277.3125 | 2334.5203 | 2400.937 | 2501.322 | 2600.187 | 2700.0271 | 2791.156 | 2874.783 | 2943.584 | 3006.0039 | 3057.5691 | 3098.946 | 3135.1211 | 3172.2251 | 3210.7461 | 3249.752 | 3289.252 | 3329.313 | 3369.8611 | 3410.937 | 3452.532 | 3494.6941 | 3537.4131 | 3580.678 | 3624.6389 | 3669.9121 | 3716.8511 | 3765.1001 | 3815.4021 | 3866.7451
TAS | 270.2875 | 280.6793 | 291.071 | 307.299 | 345.979 | 385.945 | 428.616 | 456.219 | 484.603 | 512.716 | 539.749 | 563.072 | 578.158 | 584.961 | 590.001 | 594.563 | 599.487 | 604.43 | 609.3 | 614.178 | 619.072 | 624.017 | 629.066 | 634.175 | 639.298 | 644.524 | 649.842 | 655.316 | 660.838 | 666.637 | 673.394
VIC | 4563.4292 | 5060.2432 | 5557.0571 | 6073.1709 | 6662.8599 | 7132.0122 | 7628.4639 | 7996.228 | 8365.0605 | 8716.2949 | 9055.1416 | 9363.2559 | 9620.4336 | 9814.4814 | 9985.4297 | 10137.9619 | 10282.0215 | 10432.5391 | 10583.4902 | 10736.2754 | 10891.6631 | 11049.2412 | 11209.5391 | 11374.9805 | 11574.0352 | 11800.0449 | 12031.5742 | 12261.9473 | 12495.7461 | 12745.9229 | 13027.877
Step Change | bar: 2052-53 to 2053-54
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 6467.4541 | 7081.1406 | 7694.8276 | 8360.2363 | 9249.9561 | 10121.4141 | 10996.7119 | 11748.1162 | 12468.7881 | 13203.5947 | 13933.9189 | 14673.9463 | 15413.5908 | 16038.9238 | 16642.9512 | 17234.3379 | 17821.6641 | 18389.5742 | 18948.4023 | 19502.5566 | 20050.7188 | 20697.168 | 21421.7656 | 22123.8535 | 22856.4316 | 23601.7773 | 24355.9727 | 25103.2559 | 25851.0371 | 26598.6172 | 27345.752
QLD | 5977.1318 | 6446.3184 | 6915.5054 | 7400.1812 | 7992.8643 | 8598.0928 | 9245.4355 | 9836.0869 | 10392.2549 | 10945.4707 | 11498.3369 | 12043.8496 | 12583.416 | 13035.96 | 13469.0283 | 13880.0693 | 14296.9229 | 14724.1484 | 15156.4365 | 15587.0586 | 16025.9551 | 16527.6934 | 17080.4863 | 17612.5703 | 18168.668 | 18754.2969 | 19346.7598 | 19922.373 | 20499.1543 | 21075.6133 | 21651.7988
SA | 2320.7375 | 2458.3188 | 2595.9001 | 2746.3091 | 2955.4524 | 3165.9246 | 3386.3306 | 3584.6289 | 3772.5154 | 3958.8855 | 4145.4526 | 4330.6836 | 4510.77 | 4659.3369 | 4806.9766 | 4954.2588 | 5098.8535 | 5234.4756 | 5366.3428 | 5498.8604 | 5631.4312 | 5786.7891 | 5959.0986 | 6121.1997 | 6286.6411 | 6457.4043 | 6631.2642 | 6801.8799 | 6971.832 | 7140.6885 | 7308.1919
TAS | 296.2101 | 327.306 | 358.4018 | 393.066 | 441.3755 | 491.323 | 541.7755 | 583.536 | 624.853 | 666.89 | 710.138 | 754.415 | 799.7975 | 841.508 | 883.936 | 926.99 | 969.9675 | 1011.6595 | 1053.334 | 1092.3895 | 1128.6965 | 1169.8571 | 1215.748 | 1260.6095 | 1306.38 | 1352.9015 | 1399.8035 | 1443.6775 | 1487.1475 | 1530.2625 | 1573.1935
VIC | 4687.8315 | 5284.0044 | 5880.1772 | 6484.1714 | 7149.0132 | 7741.4805 | 8342.6172 | 8861.7441 | 9372.3242 | 9896.2246 | 10434.9414 | 10988.3779 | 11563.1943 | 12089.8613 | 12624.0176 | 13168.041 | 13715.3838 | 14255.2754 | 14790.709 | 15308.4355 | 15823.9707 | 16417.2559 | 17079.6172 | 17727.5977 | 18401.5586 | 19097.0176 | 19818.9648 | 20532.4922 | 21248.2695 | 21966.2969 | 22686.5684
Green Energy Exports | bar: 2052-53 to 2053-54
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 6559.4648 | 7246.6392 | 7933.8135 | 8677.3398 | 9873.1611 | 11105.8926 | 12472.0215 | 13610.8105 | 14707.9307 | 15770.7178 | 16739.2168 | 17619.8262 | 18424.8672 | 19004.793 | 19539.9258 | 20075.8965 | 20626.6309 | 21210.9629 | 21808.375 | 22427.5918 | 23059.5332 | 23696.6543 | 24350.1992 | 24934.0508 | 25555.1484 | 26195.8906 | 26863.8203 | 27554.0352 | 28240.3164 | 28918.0586 | 29587.3008
QLD | 6058.7134 | 6593.0586 | 7127.4033 | 7704.2979 | 8640.2646 | 9610.415 | 10666.748 | 11561.0957 | 12401.2373 | 13220.8926 | 13985.2949 | 14662.1025 | 15287.5293 | 15720.5928 | 16133.6973 | 16528.8652 | 16942.8418 | 17373.6738 | 17826.2188 | 18297.293 | 18789.7773 | 19286.416 | 19802.6602 | 20243.7656 | 20707.7656 | 21196.5352 | 21687.2793 | 22203.4883 | 22716.8828 | 23223.9551 | 23724.7344
SA | 2332.7283 | 2479.8865 | 2627.0447 | 2792.3459 | 3095.542 | 3431.615 | 3814.1299 | 4125.6992 | 4416.9722 | 4684.9258 | 4933.5469 | 5159.5532 | 5367.79 | 5520.5698 | 5671.2261 | 5819.7002 | 5970.939 | 6133.3691 | 6304.8159 | 6487.0679 | 6672.2461 | 6866.019 | 7070.4902 | 7245.4321 | 7430.4209 | 7625.1528 | 7825.248 | 8037.917 | 8249.3262 | 8458.3037 | 8664.8623
TAS | 289.7114 | 315.6168 | 341.5222 | 369.906 | 418.539 | 474.816 | 539.16 | 595.315 | 648.262 | 699.558 | 748.188 | 793.43 | 836.127 | 868.64 | 899.886 | 930.629 | 961.642 | 994.467 | 1029.875 | 1067.454 | 1106.257 | 1145.71 | 1185.806 | 1222.837 | 1260.5439 | 1298.866 | 1337.635 | 1377.623 | 1417.395 | 1456.757 | 1495.708
VIC | 4680.5161 | 5270.8462 | 5861.1763 | 6452.7041 | 7138.48 | 7833.8442 | 8623.6758 | 9305.6797 | 9922.7188 | 10517.0654 | 11084.1387 | 11603.6445 | 12105.2744 | 12491.9199 | 12871.0889 | 13246.8672 | 13634.0684 | 14045.6064 | 14496.4697 | 14972.2344 | 15478.04 | 16002.3213 | 16540.4453 | 17034.8223 | 17548.1465 | 18079.5547 | 18626.9707 | 19199.3535 | 19768.5137 | 20331.5527 | 20888.5078
Rooftop PV (Energy, GWh) | bar: 2053-54
Amount of energy generated by behind-the-meter rooftop PV | bar: 2053-54
Progressive Change | bar: 2052-53 to 2053-54
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 7219.123 | 7462.9224 | 7705.9907 | 7964.0679 | 8479.0908 | 9089.0762 | 9719.3193 | 10302.3232 | 10826.335 | 11281.1289 | 11690.9678 | 12064.5938 | 12393.4648 | 12603.8076 | 12764.2598 | 12929.1895 | 13120.6299 | 13269.9004 | 13420.0684 | 13586.3926 | 13783.4307 | 13939.0039 | 14096.5098 | 14270.832 | 14477.8359 | 14642.6016 | 14812.5107 | 15003.0615 | 15234.293 | 15452.2715 | 15723.6533
QLD | 7208.3535 | 7439.7271 | 7680.5884 | 7927.9482 | 8285.5361 | 8653.1279 | 9037.2178 | 9414.5361 | 9789.7168 | 10093.6504 | 10380.9609 | 10646.751 | 10902.3779 | 11080.7012 | 11261.2832 | 11451.6582 | 11674.4033 | 11851.0967 | 12047.1533 | 12251.917 | 12488.8164 | 12676.0381 | 12883.5342 | 13100.3291 | 13351.7783 | 13554.5293 | 13792.4141 | 14054.7686 | 14360.6221 | 14613.4912 | 14894.2803
SA | 2759.1545 | 2832.0093 | 2898.4265 | 2971.3271 | 3086.6101 | 3212.812 | 3331.4954 | 3451.4895 | 3567.354 | 3664.1699 | 3739.5122 | 3811.1177 | 3876.0789 | 3925.876 | 3964.2983 | 4011.8396 | 4067.4688 | 4117.9258 | 4159.917 | 4210.582 | 4269.1284 | 4322.2588 | 4366.4907 | 4419.8413 | 4481.4883 | 4537.5405 | 4584.7974 | 4642.7578 | 4710.5796 | 4773.8213 | 4828.4204
TAS | 286.4906 | 298.0046 | 308.5031 | 320.21 | 352.9773 | 395.812 | 439.4646 | 477.4461 | 508.4446 | 539.4468 | 567.921 | 595.1163 | 616.8342 | 629.2531 | 634.1229 | 639.3052 | 645.4239 | 651.333 | 655.047 | 660.308 | 666.6133 | 672.5261 | 676.2864 | 681.7687 | 688.3549 | 694.5618 | 698.566 | 704.3907 | 711.4258 | 718.1795 | 723.2078
VIC | 4850.126 | 5413.1338 | 5959.2612 | 6518.8467 | 7162.9595 | 7763.0552 | 8288.2695 | 8773.1914 | 9201.2656 | 9612.166 | 9978.3984 | 10341.5596 | 10675.6875 | 10936.2646 | 11116.8975 | 11298.4873 | 11483.1416 | 11656.3027 | 11799.6982 | 11970.2373 | 12162.4834 | 12346.3916 | 12497.4727 | 12680.3691 | 12905.4395 | 13152.8867 | 13380.6406 | 13639.9893 | 13922.6123 | 14203.8516 | 14471.1895
Step Change | bar: 2052-53 to 2053-54
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 7593.2949 | 8342.9111 | 9090.2793 | 9852.1104 | 10867.5977 | 11941.1455 | 13005.0371 | 14006.458 | 14934.5342 | 15815.668 | 16702.0059 | 17607.5293 | 18557.9609 | 19381.6191 | 20119.123 | 20855.502 | 21626.7656 | 22316.082 | 22987.082 | 23672.4609 | 24402.4434 | 25112.4336 | 25930.3262 | 26809.6836 | 27750.9238 | 28632.3516 | 29526.1777 | 30450.6426 | 31436.9746 | 32325.4199 | 33212.5039
QLD | 7479.5674 | 8077.0439 | 8683.6621 | 9295.9502 | 10034.7471 | 10795.2764 | 11605.375 | 12410.3604 | 13179.4648 | 13876.7148 | 14589.833 | 15304.5176 | 16048.292 | 16665.2754 | 17233.9121 | 17783.2988 | 18364.752 | 18879.2754 | 19429.3926 | 19990.6543 | 20604.3945 | 21177.502 | 21853.1094 | 22559.2285 | 23321.4883 | 24020.3027 | 24775.2246 | 25535.125 | 26346.3633 | 27047.4277 | 27784.4199
SA | 2834.9375 | 3009.1763 | 3176.3298 | 3350.5825 | 3592.7517 | 3857.8503 | 4121.5796 | 4384.2529 | 4631.7686 | 4868.5923 | 5093.6553 | 5327.3984 | 5566.5845 | 5775.0439 | 5950.1016 | 6135.5166 | 6329.7271 | 6507.7314 | 6663.2573 | 6829.4536 | 7007.9775 | 7191.0923 | 7383.1177 | 7593.4995 | 7812.6206 | 8026.2056 | 8227.2246 | 8443.7061 | 8672.4561 | 8887.9277 | 9082.082
TAS | 303.1337 | 337.0952 | 369.8603 | 403.7151 | 451.2597 | 504.803 | 557.8326 | 607.5994 | 652.9285 | 698.5867 | 742.9448 | 790.1888 | 839.8921 | 887.7892 | 931.0753 | 977.2179 | 1025.246 | 1071.9436 | 1114.3588 | 1157.9365 | 1200.4751 | 1243.4027 | 1287.365 | 1336.3828 | 1387.4366 | 1438.5679 | 1485.5137 | 1534.5238 | 1584.1151 | 1632.344 | 1674.8398
VIC | 4933.6074 | 5608.6372 | 6265.9619 | 6935.9102 | 7672.9072 | 8384.2197 | 9036.4385 | 9664.7998 | 10253.6064 | 10842.1719 | 11415.0957 | 12028.458 | 12682.1768 | 13310.2979 | 13876.7646 | 14482.2373 | 15118.9932 | 15740.3125 | 16309.3896 | 16900.6348 | 17508.4414 | 18143.6543 | 18808.8145 | 19544.8164 | 20319.2031 | 21102.6914 | 21852.0234 | 22658.0332 | 23497.6016 | 24319.2207 | 25073.0547
Green Energy Exports | bar: 2052-53 to 2053-54
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 7660.3486 | 8500.6094 | 9338.3496 | 10191.0234 | 11454.3574 | 12939.0146 | 14527.2314 | 16068.5791 | 17457.1348 | 18770.4785 | 20004.0879 | 21144.5781 | 22231.4258 | 23065.8203 | 23729.7676 | 24389.6445 | 25111.5977 | 25784.5312 | 26485.8574 | 27235.0547 | 28064.4258 | 28817.1348 | 29582.3926 | 30345.4609 | 31152.5156 | 31897.5605 | 32670.4277 | 33506.8477 | 34426.4062 | 35230.8555 | 36023.9531
QLD | 7542.3804 | 8224.6455 | 8915.9727 | 9616.6826 | 10660.127 | 11880.3545 | 13193.5322 | 14461.6367 | 15606.7979 | 16657.752 | 17681.4863 | 18620.6562 | 19514.877 | 20170.9199 | 20712.3086 | 21238.375 | 21815.6445 | 22324.4688 | 22888.3438 | 23488.9414 | 24172.0938 | 24770.5781 | 25417.5859 | 26041.709 | 26692.7148 | 27262.5742 | 27886.8809 | 28541.5547 | 29279.7871 | 29889.1016 | 30530.5879
SA | 2843.9673 | 3030.2864 | 3209.4429 | 3396.2427 | 3713.3811 | 4117.4771 | 4562.2632 | 4997.0903 | 5377.5479 | 5731.1279 | 6044.9351 | 6343.4785 | 6628.0273 | 6857.3535 | 7034.918 | 7223.0552 | 7424.1245 | 7623.5542 | 7818.7476 | 8041.1504 | 8286.2422 | 8527.001 | 8760.9268 | 8999.4355 | 9241.4512 | 9482.9307 | 9712.8379 | 9972.4043 | 10256.3174 | 10523.5225 | 10764.2578
TAS | 298.9613 | 327.2953 | 354.4783 | 382.6313 | 426.8577 | 484.071 | 548.1369 | 613.076 | 671.7859 | 728.7816 | 781.0121 | 831.7291 | 880.6175 | 922.2042 | 954.427 | 987.9058 | 1022.8378 | 1058.2661 | 1092.5294 | 1131.9203 | 1174.9574 | 1218.3175 | 1258.312 | 1299.9935 | 1342.4065 | 1384.712 | 1422.9731 | 1465.4689 | 1510.8502 | 1554.9827 | 1593.4907
VIC | 4928.6982 | 5597.1406 | 6247.9268 | 6910.5679 | 7655.1553 | 8437.5039 | 9254.6904 | 10079.2842 | 10811.2363 | 11499.8838 | 12127.0088 | 12737.5166 | 13332.6035 | 13841.626 | 14241.2881 | 14665.3594 | 15117.8584 | 15577.1348 | 16027.1104 | 16547.5195 | 17125.8652 | 17716.416 | 18273.9492 | 18853.9902 | 19450.6152 | 20050.9043 | 20612.3867 | 21241.1973 | 21916.6758 | 22567.5977 | 23146.4707

## PVNSG
Go to Assumptions Summary
Distributed Energy Resources: Small-scale non-scheduled generation (PVNSG) | [13 empty] | Note: | Further information is available at https://forecasting.aemo.com.au
PVNSG trajectories based on CSIRO and Green Energy Markets (GEM) forecasts that were developed for AEMO in 2022.
AEMO has rebased the PVNSG forecasts in March 2023 using a combination of data from the Australian Photovoltaic Institute, Clean Energy Regulator (CER) and AEMO's DER Register.
The Capacity values (MW) represent the installed capacity at the end of the financial year i.e. as at 30th June. Energy values (GWh) present the total production across the year of interest, which captures PVNSG growth throughout the financial year.
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | CSIRO Progressive Change | GEM Step Change | GEM Hydrogen Export
PVNSG (Capacity, MW)
Capacity of small-scale non-scheduled generating PV systems
Progressive Change
Progressive Change | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 333.3927 | 341.1779 | 348.9631 | 358.148 | 377.951 | 397.556 | 434.013 | 445.557 | 464.486 | 483.225 | 518.827 | 529.522 | 547.611 | 565.518 | 600.297 | 610.177 | 627.461 | 644.57 | 678.557 | 687.655 | 704.163 | 720.505 | 753.734 | 762.081 | 777.844 | 793.449 | 825.947 | 833.573 | 848.62 | 863.518 | 895.317
QLD | 254.6718 | 270.2682 | 285.8647 | 300.103 | 309.451 | 326.206 | 352.342 | 368.668 | 377.33 | 393.406 | 418.87 | 434.532 | 442.534 | 457.958 | 482.778 | 497.799 | 505.171 | 519.967 | 544.167 | 558.573 | 565.337 | 579.533 | 603.136 | 616.953 | 623.133 | 636.751 | 659.782 | 673.033 | 678.652 | 691.714 | 714.196
SA | 247.9255 | 251.897 | 255.8684 | 260.694 | 274.998 | 289.159 | 320.227 | 333.937 | 347.508 | 360.944 | 391.294 | 404.293 | 417.161 | 429.899 | 459.561 | 471.876 | 484.068 | 496.138 | 525.138 | 536.797 | 548.34 | 559.768 | 588.131 | 599.16 | 610.079 | 620.889 | 648.64 | 659.065 | 669.385 | 679.602 | 706.766
TAS | 5.172 | 6.1316 | 7.0913 | 7.789 | 8.189 | 8.586 | 11.478 | 11.363 | 11.728 | 12.089 | 14.946 | 14.797 | 15.128 | 15.454 | 18.278 | 18.095 | 18.393 | 18.687 | 21.479 | 21.263 | 21.529 | 21.793 | 24.553 | 24.307 | 24.542 | 24.775 | 27.506 | 27.23 | 27.437 | 27.641 | 30.343
VIC | 383.1517 | 413.2216 | 443.2916 | 475.204 | 493.363 | 528.391 | 546.018 | 580.519 | 597.624 | 631.609 | 648.204 | 681.684 | 697.779 | 730.761 | 746.364 | 778.863 | 793.985 | 826.006 | 840.657 | 872.212 | 886.4 | 917.499 | 931.233 | 961.883 | 975.174 | 1005.384 | 1018.241 | 1048.02 | 1060.452 | 1089.808 | 1101.8199
Step Change
Step Change | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 471.3261 | 589.4581 | 707.59 | 821.845 | 906.617 | 1035.004 | 1144.4919 | 1256.037 | 1369.239 | 1528.389 | 1631.739 | 1761.213 | 1871.007 | 2039.229 | 2215.123 | 2412.842 | 2618.0471 | 2801.634 | 3003.844 | 3182.803 | 3365.3601 | 3550.96 | 3730.623 | 3915.4509 | 4106.9468 | 4289.6841 | 4477.7471 | 4663.3662 | 4850.083 | 5043.5308 | 5239.354
QLD | 328.8318 | 403.7562 | 478.6807 | 556.584 | 630.579 | 742.567 | 838.167 | 935.957 | 1034.131 | 1175.303 | 1259.457 | 1369.734 | 1461.269 | 1607.322 | 1756.5129 | 1927.053 | 2097.895 | 2250.345 | 2425.6001 | 2580.48 | 2738.7671 | 2895.0081 | 3051.645 | 3206.957 | 3370.739 | 3525.656 | 3687.4651 | 3846.0439 | 4008.4141 | 4168.415 | 4332.3179
SA | 283.6358 | 316.1755 | 348.7152 | 380.711 | 417.865 | 464.549 | 507.812 | 551.717 | 596.657 | 652.123 | 701.322 | 756.791 | 806.524 | 867.849 | 929.964 | 995.132 | 1063.125 | 1127.29 | 1195.228 | 1259.618 | 1324.726 | 1389.2581 | 1453.51 | 1520.423 | 1589.473 | 1659.734 | 1731.657 | 1801.037 | 1870.446 | 1940.291 | 2009.236
TAS | 12.5698 | 19.4477 | 26.3256 | 33.313 | 36.039 | 44.999 | 50.88 | 56.79 | 63.248 | 75.683 | 79.3 | 86.051 | 89.649 | 102.032 | 114.367 | 129.957 | 145.431 | 157.993 | 173.15 | 185.31 | 197.975 | 210.212 | 222.348 | 234.387 | 246.936 | 258.802 | 270.755 | 282.332 | 294.601 | 306.874 | 319.938
VIC | 462.4655 | 555.9864 | 649.5073 | 739.188 | 813.356 | 916.446 | 1007.72 | 1100.526 | 1194.676 | 1336.765 | 1439.969 | 1561.786 | 1669.99 | 1825.689 | 1985.327 | 2156.3879 | 2328.04 | 2484.8589 | 2665.0591 | 2830.2649 | 2997.937 | 3163.9871 | 3329.667 | 3494.8611 | 3667.522 | 3842.3721 | 4021.605 | 4198.4458 | 4376.7422 | 4557.791 | 4736.5742
Green Energy Exports
Green Energy Exports | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 503.0587 | 646.5766 | 790.0945 | 950.07 | 1147.141 | 1373.615 | 1510.948 | 1733.687 | 1853.418 | 2061.4771 | 2289.0249 | 2676.2849 | 2908.696 | 3116.1079 | 3500.958 | 3779.7959 | 3889.1211 | 4189.1138 | 4812.6851 | 5130.022 | 5448.8579 | 5757.2861 | 6073.0181 | 6376.9712 | 6691.1211 | 7003.3789 | 7333.7061 | 7647.439 | 7953.2969 | 8283.1465 | 8600.8281
QLD | 357.5705 | 455.486 | 553.4014 | 671.84 | 841.719 | 1031.042 | 1149.934 | 1342.856 | 1445.7629 | 1626.9821 | 1824.0179 | 2147.386 | 2337.0601 | 2507.5039 | 2824.3259 | 3052.894 | 3138.926 | 3387.0559 | 3915.1321 | 4177.918 | 4441.5659 | 4697.1548 | 4959.6011 | 5210.8799 | 5473.3179 | 5733.3198 | 6004.7949 | 6260.7251 | 6512.293 | 6780.376 | 7040.3062
SA | 296.7046 | 339.6993 | 382.694 | 430.772 | 493.631 | 564.827 | 616 | 685.485 | 733.932 | 802.157 | 877.661 | 985.558 | 1060.9969 | 1131.433 | 1237.516 | 1320.5 | 1368.907 | 1456.578 | 1609.954 | 1703.842 | 1798.129 | 1890.021 | 1983.215 | 2074.1299 | 2167.8679 | 2263.958 | 2364.134 | 2458.9099 | 2551.8711 | 2649.0039 | 2742.114
TAS | 16.4554 | 26.4418 | 36.4282 | 49.42 | 68.613 | 91.133 | 100.71 | 122.526 | 128.721 | 147.282 | 168.759 | 210.934 | 231.668 | 249.107 | 289.563 | 315.615 | 318.548 | 347.041 | 418.275 | 447.812 | 477.297 | 505.078 | 533.676 | 560.269 | 587.758 | 615.3 | 644.468 | 671.205 | 697.203 | 725.437 | 752.588
VIC | 489.618 | 604.8609 | 720.1038 | 845.13 | 1001.826 | 1180.931 | 1308.123 | 1491.194 | 1608.0909 | 1784.698 | 1969.074 | 2261.8601 | 2450.23 | 2622.447 | 2909.2219 | 3123.791 | 3228.4209 | 3468.8059 | 3924.2891 | 4172.9419 | 4423.3428 | 4668.041 | 4917.6602 | 5159.9771 | 5410.895 | 5671.8999 | 5946.0898 | 6208.6592 | 6456.8271 | 6719.106 | 6969.6069
PVNSG (Energy, GWh)
Amount of energy generated by small-scale non-scheduled generating PV systems
Progressive Change
Progressive Change | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 599.9721 | 612.4407 | 626.5682 | 641.0121 | 670.3334 | 704.2222 | 755.5663 | 798.4065 | 828.5668 | 860.4423 | 910.2244 | 951.5177 | 980.5658 | 1010.5059 | 1058.7877 | 1098.5957 | 1126.575 | 1154.6566 | 1201.4971 | 1239.8782 | 1266.8306 | 1293.1281 | 1338.5833 | 1375.5935 | 1401.5597 | 1426.1432 | 1470.2678 | 1505.9617 | 1530.9791 | 1553.9161 | 1596.7638
QLD | 479.533 | 508.4438 | 538.6154 | 568.4222 | 591.3706 | 615.2417 | 656.9452 | 697.7911 | 723.6765 | 745.8826 | 786.2793 | 825.8317 | 850.7679 | 871.376 | 910.5178 | 948.8279 | 972.8516 | 991.9238 | 1029.8607 | 1066.9775 | 1090.1245 | 1107.722 | 1144.5007 | 1180.4702 | 1202.7765 | 1218.9573 | 1254.6232 | 1289.4923 | 1310.9894 | 1325.8085 | 1360.4071
SA | 465.1095 | 471.0899 | 478.5722 | 486.2344 | 506.8762 | 532.0401 | 575.3201 | 616.8102 | 644.5894 | 667.9375 | 709.8583 | 750.0042 | 776.8777 | 798.4807 | 839.0966 | 877.9488 | 903.9517 | 923.8794 | 963.2419 | 1000.8518 | 1026.0192 | 1044.3374 | 1082.4952 | 1118.9127 | 1143.2764 | 1160.049 | 1197.0496 | 1232.3223 | 1255.9142 | 1271.2007 | 1307.0895
TAS | 7.5092 | 9.0041 | 10.5254 | 12.0065 | 12.7202 | 13.3083 | 15.988 | 18.1022 | 18.3773 | 18.8891 | 21.5128 | 23.5717 | 23.8108 | 24.25 | 26.82 | 28.8263 | 29.0303 | 29.3994 | 31.9181 | 33.8732 | 34.044 | 34.3465 | 36.8155 | 38.7211 | 38.8601 | 39.0977 | 41.5196 | 43.3785 | 43.4864 | 43.6625 | 46.0386
VIC | 625.4564 | 674.1452 | 724.9241 | 776.0399 | 821.2431 | 864.0394 | 907.8613 | 952.4925 | 998.7438 | 1039.1848 | 1081.2552 | 1124.1527 | 1169.2506 | 1207.4299 | 1247.8174 | 1289.0492 | 1333.0387 | 1369.0446 | 1407.8159 | 1447.448 | 1490.3727 | 1524.2908 | 1561.5101 | 1599.605 | 1641.5074 | 1673.4203 | 1709.1481 | 1745.7667 | 1786.6869 | 1816.673 | 1850.9688
Step Change
Step Change | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 756.0992 | 968.3021 | 1182.671 | 1396.1603 | 1576.9635 | 1768.1638 | 1983.0403 | 2183.6541 | 2393.9734 | 2634.6255 | 2872.6895 | 3085.8425 | 3310.5457 | 3555.8245 | 3868.9641 | 4209.0552 | 4587.8037 | 4926.6875 | 5277.6714 | 5622.3452 | 5967.1113 | 6284.7324 | 6615.8066 | 6946.4189 | 7306.3682 | 7627.9199 | 7965.2139 | 8303.5469 | 8664.7197 | 8986.5117 | 9339.8291
QLD | 568.5128 | 711.9199 | 856.8626 | 1002.6 | 1154.7223 | 1333.2798 | 1533.3265 | 1720.8422 | 1915.0966 | 2145.3064 | 2358.9792 | 2548.6833 | 2749.6338 | 2974.9495 | 3260.4822 | 3570.7151 | 3911.2507 | 4212.8057 | 4530.8188 | 4849.2197 | 5165.8643 | 5456.4253 | 5759.437 | 6060.7402 | 6388.3462 | 6677.7554 | 6984.877 | 7293.9927 | 7624.8535 | 7916.3882 | 8229.8652
SA | 507.4256 | 567.0701 | 628.376 | 689.5672 | 757.1141 | 834.2292 | 918.7425 | 1000.8736 | 1088.101 | 1178.6655 | 1276.8348 | 1378.1803 | 1478.9001 | 1583.1747 | 1697.5364 | 1817.6349 | 1949.5923 | 2067.5061 | 2192.1895 | 2316.6172 | 2446.5886 | 2560.7395 | 2682.0151 | 2805.6694 | 2942.2703 | 3064.0195 | 3200.4119 | 3330.543 | 3476.2588 | 3594.238 | 3724.9233
TAS | 14.8493 | 25.6968 | 36.6003 | 47.5206 | 55.293 | 64.6588 | 76.2763 | 85.637 | 95.7856 | 110.7143 | 123.1023 | 131.3804 | 139.8811 | 152.5137 | 172.1108 | 194.3993 | 219.7806 | 241.1016 | 263.197 | 284.7078 | 305.4625 | 324.126 | 343.4535 | 362.5982 | 383.4362 | 401.5175 | 420.3138 | 438.9106 | 459.4571 | 477.3367 | 497.4567
VIC | 709.7942 | 865.3065 | 1023.2347 | 1180.4797 | 1319.6536 | 1466.5979 | 1630.0161 | 1785.5066 | 1949.8475 | 2143.6548 | 2349.7539 | 2540.1443 | 2744.5444 | 2962.4253 | 3227.1807 | 3507.0747 | 3809.1985 | 4072.9512 | 4358.8853 | 4649.6479 | 4947.3374 | 5212.5386 | 5492.5859 | 5771.8218 | 6075.7827 | 6350.3848 | 6648.9146 | 6951.2393 | 7276.812 | 7554.4619 | 7858.1528
Green Energy Exports
Green Energy Exports | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 792.0173 | 1050.1704 | 1310.6062 | 1574.7849 | 1918.2205 | 2298.5752 | 2624.1714 | 2955.1421 | 3269.4124 | 3560.0859 | 3959.0127 | 4525.4878 | 5093.5239 | 5476.4082 | 6023.2588 | 6620.0962 | 6983.0586 | 7344.7407 | 8199.0352 | 9037.3037 | 9641.3887 | 10183.2061 | 10749.8525 | 11311.1553 | 11903.4092 | 12441.3584 | 13025.8936 | 13608.834 | 14209.2588 | 14748.4199 | 15335.3301
QLD | 602.9946 | 790.7716 | 980.191 | 1175.0774 | 1475.6959 | 1820.0525 | 2114.9744 | 2420.3027 | 2709.1174 | 2982.1724 | 3347.0781 | 3856.6375 | 4357.665 | 4693.8857 | 5171.6636 | 5695.1855 | 6008.7285 | 6323.5972 | 7087.1147 | 7840.0259 | 8371.2686 | 8851.1328 | 9352.8789 | 9848.9033 | 10375.3438 | 10851.6553 | 11366.7051 | 11875.501 | 12398.9375 | 12869.6465 | 13380.002
SA | 522.9119 | 602.1956 | 683.199 | 765.2796 | 877.6957 | 1001.6312 | 1115.6255 | 1230.433 | 1344.4803 | 1450.1302 | 1585.9634 | 1763.1442 | 1937.2585 | 2071.7737 | 2238.3621 | 2414.9927 | 2544.7971 | 2667.2522 | 2898.5171 | 3127.6455 | 3315.696 | 3480.1672 | 3654.5803 | 3827.7935 | 4013.7786 | 4179.7148 | 4367.2075 | 4547.6948 | 4743.5068 | 4905.5137 | 5084.4688
TAS | 18.7047 | 34.4645 | 50.2958 | 66.589 | 94.806 | 127.6881 | 152.5171 | 177.9925 | 200.1327 | 219.6544 | 251.6107 | 302.9554 | 352.9919 | 381.9012 | 428.8892 | 480.9251 | 504.5327 | 528.9246 | 609.997 | 687.8967 | 737.223 | 779.9886 | 824.7286 | 868.3677 | 914.4301 | 954.9851 | 999.9259 | 1044.0875 | 1089.632 | 1128.9827 | 1172.8317
VIC | 738.6666 | 930.7493 | 1125.3593 | 1321.7133 | 1573.9802 | 1853.507 | 2109.0833 | 2374.3032 | 2632.3809 | 2872.9563 | 3179.4729 | 3588.0229 | 4003.3647 | 4294.9277 | 4687.4639 | 5106.5376 | 5387.4956 | 5668.8794 | 6269.0469 | 6851.4531 | 7297.2402 | 7690.6313 | 8108.27 | 8523.0977 | 8967.9385 | 9372.2051 | 9824.1729 | 10278.5176 | 10746.0615 | 11140.4385 | 11572.7129

## Battery & Plug-in EVs
Go to Assumptions Summary
Distributed Energy Resources: Battery Electric Vehicles (BEVs) and Plug-in Hybrid Electric Vehicles (PHEVs) | [13 empty] | Note: | Further information is available at http://forecasting.aemo.com.au
These forecasts are 2022 CSIRO trajectories developed for AEMO, with uptakes rebased using actuals from FCAI, EVC till March 2023 and charge profiles updated based on trial data from Energex and Ergon Energy Networks and Origin Energy
More detail is provided in the 2023 IASR EV Workbook available at https://www.aemo.com.au/-/media/files/Major-Publications/ISP/2023/2023-IASR-EV-Workbook
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | Progressive Change | Step Change | Hydrogen Export
Aggregated BEV and PHEV (Energy, GWh)
Amount of energy consumed by these electric vehicles
Progressive Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 72.2462 | 104.8823 | 144.8711 | 243.4923 | 401.5897 | 629.0473 | 921.8381 | 1275.3575 | 1683.824 | 2150.7379 | 2656.5598 | 3216.4421 | 3818.899 | 4489.4445 | 5166.9092 | 5884.4196 | 6627.4315 | 7416.54 | 8185.5335 | 8991.4609 | 9817.919 | 10688.523 | 11512.1365 | 12381.8103 | 13257.9369 | 14168.0802 | 15007.2843 | 15881.4893 | 16706.7984 | 17506.4167 | 18114.2296 | 18712.4878
QLD | 45.8998 | 67.916 | 95.817 | 166.0622 | 279.397 | 442.4704 | 652.824 | 906.3524 | 1198.1866 | 1531.6544 | 1893.5332 | 2295.5801 | 2730.4992 | 3217.0063 | 3711.4575 | 4237.5683 | 4784.854 | 5368.2992 | 5940.1101 | 6541.5586 | 7160.8988 | 7815.492 | 8438.3372 | 9097.676 | 9764.4252 | 10458.1942 | 11101.755 | 11773.6391 | 12412.8229 | 13037.8579 | 13524.7433 | 14008.3339
SA | 12.3804 | 17.3627 | 24.8546 | 42.6939 | 72.5095 | 115.1223 | 169.4014 | 234.8536 | 310.3524 | 396.5784 | 489.8075 | 592.7864 | 703.3657 | 826.2667 | 950.0715 | 1080.7751 | 1215.5323 | 1358.049 | 1496.1629 | 1640.3421 | 1787.6381 | 1942.0594 | 2086.6559 | 2238.8732 | 2391.591 | 2549.0865 | 2692.4006 | 2840.7709 | 2979.8391 | 3114.1573 | 3214.0365 | 3311.8878
TAS | 3.8211 | 4.5755 | 4.8371 | 5.3162 | 6.0415 | 6.9936 | 8.3303 | 12.3413 | 20.7455 | 33.4969 | 50.2416 | 71.1451 | 95.8197 | 124.7299 | 155.976 | 190.2296 | 226.9248 | 266.6582 | 306.9132 | 349.6115 | 394.0417 | 441.0912 | 486.6046 | 534.6798 | 584.0108 | 635.658 | 684.787 | 736.1178 | 785.3932 | 832.8984 | 870.2941 | 906.2576
VIC | 62.0865 | 90.0077 | 123.7414 | 201.0815 | 330.0603 | 519.6895 | 762.3887 | 1055.719 | 1396.0097 | 1786.547 | 2211.1256 | 2682.4666 | 3191.4879 | 3760.4429 | 4338.6229 | 4953.9656 | 5594.2359 | 6276.8353 | 6945.582 | 7648.6526 | 8372.1043 | 9136.0277 | 9861.4917 | 10628.8888 | 11404.831 | 12211.5318 | 12958.1549 | 13736.135 | 14474.23 | 15193.7896 | 15750.351 | 16301.6848
Step Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 72.7242 | 123.608 | 216.4778 | 469.9346 | 873.8687 | 1427.3609 | 2139.938 | 3014.4913 | 4002.954 | 5076.8148 | 6276.6407 | 7595.0886 | 8903.5614 | 10276.952 | 11592.1878 | 12936.7473 | 14281.5323 | 15674.4934 | 16978.9043 | 18319.7685 | 19665.5832 | 21064.8462 | 22355.1521 | 23708.424 | 25053.9738 | 26464.2357 | 27738.8896 | 28958.617 | 29625.3967 | 29989.0033 | 30156.6377 | 30469.1176
QLD | 45.9726 | 77.9082 | 142.1147 | 318.5929 | 598.2918 | 985.5844 | 1486.6364 | 2102.6701 | 2800.213 | 3559.0891 | 4407.3847 | 5338.3324 | 6262.1459 | 7231.6204 | 8160.1325 | 9109.1716 | 10058.4572 | 11041.8964 | 11962.764 | 12909.0676 | 13859.0469 | 14846.8733 | 15757.617 | 16712.7582 | 17662.722 | 18658.333 | 19558.1054 | 20412.2103 | 20883.0442 | 21152.2766 | 21282.562 | 21516.6885
SA | 12.4157 | 19.9875 | 36.1928 | 81.3429 | 157.3594 | 262.4735 | 398.1398 | 566.1174 | 756.2657 | 962.0213 | 1191.1022 | 1442.6579 | 1692.3446 | 1954.3136 | 2205.2655 | 2461.8538 | 2718.4145 | 2984.0772 | 3232.8512 | 3488.7236 | 3745.6554 | 4012.5786 | 4258.6405 | 4516.92 | 4773.6074 | 5042.5005 | 5285.6727 | 5517.9666 | 5634.5978 | 5684.1338 | 5696.2113 | 5739.4518
TAS | 3.867 | 5.5535 | 7.8332 | 11.8083 | 19.5428 | 29.9183 | 45.1161 | 73.1586 | 112.7579 | 160.7365 | 224.8238 | 301.11 | 376.7577 | 455.097 | 530.8365 | 607.8732 | 684.9162 | 764.3168 | 839.3917 | 916.2292 | 993.3101 | 1073.119 | 1147.3732 | 1224.8491 | 1301.9221 | 1382.3743 | 1455.7314 | 1525.1521 | 1557.4655 | 1567.3686 | 1566.9678 | 1574.7175
VIC | 62.2176 | 103.1279 | 177.2549 | 371.2832 | 695.63 | 1153.4141 | 1746.0021 | 2476.4165 | 3304.4367 | 4207.7093 | 5196.3584 | 6263.6363 | 7322.676 | 8435.4048 | 9500.3547 | 10589.369 | 11678.561 | 12807.3046 | 13863.54 | 14949.3966 | 16039.4077 | 17173.0344 | 18217.8745 | 19314.0934 | 20403.8911 | 21546.3748 | 22578.4085 | 23558.1823 | 24094.892 | 24397.9811 | 24540.8789 | 24794.2641
Green Energy Exports
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 73.0299 | 150.9462 | 367.5578 | 776.2126 | 1342.4433 | 2121.9214 | 3104.2514 | 4272.6354 | 5764.3581 | 7495.1907 | 9167.9529 | 10844.2579 | 12508.9467 | 14263.3839 | 15937.2907 | 17653.4498 | 19370.0274 | 21148.8165 | 22809.277 | 24518.3719 | 26233.8932 | 28022.3502 | 29663.8964 | 30726.3951 | 31170.9061 | 31691.4882 | 32056.3052 | 32506.9718 | 32954.7114 | 33513.492 | 33855.7004 | 34429.4997
QLD | 46.0375 | 113.4728 | 286.1152 | 582.8842 | 980.008 | 1519.8938 | 2194.8825 | 2998.7099 | 4021.3659 | 5202.4828 | 6343.3402 | 7486.6518 | 8621.7365 | 9819.1065 | 10961.0967 | 12132.1414 | 13303.4681 | 14517.5461 | 15650.3142 | 16816.2801 | 17986.9449 | 19207.7859 | 20327.4527 | 21055.6051 | 21364.3291 | 21722.9055 | 21972.3591 | 22278.0946 | 22578.7537 | 22953.792 | 23178.982 | 23562.4992
SA | 12.4648 | 20.1577 | 49.4352 | 116.5446 | 219.5152 | 364.2207 | 548.6394 | 765.4202 | 1046.9547 | 1379.8919 | 1701.9187 | 2024.4949 | 2344.8628 | 2682.0164 | 3004.0924 | 3334.0456 | 3663.8828 | 4005.6868 | 4325.1777 | 4653.7555 | 4983.6893 | 5327.3859 | 5643.0028 | 5834.2524 | 5894.3823 | 5967.9688 | 6011.3538 | 6070.3964 | 6128.3153 | 6205.9397 | 6242.7908 | 6327.4385
TAS | 3.8845 | 6.5239 | 15.0532 | 33.9482 | 63.2007 | 104.2133 | 156.6009 | 219.7416 | 298.0884 | 387.0165 | 472.9284 | 559.0029 | 644.4629 | 734.5796 | 820.5382 | 908.6807 | 996.8443 | 1088.2161 | 1173.4878 | 1261.2386 | 1349.3329 | 1441.198 | 1525.4971 | 1573.2488 | 1582.9305 | 1596.2299 | 1601.581 | 1611.1868 | 1620.5262 | 1635.1604 | 1639.0258 | 1654.8135
VIC | 62.3644 | 127.9962 | 301.9201 | 633.4185 | 1106.9815 | 1755.5948 | 2570.1015 | 3536.2989 | 4753.6686 | 6155.8994 | 7510.3913 | 8867.7483 | 10215.5771 | 11637.1617 | 12992.9642 | 14383.3734 | 15774.1208 | 17215.5727 | 18560.5763 | 19944.912 | 21334.6254 | 22783.8564 | 24113.5295 | 24990.6938 | 25379.7715 | 25826.0024 | 26140.2794 | 26518.7402 | 26888.7206 | 27346.6577 | 27626.0878 | 28087.3049
Aggregated BEV and PHEV (Uptake, Number of vehicles)
Number of BEVs and PHEVs in use.
Progressive Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 39669.9605 | 49529.826 | 66597.471 | 103931.8007 | 158771.1715 | 238973.3848 | 338196.0029 | 451611.4567 | 578757.18 | 719165.3944 | 872737.6595 | 1039000.2187 | 1214891.5651 | 1399993.4508 | 1591098.3832 | 1788128.9419 | 1990676.5546 | 2198285.2143 | 2410539.3397 | 2627130.6487 | 2847666.4565 | 3071743.9778 | 3293259.7856 | 3523161.6675 | 3751909.6334 | 3979960.9273 | 4207117.3877 | 4432537.0976 | 4634299.3227 | 4815195.3056 | 4977988.1827 | 5123839.7484
QLD | 22128.1091 | 28331.6998 | 39582.1684 | 66846.5564 | 105089.102 | 160830.5659 | 229844.0885 | 308190.7191 | 395732.0669 | 492331.5517 | 598109.1157 | 713025.8189 | 835164.663 | 964283.9696 | 1098186.2323 | 1236791.7921 | 1379799.5531 | 1526945.7363 | 1677947.2094 | 1832605.8928 | 1990630.7546 | 2151741.0321 | 2311928.7176 | 2478361.2064 | 2644375.9416 | 2810193.3471 | 2975815.6056 | 3140631.8657 | 3289933.3852 | 3425697.4913 | 3549729.4416 | 3662647.3029
SA | 6322.0433 | 8085.2086 | 11556.5473 | 19286.5197 | 30931.1584 | 47184.2199 | 67390.6126 | 90401.5909 | 116136.352 | 144487.282 | 175365.0145 | 208697.9289 | 243820.9894 | 280679.6261 | 318553.4785 | 357407.5244 | 397134.5181 | 437630.7015 | 478806.6965 | 520597.4065 | 562908.3609 | 605649.477 | 647464.8864 | 690816.8395 | 733484.156 | 775589.8821 | 817110.1553 | 857850.6233 | 893987.1769 | 926067.5361 | 954611.4338 | 979774.071
TAS | 2044.7685 | 2103.8522 | 2134.2211 | 2165.9237 | 2247.3413 | 2300.7123 | 2450.7799 | 3936.7588 | 6707.3593 | 10767.7396 | 16109.5021 | 22720.0054 | 30461.2703 | 39245.6674 | 48870.1143 | 59278.7972 | 70405.0871 | 82183.77 | 94552.8196 | 107460.8262 | 120852.5812 | 134676.4019 | 148378.7374 | 162924.7123 | 177748.8952 | 192817.1963 | 208091.6311 | 223529.4489 | 237700.6577 | 250418.2532 | 261850.5817 | 272049.2688
VIC | 29505.0203 | 37348.6099 | 51056.7477 | 81149.3014 | 127020.0722 | 192643.0231 | 273925.7382 | 366342.904 | 469624.0816 | 583494.5504 | 707793.6429 | 842281.5361 | 984616.4858 | 1134791.3302 | 1290303.0475 | 1451114.1692 | 1616893.6156 | 1787265.0956 | 1961884.814 | 2140498.3398 | 2322760.9044 | 2508320.8949 | 2691854.6564 | 2882939.8408 | 3073240.521 | 3262893.1892 | 3451829.6713 | 3639359.5171 | 3808416.2944 | 3961450.7734 | 4100651.8381 | 4226795.5819
Step Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 40951.8006 | 62249.1856 | 104029.7704 | 205355.8745 | 341000.7848 | 532913.5715 | 774035.9798 | 1063740.1161 | 1370825.4267 | 1693180.3595 | 2020732.9398 | 2348251.1737 | 2675801.2291 | 3003389.4877 | 3331018.4374 | 3658683.3862 | 3986380.1677 | 4314105.0779 | 4641854.818 | 4969626.4394 | 5297412.9217 | 5625204.0041 | 5952995.0864 | 6280786.1687 | 6608577.251 | 6936368.3333 | 7264159.4156 | 7509097.1685 | 7559265.8616 | 7609191.3774 | 7658824.0701 | 7737541.1435
QLD | 22466.6699 | 34583.4898 | 60028.0675 | 129051.2133 | 219386.8347 | 349249.146 | 512008.4487 | 707378.7594 | 914877.5111 | 1133599.8375 | 1372219.7936 | 1610818.5347 | 1849434.8787 | 2088073.6142 | 2326736.9742 | 2565422.2649 | 2804127.0768 | 3042849.2518 | 3281586.8518 | 3520338.1298 | 3759095.5426 | 3997853.0895 | 4236610.6363 | 4475368.1832 | 4714125.7301 | 4952883.2769 | 5191640.8238 | 5368922.3271 | 5413500.3676 | 5457997.8188 | 5502366.9 | 5567055.0493
SA | 6405.4559 | 9883.1424 | 17815.4748 | 38229.005 | 66504.2131 | 105898.4727 | 155416.7008 | 214979.4357 | 278327.8775 | 344822.6546 | 412477.1533 | 480119.34 | 547766.0853 | 615418.8033 | 683078.1914 | 750743.5367 | 818414.1998 | 886089.6058 | 953769.2369 | 1021452.2655 | 1089136.6297 | 1156820.9938 | 1224505.358 | 1292189.7222 | 1359874.0864 | 1427558.4506 | 1495242.8148 | 1545694.786 | 1551112.6977 | 1556422.5184 | 1561612.8683 | 1574822.7353
TAS | 2178.048 | 2736.9544 | 3537.6918 | 4800.8602 | 7894.886 | 10438.8923 | 15918.2685 | 25990.6708 | 38702.8898 | 53926.0278 | 78831.2942 | 103738.6236 | 128646.5151 | 153555.2598 | 178465.0244 | 203375.7093 | 228287.224 | 253199.4865 | 278112.3709 | 303025.5082 | 327938.6456 | 352851.7829 | 377764.9203 | 402678.0576 | 427591.195 | 452504.3323 | 477417.4697 | 496230.4387 | 496650.7016 | 497063.0117 | 497466.4545 | 499809.1698
VIC | 29958.6246 | 45547.9332 | 77137.6199 | 155791.0114 | 265346.1474 | 420018.0987 | 613689.8742 | 846086.3333 | 1092894.3004 | 1352455.312 | 1628341.515 | 1904186.475 | 2180054.9192 | 2455952.7041 | 2731882.4459 | 3007840.5948 | 3283823.9821 | 3559829.7758 | 3835855.4388 | 4111898.6898 | 4387951.096 | 4664004.7776 | 4940058.4592 | 5216112.1408 | 5492165.8224 | 5768219.504 | 6044273.1856 | 6249089.7552 | 6303568.5731 | 6358160.7736 | 6412828.0688 | 6484048.8098
Green Energy Exports
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 41836.1299 | 74808.5106 | 168569.5792 | 315915.4986 | 513939.0792 | 785407.7651 | 1119898.3703 | 1480242.4701 | 1893886.3781 | 2307132.8601 | 2720408.449 | 3133714.0354 | 3547049.9748 | 3960422.274 | 4373833.2758 | 4787270.5398 | 5200715.8765 | 5614161.1427 | 6027606.3623 | 6441051.5717 | 6854496.8327 | 7267942.2751 | 7681388.5248 | 7770958.6811 | 7859289.1319 | 7946457.6526 | 8032436.2795 | 8117086.0347 | 8198161.7179 | 8278615.0205 | 8358348.1266 | 8516814.0821
QLD | 22926.5629 | 51711.3153 | 117300.3182 | 217102.0221 | 348012.743 | 526875.9783 | 745631.1711 | 982249.5972 | 1272509.8843 | 1562519.4459 | 1852544.1437 | 2142584.9552 | 2432642.5164 | 2722721.3501 | 3012823.5756 | 3302936.2516 | 3593049.087 | 3883161.8675 | 4173274.6154 | 4463387.3648 | 4753500.1734 | 5043613.1624 | 5333726.9161 | 5401868.4679 | 5469066.8414 | 5535352.9501 | 5600672.3898 | 5664929.8188 | 5726511.6074 | 5787731.8063 | 5848492.8705 | 5959925.0591
SA | 6519.6513 | 9568.2218 | 24235.0334 | 51132.4002 | 89993.3532 | 143318.8506 | 210295.3038 | 282328.0429 | 369478.0668 | 456553.1695 | 543631.8433 | 630714.3853 | 717801.0041 | 804892.9583 | 891990.3029 | 979089.7666 | 1066189.2301 | 1153288.6935 | 1240388.1568 | 1327487.6202 | 1414587.0837 | 1501686.5475 | 1588786.0129 | 1601452.7069 | 1613780.8871 | 1625798.338 | 1637553.0384 | 1649023.4672 | 1659689.2975 | 1670137.9599 | 1680354.8668 | 1708646.3873
TAS | 2225.4836 | 3316.7953 | 7672.5358 | 15437.2789 | 26796.556 | 42205.571 | 61648.9459 | 82855.1061 | 110755.6357 | 138637.0798 | 166519.0414 | 194401.6222 | 222284.9052 | 250169.1491 | 278053.9291 | 305938.7087 | 333823.488 | 361708.267 | 389593.046 | 417477.8251 | 445362.6048 | 473247.3859 | 501132.1725 | 503038.9263 | 504854.838 | 506591.2874 | 508282.4135 | 509927.3196 | 511353.5167 | 512736.2502 | 514074.7867 | 519858.4928
VIC | 30580.8043 | 57590.1548 | 128649.6508 | 245251.0305 | 404182.3145 | 619353.078 | 884752.4684 | 1170957.8215 | 1517511.1153 | 1863739.619 | 2209987.9521 | 2556257.1798 | 2902547.9459 | 3248865.5732 | 3595212.4487 | 3941574.5268 | 4287938.6839 | 4634302.8045 | 4980666.9028 | 5327031.0001 | 5673395.1324 | 6019759.3758 | 6366124.0971 | 6456205.0735 | 6545076.6282 | 6632727.5172 | 6719047.6579 | 6803811.1761 | 6885289.2714 | 6966571.3602 | 7047545.2734 | 7182269.3645

## Fuel cell EVs
Go to Assumptions Summary
Distributed Energy Resources: Fuel Cell Electric Vehicles (FCEVs)
These forecasts are 2022 CSIRO trajectories developed for AEMO.
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | Progressive Change | Step Change | Hydrogen Export
FCEV (Uptake, Number of vehicles)
Number of FCEVs in use.
Progressive Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 22.945 | 33.0392 | 139.3677 | 314.832 | 578.78 | 917.1621 | 1343.434 | 1740.5849 | 2114.1533 | 2463.639 | 2789.1336 | 3090.8304 | 3363.8566 | 3612.5227 | 3833.8869 | 4030.9043 | 4205.6455 | 4359.8892 | 4495.2859 | 4613.4468 | 4715.718 | 4803.3044 | 4873.4912 | 4933.2681 | 4966.5799 | 4979.4363 | 4970.5149 | 4942.4082 | 4900.8907 | 4862.7713 | 4827.6856 | 4795.0669
QLD | 0 | 46.9153 | 112.9083 | 228.1912 | 401.4725 | 624.7567 | 905.9451 | 1171.8422 | 1425.8673 | 1667.7954 | 1897.7497 | 2115.9993 | 2318.9514 | 2508.9774 | 2683.4269 | 2843.822 | 2991.1533 | 3126.372 | 3250.311 | 3363.8367 | 3467.6162 | 3562.2706 | 3648.3312 | 3717.6092 | 3776.4183 | 3820.1119 | 3848.1363 | 3862.1482 | 3863.8309 | 3865.7575 | 3867.9416 | 3870.0479
SA | 0 | 1.067 | 17.3029 | 46.847 | 90.2185 | 147.1038 | 217.9937 | 286.0541 | 351.8972 | 415.2662 | 475.9071 | 533.8088 | 587.8827 | 638.7708 | 685.6689 | 728.9831 | 768.9642 | 805.8411 | 839.8376 | 871.1835 | 900.0496 | 926.5947 | 950.951 | 973.0344 | 990.2989 | 1003.4396 | 1012.6197 | 1017.9371 | 1019.3186 | 1019.8982 | 1019.7912 | 1018.9573
TAS | 0 | 0.30106 | 3.0906 | 6.629 | 12.6496 | 20.3226 | 31.1675 | 42.0543 | 53.1402 | 64.3834 | 75.7157 | 87.1158 | 98.3434 | 109.4497 | 120.2209 | 130.6954 | 140.8863 | 150.803 | 160.4536 | 169.8533 | 179.0091 | 187.9277 | 196.6116 | 204.9865 | 212.5272 | 219.7081 | 226.1384 | 231.9988 | 236.5072 | 240.438 | 243.8339 | 246.7063
VIC | 28.56 | 50.6475 | 99.7344 | 212.3442 | 390.6313 | 626.2415 | 920.2987 | 1200.3789 | 1469.6177 | 1727.4868 | 1973.4185 | 2207.4793 | 2425.8665 | 2631.5757 | 2821.8951 | 2998.5069 | 3162.4533 | 3314.6066 | 3455.7961 | 3586.8787 | 3708.5177 | 3821.3061 | 3920.5223 | 4016.8734 | 4095.394 | 4157.8956 | 4205.0989 | 4237.4559 | 4255.8494 | 4272.487 | 4287.7409 | 4301.4178
Step Change | bar: 2022-23 to 2049-50
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 23.155 | 39.1425 | 173.1939 | 394.3714 | 729.2913 | 1167.144 | 1728.0793 | 2413.8301 | 3865.3748 | 6066.3619 | 13585.6661 | 21104.9703 | 28624.2745 | 36143.5787 | 43662.8829 | 51182.1871 | 58701.4913 | 66220.7955 | 73740.0996 | 81259.4038 | 88778.708 | 96298.0122 | 103817.3164 | 111336.6206 | 118855.9248 | 126375.229 | 133894.5332 | 141413.8374 | 142877.3025 | 144351.36 | 145835.6634 | 147631.0043
QLD | 0 | 12.015 | 96.9689 | 243.2924 | 463.3584 | 750.5142 | 1115.7362 | 1559.7238 | 2522.4712 | 4000.7152 | 8868.3771 | 13736.0389 | 18603.7007 | 23471.3626 | 28339.0244 | 33206.6862 | 38074.3481 | 42942.0099 | 47809.6717 | 52677.3336 | 57544.9954 | 62412.6572 | 67280.319 | 72147.9809 | 77015.6427 | 81883.3045 | 86750.9664 | 91618.6282 | 92585.9593 | 93559.4701 | 94538.766 | 95732.6397
SA | 0 | 2.4074 | 23.4655 | 61.5339 | 117.6294 | 192.417 | 286.3139 | 399.1736 | 670.9489 | 1099.356 | 2650.6102 | 4201.8644 | 5753.1186 | 7304.3727 | 8855.6269 | 10406.8811 | 11958.1353 | 13509.3895 | 15060.6437 | 16611.8979 | 18163.1521 | 19714.4063 | 21265.6605 | 22816.9147 | 24368.1688 | 25919.423 | 27470.6772 | 29021.9314 | 29229.3496 | 29437.6518 | 29646.7521 | 29939.4139
TAS | 0 | 0.6429 | 5.4577 | 12.0366 | 23.1173 | 37.9087 | 58.7864 | 86.8043 | 162.6915 | 286.2901 | 723.3988 | 1160.5076 | 1597.6163 | 2034.7251 | 2471.8338 | 2908.9426 | 3346.0513 | 3783.1601 | 4220.2688 | 4657.3776 | 5094.4863 | 5531.5951 | 5968.7038 | 6405.8126 | 6842.9213 | 7280.0301 | 7717.1388 | 8154.2475 | 8193.4231 | 8233.1268 | 8273.3666 | 8333.8542
VIC | 30.24 | 56.3551 | 116.8655 | 261.3168 | 485.9038 | 788.1059 | 1169.5163 | 1630.8019 | 2719.7388 | 4429.2854 | 10201.2027 | 15973.1201 | 21745.0375 | 27516.9548 | 33288.8722 | 39060.7896 | 44832.707 | 50604.6243 | 56376.5417 | 62148.4591 | 67920.3764 | 73692.2938 | 79464.2112 | 85236.1285 | 91008.0459 | 96779.9633 | 102551.8806 | 108323.798 | 109379.3206 | 110441.6871 | 111510.573 | 112753.9742
Green Energy Exports
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 23.47 | 154.6864 | 412.7708 | 743.1039 | 1166.8262 | 1671.4029 | 2277.8538 | 10454.7994 | 41888.1852 | 73321.571 | 104754.9568 | 136188.3426 | 167621.7284 | 199055.1141 | 230488.4999 | 261921.8857 | 293355.2715 | 324788.6573 | 356222.043 | 387655.4288 | 419088.8146 | 450522.2004 | 481955.5862 | 488302.4533 | 494610.9863 | 500900.2625 | 507176.4742 | 513431.3768 | 519519.8448 | 525614.206 | 531710.1199 | 542037.8267
QLD | 0 | 190.684 | 459.0365 | 756.768 | 1086.4216 | 1439.2049 | 1826.7923 | 7127.5878 | 28313.0848 | 49498.5818 | 70684.0788 | 91869.5758 | 113055.0727 | 134240.5697 | 155426.0667 | 176611.5637 | 197797.0607 | 218982.5576 | 240168.0546 | 261353.5516 | 282539.0486 | 303724.5456 | 324910.0425 | 329415.0953 | 333876.9365 | 338303.3617 | 342696.9276 | 347052.053 | 351268.1082 | 355485.0388 | 359698.1039 | 366628.5195
SA | 0 | 6.305 | 29.8471 | 71.6183 | 132.2391 | 212.2554 | 312.045 | 1898.3019 | 8402.4245 | 14906.5472 | 21410.6698 | 27914.7924 | 34418.9151 | 40923.0377 | 47427.1603 | 53931.283 | 60435.4056 | 66939.5282 | 73443.6508 | 79947.7735 | 86451.8961 | 92956.0187 | 99460.1414 | 100398.3987 | 101319.4638 | 102227.6464 | 103127.8569 | 104018.8489 | 104867.7693 | 105710.6199 | 106546.7452 | 108349.8936
TAS | 0 | 1.4499 | 10.8935 | 25.9939 | 49.2595 | 79.5468 | 118.6869 | 580.2887 | 2543.1002 | 4505.9118 | 6468.7234 | 8431.5349 | 10394.3465 | 12357.1581 | 14319.9696 | 16282.7812 | 18245.5928 | 20208.4044 | 22171.2159 | 24134.0275 | 26096.8391 | 28059.6506 | 30022.4622 | 30176.2965 | 30325.6346 | 30471.8575 | 30617.4706 | 30762.436 | 30896.3252 | 31029.1649 | 31160.9543 | 31530.462
VIC | 32.76 | 124.7393 | 284.5122 | 507.2635 | 791.3985 | 1138.641 | 1551.6839 | 7953.3856 | 33427.8515 | 58902.3174 | 84376.7833 | 109851.2492 | 135325.7152 | 160800.1811 | 186274.647 | 211749.1129 | 237223.5788 | 262698.0447 | 288172.5107 | 313646.9766 | 339121.4425 | 364595.9084 | 390070.3743 | 395949.3555 | 401758.5276 | 407505.9592 | 413191.3457 | 418798.3832 | 424216.6485 | 429646.3876 | 435082.1053 | 443400.6842

## EV V2G
Go to Assumptions Summary
Distributed Energy Resources: Vehicle to Grid battery characteristics
Vehicle to Grid data represents the use of EV batteries to store energy which can be called on by a retailer or aggregator to supply back into the grid.
This data is used within the Plexos model in addition to the capacities listed in the 'Aggregated energy storages' tab.
These forecasts are 2022 CSIRO trajectories developed for AEMO.
More detail is provided in the 2023 IASR EV Workbook available at https://www.aemo.com.au/-/media/files/Major-Publications/ISP/2023/2023-IASR-EV-Workbook
Depth | Max available energy storage for charge / discharge (MWh)
Capacity | Total capacity of all batteries assumed to be participating in V2G (MW)
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | Progressive Change | Step Change | Hydrogen Export
Vehicle to grid (Capacity and depth)
FYE | Region | Scenario | V2G_capacity (MW) | V2G_depth (MWh)
2023 | NSW | Progressive Change | 0 | 0
2023 | NSW | Step Change | 0 | 0
2023 | NSW | Green Energy Exports | 0 | 0
2023 | QLD | Progressive Change | 0 | 0
2023 | QLD | Step Change | 0 | 0
2023 | QLD | Green Energy Exports | 0 | 0
2023 | SA | Progressive Change | 0 | 0
2023 | SA | Step Change | 0 | 0
2023 | SA | Green Energy Exports | 0 | 0
2023 | TAS | Progressive Change | 0 | 0
2023 | TAS | Step Change | 0 | 0
2023 | TAS | Green Energy Exports | 0 | 0
2023 | VIC | Progressive Change | 0 | 0
2023 | VIC | Step Change | 0 | 0
2023 | VIC | Green Energy Exports | 0 | 0
2024 | NSW | Progressive Change | 0 | 0
2024 | NSW | Step Change | 0 | 0
2024 | NSW | Green Energy Exports | 0 | 0
2024 | QLD | Progressive Change | 0 | 0
2024 | QLD | Step Change | 0 | 0
2024 | QLD | Green Energy Exports | 0 | 0
2024 | SA | Progressive Change | 0 | 0
2024 | SA | Step Change | 0 | 0
2024 | SA | Green Energy Exports | 0 | 0
2024 | TAS | Progressive Change | 0 | 0
2024 | TAS | Step Change | 0 | 0
2024 | TAS | Green Energy Exports | 0 | 0
2024 | VIC | Progressive Change | 0 | 0
2024 | VIC | Step Change | 0 | 0
2024 | VIC | Green Energy Exports | 0 | 0
2025 | NSW | Progressive Change | 0 | 0
2025 | NSW | Step Change | 0 | 0
2025 | NSW | Green Energy Exports | 0 | 0
2025 | QLD | Progressive Change | 0 | 0
2025 | QLD | Step Change | 0 | 0
2025 | QLD | Green Energy Exports | 0 | 0
2025 | SA | Progressive Change | 0 | 0
2025 | SA | Step Change | 0 | 0
2025 | SA | Green Energy Exports | 0 | 0
2025 | TAS | Progressive Change | 0 | 0
2025 | TAS | Step Change | 0 | 0
2025 | TAS | Green Energy Exports | 0 | 0
2025 | VIC | Progressive Change | 0 | 0
2025 | VIC | Step Change | 0 | 0
2025 | VIC | Green Energy Exports | 0 | 0
2026 | NSW | Progressive Change | 0 | 0
2026 | NSW | Step Change | 0 | 0
2026 | NSW | Green Energy Exports | 0 | 0
2026 | QLD | Progressive Change | 0 | 0
2026 | QLD | Step Change | 0 | 0
2026 | QLD | Green Energy Exports | 0 | 0
2026 | SA | Progressive Change | 0 | 0
2026 | SA | Step Change | 0 | 0
2026 | SA | Green Energy Exports | 0 | 0
2026 | TAS | Progressive Change | 0 | 0
2026 | TAS | Step Change | 0 | 0
2026 | TAS | Green Energy Exports | 0 | 0
2026 | VIC | Progressive Change | 0 | 0
2026 | VIC | Step Change | 0 | 0
2026 | VIC | Green Energy Exports | 0 | 0
2027 | NSW | Progressive Change | 0 | 0
2027 | NSW | Step Change | 0 | 0
2027 | NSW | Green Energy Exports | 0 | 0
2027 | QLD | Progressive Change | 0 | 0
2027 | QLD | Step Change | 0 | 0
2027 | QLD | Green Energy Exports | 0 | 0
2027 | SA | Progressive Change | 0 | 0
2027 | SA | Step Change | 0 | 0
2027 | SA | Green Energy Exports | 0 | 0
2027 | TAS | Progressive Change | 0 | 0
2027 | TAS | Step Change | 0 | 0
2027 | TAS | Green Energy Exports | 0 | 0
2027 | VIC | Progressive Change | 0 | 0
2027 | VIC | Step Change | 0 | 0
2027 | VIC | Green Energy Exports | 0 | 0
2028 | NSW | Progressive Change | 0 | 0
2028 | NSW | Step Change | 0 | 0
2028 | NSW | Green Energy Exports | 18.406 | 91.7847
2028 | QLD | Progressive Change | 0 | 0
2028 | QLD | Step Change | 0 | 0
2028 | QLD | Green Energy Exports | 11.337 | 56.4992
2028 | SA | Progressive Change | 0 | 0
2028 | SA | Step Change | 0 | 0
2028 | SA | Green Energy Exports | 3.412 | 17.0457
2028 | TAS | Progressive Change | 0 | 0
2028 | TAS | Step Change | 0 | 0
2028 | TAS | Green Energy Exports | 0.92856 | 4.6231
2028 | VIC | Progressive Change | 0 | 0
2028 | VIC | Step Change | 0 | 0
2028 | VIC | Green Energy Exports | 14.8473 | 74.1404
2029 | NSW | Progressive Change | 0 | 0
2029 | NSW | Step Change | 0 | 0
2029 | NSW | Green Energy Exports | 65.019 | 325.507
2029 | QLD | Progressive Change | 0 | 0
2029 | QLD | Step Change | 0 | 0
2029 | QLD | Green Energy Exports | 39.9364 | 199.7114
2029 | SA | Progressive Change | 0 | 0
2029 | SA | Step Change | 0 | 0
2029 | SA | Green Energy Exports | 12.4022 | 62.2099
2029 | TAS | Progressive Change | 0 | 0
2029 | TAS | Step Change | 0 | 0
2029 | TAS | Green Energy Exports | 3.3353 | 16.6806
2029 | VIC | Progressive Change | 0 | 0
2029 | VIC | Step Change | 0 | 0
2029 | VIC | Green Energy Exports | 52.538 | 263.3914
2030 | NSW | Progressive Change | 0 | 0
2030 | NSW | Step Change | 0 | 0
2030 | NSW | Green Energy Exports | 136.7464 | 686.0927
2030 | QLD | Progressive Change | 0 | 0
2030 | QLD | Step Change | 0 | 0
2030 | QLD | Green Energy Exports | 83.9251 | 420.4946
2030 | SA | Progressive Change | 0 | 0
2030 | SA | Step Change | 0 | 0
2030 | SA | Green Energy Exports | 26.5157 | 133.2907
2030 | TAS | Progressive Change | 0 | 0
2030 | TAS | Step Change | 0 | 0
2030 | TAS | Green Energy Exports | 7.0983 | 35.5882
2030 | VIC | Progressive Change | 0 | 0
2030 | VIC | Step Change | 0 | 0
2030 | VIC | Green Energy Exports | 110.6724 | 556.0613
2031 | NSW | Progressive Change | 7.0925 | 35.4651
2031 | NSW | Step Change | 36.2644 | 182.3451
2031 | NSW | Green Energy Exports | 236.7082 | 1183.2875
2031 | QLD | Progressive Change | 4.5623 | 22.7911
2031 | QLD | Step Change | 22.6532 | 113.6452
2031 | QLD | Green Energy Exports | 150.1391 | 750.0962
2031 | SA | Progressive Change | 1.455 | 7.2879
2031 | SA | Step Change | 7.4934 | 37.7281
2031 | SA | Green Energy Exports | 46.1991 | 230.9049
2031 | TAS | Progressive Change | 0.075177 | 0.35623
2031 | TAS | Step Change | 0.93518 | 4.7871
2031 | TAS | Green Energy Exports | 13.0592 | 64.997
2031 | VIC | Progressive Change | 5.9234 | 29.6745
2031 | VIC | Step Change | 29.6211 | 149.0864
2031 | VIC | Green Energy Exports | 193.2083 | 965.5272
2032 | NSW | Progressive Change | 17.6187 | 88.2879
2032 | NSW | Step Change | 89.4511 | 450.2523
2032 | NSW | Green Energy Exports | 363.2559 | 1811.5097
2032 | QLD | Progressive Change | 11.3334 | 56.7244
2032 | QLD | Step Change | 56.0273 | 281.3447
2032 | QLD | Green Energy Exports | 235.3157 | 1173.5358
2032 | SA | Progressive Change | 3.6176 | 18.159
2032 | SA | Step Change | 18.5435 | 93.4528
2032 | SA | Green Energy Exports | 71.201 | 354.5302
2032 | TAS | Progressive Change | 0.23938 | 1.1628
2032 | TAS | Step Change | 2.5765 | 13.2053
2032 | TAS | Green Energy Exports | 20.8201 | 103.1707
2032 | VIC | Progressive Change | 14.7055 | 73.8232
2032 | VIC | Step Change | 73.1978 | 368.7923
2032 | VIC | Green Energy Exports | 298.1497 | 1484.7243
2033 | NSW | Progressive Change | 32.0472 | 160.8313
2033 | NSW | Step Change | 158.5143 | 795.1324
2033 | NSW | Green Energy Exports | 516.3895 | 2570.7591
2033 | QLD | Progressive Change | 20.6172 | 103.3282
2033 | QLD | Step Change | 102.1024 | 511.3079
2033 | QLD | Green Energy Exports | 339.4551 | 1690.8133
2033 | SA | Progressive Change | 6.5792 | 33.0743
2033 | SA | Step Change | 32.5606 | 163.3456
2033 | SA | Green Energy Exports | 101.5214 | 504.1665
2033 | TAS | Progressive Change | 0.53521 | 2.6348
2033 | TAS | Step Change | 5.7198 | 28.8389
2033 | TAS | Green Energy Exports | 30.3811 | 150.1095
2033 | VIC | Progressive Change | 26.7237 | 134.3505
2033 | VIC | Step Change | 130.4576 | 654.2284
2033 | VIC | Green Energy Exports | 425.4966 | 2113.6524
2034 | NSW | Progressive Change | 50.824 | 255.3437
2034 | NSW | Step Change | 243.8026 | 1219.8486
2034 | NSW | Green Energy Exports | 696.1088 | 3461.0359
2034 | QLD | Progressive Change | 32.7158 | 164.123
2034 | QLD | Step Change | 160.2184 | 800.7984
2034 | QLD | Green Energy Exports | 462.5571 | 2301.9288
2034 | SA | Progressive Change | 10.4275 | 52.4768
2034 | SA | Step Change | 49.7413 | 248.6827
2034 | SA | Green Energy Exports | 137.1603 | 679.8139
2034 | TAS | Progressive Change | 1.0047 | 4.9844
2034 | TAS | Step Change | 10.0998 | 50.4931
2034 | TAS | Green Energy Exports | 41.742 | 205.8132
2034 | VIC | Progressive Change | 42.3435 | 213.1018
2034 | VIC | Step Change | 201.4914 | 1007.0245
2034 | VIC | Green Energy Exports | 575.2491 | 2852.3118
2035 | NSW | Progressive Change | 74.2152 | 373.165
2035 | NSW | Step Change | 345.316 | 1724.4008
2035 | NSW | Green Energy Exports | 902.414 | 4482.3401
2035 | QLD | Progressive Change | 47.8228 | 240.0825
2035 | QLD | Step Change | 230.3754 | 1149.8161
2035 | QLD | Green Energy Exports | 604.6218 | 3006.8823
2035 | SA | Progressive Change | 15.21 | 76.606
2035 | SA | Step Change | 70.0856 | 349.464
2035 | SA | Green Energy Exports | 178.1177 | 881.4725
2035 | TAS | Progressive Change | 1.6824 | 8.386
2035 | TAS | Step Change | 15.7166 | 78.1679
2035 | TAS | Green Energy Exports | 54.903 | 270.282
2035 | VIC | Progressive Change | 61.7875 | 311.2008
2035 | VIC | Step Change | 286.2991 | 1427.1805
2035 | VIC | Green Energy Exports | 747.407 | 3700.7023
2036 | NSW | Progressive Change | 102.5327 | 515.8639
2036 | NSW | Step Change | 463.0545 | 2308.789
2036 | NSW | Green Energy Exports | 1135.3051 | 5634.6715
2036 | QLD | Progressive Change | 66.1607 | 332.3237
2036 | QLD | Step Change | 312.5734 | 1558.361
2036 | QLD | Green Energy Exports | 765.6491 | 3805.6738
2036 | SA | Progressive Change | 20.987 | 105.7659
2036 | SA | Step Change | 93.5934 | 465.6895
2036 | SA | Green Energy Exports | 224.3936 | 1109.1421
2036 | TAS | Progressive Change | 2.6002 | 13
2036 | TAS | Step Change | 22.57 | 111.8633
2036 | TAS | Green Energy Exports | 69.864 | 343.5158
2036 | VIC | Progressive Change | 85.3386 | 430.0714
2036 | VIC | Step Change | 384.8807 | 1914.6966
2036 | VIC | Green Energy Exports | 941.9705 | 4658.8239
2037 | NSW | Progressive Change | 135.8315 | 683.7153
2037 | NSW | Step Change | 597.0182 | 2973.0132
2037 | NSW | Green Energy Exports | 1394.782 | 6918.0303
2037 | QLD | Progressive Change | 87.7856 | 441.1275
2037 | QLD | Step Change | 406.8123 | 2026.4332
2037 | QLD | Green Energy Exports | 945.6391 | 4698.3032
2037 | SA | Progressive Change | 27.7586 | 139.956
2037 | SA | Step Change | 120.2647 | 597.3593
2037 | SA | Green Energy Exports | 275.988 | 1362.8228
2037 | TAS | Progressive Change | 3.7771 | 18.9223
2037 | TAS | Step Change | 30.6602 | 151.5793
2037 | TAS | Green Energy Exports | 86.6249 | 425.5146
2037 | VIC | Progressive Change | 113.0619 | 570.0407
2037 | VIC | Step Change | 497.2363 | 2469.5726
2037 | VIC | Green Energy Exports | 1158.9396 | 5726.6767
2038 | NSW | Progressive Change | 174.3158 | 877.748
2038 | NSW | Step Change | 747.207 | 3717.0734
2038 | NSW | Green Energy Exports | 1680.8447 | 8332.4164
2038 | QLD | Progressive Change | 112.847 | 567.2452
2038 | QLD | Step Change | 513.0922 | 2554.0326
2038 | QLD | Green Energy Exports | 1144.5918 | 5684.7706
2038 | SA | Progressive Change | 35.5573 | 179.3401
2038 | SA | Step Change | 150.0997 | 744.4733
2038 | SA | Green Energy Exports | 332.9009 | 1642.5145
2038 | TAS | Progressive Change | 5.236 | 26.269
2038 | TAS | Step Change | 39.987 | 197.316
2038 | TAS | Green Energy Exports | 105.1859 | 516.2784
2038 | VIC | Progressive Change | 145.1446 | 732.0525
2038 | VIC | Step Change | 623.3658 | 3091.8087
2038 | VIC | Green Energy Exports | 1398.3142 | 6904.2606
2039 | NSW | Progressive Change | 218.1511 | 1098.794
2039 | NSW | Step Change | 913.6208 | 4540.9696
2039 | NSW | Green Energy Exports | 1993.4933 | 9877.8298
2039 | QLD | Progressive Change | 141.4687 | 711.2991
2039 | QLD | Step Change | 631.413 | 3141.1593
2039 | QLD | Green Energy Exports | 1362.5072 | 6765.076
2039 | SA | Progressive Change | 44.406 | 224.0338
2039 | SA | Step Change | 183.0982 | 907.0316
2039 | SA | Green Energy Exports | 395.1323 | 1948.2174
2039 | TAS | Progressive Change | 6.9965 | 35.1382
2039 | TAS | Step Change | 50.5506 | 249.0732
2039 | TAS | Green Energy Exports | 125.5469 | 615.8072
2039 | VIC | Progressive Change | 181.7401 | 916.8794
2039 | VIC | Step Change | 763.2693 | 3781.4047
2039 | VIC | Green Energy Exports | 1660.0943 | 8191.5756
2040 | NSW | Progressive Change | 267.4777 | 1347.5598
2040 | NSW | Step Change | 1096.2598 | 5444.7018
2040 | NSW | Green Energy Exports | 2332.7277 | 11554.2705
2040 | QLD | Progressive Change | 173.7657 | 873.8667
2040 | QLD | Step Change | 761.7748 | 3787.8132
2040 | QLD | Green Energy Exports | 1599.3852 | 7939.2194
2040 | SA | Progressive Change | 54.323 | 274.1288
2040 | SA | Step Change | 219.2603 | 1085.0342
2040 | SA | Green Energy Exports | 462.6822 | 2279.9313
2040 | TAS | Progressive Change | 9.0752 | 45.6141
2040 | TAS | Step Change | 62.3509 | 306.8511
2040 | TAS | Green Energy Exports | 147.7079 | 724.1011
2040 | VIC | Progressive Change | 222.9802 | 1125.1865
2040 | VIC | Step Change | 916.9467 | 4538.3607
2040 | VIC | Green Energy Exports | 1944.2799 | 9588.6218
2041 | NSW | Progressive Change | 322.4201 | 1624.6715
2041 | NSW | Step Change | 1295.1239 | 6428.2701
2041 | NSW | Green Energy Exports | 2698.548 | 13361.7386
2041 | QLD | Progressive Change | 209.839 | 1055.4557
2041 | QLD | Step Change | 904.1775 | 4493.9944
2041 | QLD | Green Energy Exports | 1855.2259 | 9207.2007
2041 | SA | Progressive Change | 65.3235 | 329.7017
2041 | SA | Step Change | 258.5859 | 1278.481
2041 | SA | Green Energy Exports | 535.5506 | 2637.6563
2041 | TAS | Progressive Change | 11.4863 | 57.7681
2041 | TAS | Step Change | 75.3879 | 370.6496
2041 | TAS | Green Energy Exports | 171.669 | 841.1599
2041 | VIC | Progressive Change | 268.9834 | 1357.5704
2041 | VIC | Step Change | 1084.398 | 5362.6767
2041 | VIC | Green Energy Exports | 2250.8711 | 11095.3992
2042 | NSW | Progressive Change | 383.0985 | 1930.735
2042 | NSW | Step Change | 1510.2132 | 7491.6744
2042 | NSW | Green Energy Exports | 3090.9541 | 15300.234
2042 | QLD | Progressive Change | 249.7889 | 1256.5698
2042 | QLD | Step Change | 1058.6212 | 5259.7028
2042 | QLD | Green Energy Exports | 2130.0293 | 10569.02
2042 | SA | Progressive Change | 77.422 | 390.8256
2042 | SA | Step Change | 301.0751 | 1487.372
2042 | SA | Green Energy Exports | 613.7375 | 3021.3924
2042 | TAS | Progressive Change | 14.2426 | 71.6648
2042 | TAS | Step Change | 89.6616 | 440.4687
2042 | TAS | Green Energy Exports | 197.43 | 966.9838
2042 | VIC | Progressive Change | 319.8648 | 1614.6116
2042 | VIC | Step Change | 1265.6233 | 6254.3526
2042 | VIC | Green Energy Exports | 2579.8678 | 12711.9077
2043 | NSW | Progressive Change | 449.6056 | 2266.2167
2043 | NSW | Step Change | 1741.5275 | 8634.9146
2043 | NSW | Green Energy Exports | 3509.946 | 17369.7567
2043 | QLD | Progressive Change | 293.6931 | 1477.6004
2043 | QLD | Step Change | 1225.1059 | 6084.9384
2043 | QLD | Green Energy Exports | 2423.7954 | 12024.6773
2043 | SA | Progressive Change | 90.6254 | 457.5345
2043 | SA | Step Change | 346.7278 | 1711.7073
2043 | SA | Green Energy Exports | 697.2429 | 3431.1396
2043 | TAS | Progressive Change | 17.3541 | 87.3547
2043 | TAS | Step Change | 105.172 | 516.3084
2043 | TAS | Green Energy Exports | 224.991 | 1101.5726
2043 | VIC | Progressive Change | 375.7129 | 1896.7564
2043 | VIC | Step Change | 1460.6225 | 7213.3886
2043 | VIC | Green Energy Exports | 2931.27 | 14438.1473
2044 | NSW | Progressive Change | 522.0138 | 2631.4808
2044 | NSW | Step Change | 1989.067 | 9857.9909
2044 | NSW | Green Energy Exports | 3955.5238 | 19570.3067
2044 | QLD | Progressive Change | 341.6184 | 1718.8828
2044 | QLD | Step Change | 1403.6315 | 6969.7013
2044 | QLD | Green Energy Exports | 2736.5241 | 13574.1725
2044 | SA | Progressive Change | 104.9365 | 529.8429
2044 | SA | Step Change | 395.5442 | 1951.4869
2044 | SA | Green Energy Exports | 786.0668 | 3866.8979
2044 | TAS | Progressive Change | 20.8289 | 104.8785
2044 | TAS | Step Change | 121.9191 | 598.1688
2044 | TAS | Green Energy Exports | 254.3521 | 1244.9265
2044 | VIC | Progressive Change | 436.5985 | 2204.3613
2044 | VIC | Step Change | 1669.3957 | 8239.7845
2044 | VIC | Green Energy Exports | 3305.0777 | 16274.1181
2045 | NSW | Progressive Change | 599.4116 | 3022.9664
2045 | NSW | Step Change | 2252.8315 | 11160.9032
2045 | NSW | Green Energy Exports | 4427.6874 | 21901.8841
2045 | QLD | Progressive Change | 392.992 | 1978.2195
2045 | QLD | Step Change | 1594.198 | 7913.9915
2045 | QLD | Green Energy Exports | 3068.2155 | 15217.5057
2045 | SA | Progressive Change | 120.1408 | 606.9341
2045 | SA | Step Change | 447.5241 | 2206.7107
2045 | SA | Green Energy Exports | 880.2092 | 4328.6672
2045 | TAS | Progressive Change | 24.5752 | 123.8752
2045 | TAS | Step Change | 139.9029 | 686.0497
2045 | TAS | Green Energy Exports | 285.5131 | 1397.0454
2045 | VIC | Progressive Change | 501.725 | 2534.3463
2045 | VIC | Step Change | 1891.9428 | 9333.5404
2045 | VIC | Green Energy Exports | 3701.291 | 18219.82
2046 | NSW | Progressive Change | 683.6802 | 3448.1077
2046 | NSW | Step Change | 2532.8212 | 12543.6515
2046 | NSW | Green Energy Exports | 4724.6133 | 23368.5947
2046 | QLD | Progressive Change | 449.0625 | 2260.5402
2046 | QLD | Step Change | 1796.8055 | 8917.8088
2046 | QLD | Green Energy Exports | 3278.6061 | 16259.7448
2046 | SA | Progressive Change | 136.6468 | 690.3418
2046 | SA | Step Change | 502.6675 | 2477.3787
2046 | SA | Green Energy Exports | 935.6164 | 4600.5494
2046 | TAS | Progressive Change | 28.7877 | 145.1255
2046 | TAS | Step Change | 159.1235 | 779.9513
2046 | TAS | Green Energy Exports | 302.3063 | 1479.0076
2046 | VIC | Progressive Change | 572.7621 | 2893.2771
2046 | VIC | Step Change | 2128.2639 | 10494.6563
2046 | VIC | Green Energy Exports | 3961.8062 | 19500.3514
2047 | NSW | Progressive Change | 773.2216 | 3899.8536
2047 | NSW | Step Change | 2829.036 | 14006.2358
2047 | NSW | Green Energy Exports | 5025.2605 | 24853.2456
2047 | QLD | Progressive Change | 508.7576 | 2561.1078
2047 | QLD | Step Change | 2011.454 | 9981.1535
2047 | QLD | Green Energy Exports | 3492.1238 | 17317.2089
2047 | SA | Progressive Change | 154.0624 | 778.3454
2047 | SA | Step Change | 560.9745 | 2763.491
2047 | SA | Green Energy Exports | 991.354 | 4873.9313
2047 | TAS | Progressive Change | 33.3752 | 168.2688
2047 | TAS | Step Change | 179.5807 | 879.8735
2047 | TAS | Green Energy Exports | 319.0945 | 1560.9024
2047 | VIC | Progressive Change | 648.2915 | 3274.903
2047 | VIC | Step Change | 2378.3589 | 11723.1322
2047 | VIC | Green Energy Exports | 4226.9281 | 20803.1444
2048 | NSW | Progressive Change | 868.0876 | 4378.4641
2048 | NSW | Step Change | 3141.4759 | 15548.6562
2048 | NSW | Green Energy Exports | 5329.2978 | 26354.1249
2048 | QLD | Progressive Change | 572.1023 | 2880.0503
2048 | QLD | Step Change | 2238.1434 | 11104.0253
2048 | QLD | Green Energy Exports | 3708.5671 | 18388.8554
2048 | SA | Progressive Change | 172.3893 | 870.9537
2048 | SA | Step Change | 622.4451 | 3065.0476
2048 | SA | Green Energy Exports | 1047.3591 | 5148.4828
2048 | TAS | Progressive Change | 38.3392 | 193.3127
2048 | TAS | Step Change | 201.2747 | 985.8163
2048 | TAS | Green Energy Exports | 335.8633 | 1642.6525
2048 | VIC | Progressive Change | 728.312 | 3679.2188
2048 | VIC | Step Change | 2642.2278 | 13018.968
2048 | VIC | Green Energy Exports | 4496.3924 | 22126.8325
2049 | NSW | Progressive Change | 968.21 | 4883.5934
2049 | NSW | Step Change | 3470.1409 | 17170.9125
2049 | NSW | Green Energy Exports | 5636.3775 | 27869.4719
2049 | QLD | Progressive Change | 639.0916 | 3217.3391
2049 | QLD | Step Change | 2476.8738 | 12286.4244
2049 | QLD | Green Energy Exports | 3927.6696 | 19473.3167
2049 | SA | Progressive Change | 191.6007 | 968.03
2049 | SA | Step Change | 687.0793 | 3382.0484
2049 | SA | Green Energy Exports | 1103.5924 | 5424.0026
2049 | TAS | Progressive Change | 43.6799 | 220.259
2049 | TAS | Step Change | 224.2054 | 1097.7797
2049 | TAS | Green Energy Exports | 352.6198 | 1724.2926
2049 | VIC | Progressive Change | 812.7815 | 4106.0089
2049 | VIC | Step Change | 2919.8707 | 14382.1639
2049 | VIC | Green Energy Exports | 4769.8758 | 23469.7591
2050 | NSW | Progressive Change | 1073.3496 | 5414.0312
2050 | NSW | Step Change | 3772.3471 | 18662.9767
2050 | NSW | Green Energy Exports | 5946.1286 | 29397.3898
2050 | QLD | Progressive Change | 709.5755 | 3572.2187
2050 | QLD | Step Change | 2695.5668 | 13369.762
2050 | QLD | Green Energy Exports | 4149.1811 | 20569.3031
2050 | SA | Progressive Change | 211.6266 | 1069.2202
2050 | SA | Step Change | 746.4391 | 3673.3024
2050 | SA | Green Energy Exports | 1159.9862 | 5700.1438
2050 | TAS | Progressive Change | 49.3974 | 249.1053
2050 | TAS | Step Change | 245.2064 | 1200.3562
2050 | TAS | Green Energy Exports | 369.3523 | 1805.7628
2050 | VIC | Progressive Change | 901.4988 | 4554.2557
2050 | VIC | Step Change | 3174.5909 | 15633.2526
2050 | VIC | Green Energy Exports | 5047.031 | 24830.1471
2051 | NSW | Progressive Change | 1121.8275 | 5658.6503
2051 | NSW | Step Change | 3792.4502 | 18761.0466
2051 | NSW | Green Energy Exports | 5991.5742 | 29618.0224
2051 | QLD | Progressive Change | 742.9357 | 3740.1978
2051 | QLD | Step Change | 2715.4648 | 13467.5332
2051 | QLD | Green Energy Exports | 4186.6121 | 20752.3221
2051 | SA | Progressive Change | 220.4365 | 1113.7407
2051 | SA | Step Change | 747.8953 | 3680.0453
2051 | SA | Green Energy Exports | 1164.5999 | 5721.7262
2051 | TAS | Progressive Change | 52.5358 | 264.945
2051 | TAS | Step Change | 245.0572 | 1199.4845
2051 | TAS | Green Energy Exports | 369.5841 | 1806.5194
2051 | VIC | Progressive Change | 942.885 | 4763.3798
2051 | VIC | Step Change | 3200.8024 | 15761.2089
2051 | VIC | Green Energy Exports | 5100.7633 | 25090.7747
2052 | NSW | Progressive Change | 1165.2949 | 5877.9876
2052 | NSW | Step Change | 3812.2352 | 18857.4065
2052 | NSW | Green Energy Exports | 6035.7581 | 29832.0454
2052 | QLD | Progressive Change | 773.2717 | 3892.9491
2052 | QLD | Step Change | 2735.1986 | 13564.3858
2052 | QLD | Green Energy Exports | 4223.2783 | 20931.2714
2052 | SA | Progressive Change | 228.2559 | 1153.2558
2052 | SA | Step Change | 749.2533 | 3686.2661
2052 | SA | Green Energy Exports | 1168.9006 | 5741.6818
2052 | TAS | Progressive Change | 55.3524 | 279.1607
2052 | TAS | Step Change | 244.894 | 1198.5345
2052 | TAS | Green Energy Exports | 369.75 | 1806.9288
2052 | VIC | Progressive Change | 980.3487 | 4952.6841
2052 | VIC | Step Change | 3226.9843 | 15888.898
2052 | VIC | Green Energy Exports | 5153.8512 | 25347.8289

## Electrification
Go to Assumptions Summary
Electrification (TWh) | [8 empty] | Note: | Further information is available at https://forecasting.aemo.com.au
Electrification of end-use energy consumption otherwise served by other fuels (e.g. gas heating, cooking and industrial processes)
The values also include electrification of the transportation sector.
Transport sector electrification is based on CSIRO's 2022 EV study. Electrification in other sectors is based on 2022 CSIRO/ClimateWorks Australia multi-sector study.
Electrification Alternatives sensitivity is based on Step Change but with a reduced pace and breadth of industrial electrification.
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports | Electrification Alternatives (Sensitivity)
Consultant's scenario name | Progressive Change | Step Change | Hydrogen Export | Sensitivity based on Step Change
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 0.9119 | 1.8758 | 3.0036 | 4.0414 | 4.8511 | 5.3951 | 5.7914 | 6.1987 | 6.7341 | 7.2322 | 7.9022 | 8.6208 | 9.5222 | 10.3443 | 11.1817 | 12.0235 | 12.9529 | 13.6769 | 14.3602 | 14.8847 | 15.4259 | 16.0568 | 16.8352 | 17.7561 | 18.7248 | 19.668 | 20.6388 | 21.4991 | 22.352 | 23.0655 | 23.7615
QLD | 0.10236 | 0.18397 | 0.53798 | 0.92716 | 1.4832 | 2.1419 | 3.052 | 3.9719 | 4.7093 | 5.7005 | 6.8732 | 8.1764 | 9.66 | 11.4527 | 12.5036 | 13.5833 | 15.3608 | 15.9968 | 16.6906 | 17.6588 | 18.7527 | 19.6915 | 20.7833 | 22.1849 | 23.3796 | 26.6981 | 29.3207 | 31.9893 | 32.3694 | 33.2028 | 34.3358
SA | 0.048796 | 0.18387 | 0.40463 | 0.73606 | 1.0337 | 1.2729 | 1.3907 | 1.4782 | 1.5805 | 1.6834 | 1.7951 | 1.9371 | 2.2153 | 2.5061 | 2.7849 | 2.9668 | 3.1959 | 3.4754 | 3.7751 | 4.0402 | 4.2627 | 4.4339 | 4.5631 | 4.6362 | 4.7368 | 4.8553 | 5.0251 | 5.1757 | 5.377 | 5.5467 | 5.7328
TAS | 0.045767 | 0.083139 | 0.11268 | 0.15339 | 0.23454 | 0.42849 | 0.73036 | 1.0045 | 1.2713 | 1.4067 | 1.5301 | 1.5567 | 1.6052 | 1.6644 | 1.7276 | 1.7891 | 1.87 | 1.9515 | 2.0456 | 2.1085 | 2.1691 | 2.2247 | 2.28 | 2.3336 | 2.4533 | 2.5177 | 2.4932 | 2.3672 | 2.263 | 2.2354 | 2.2408
VIC | 0.72029 | 1.2435 | 1.6818 | 2.217 | 3.0157 | 4.0595 | 5.0259 | 5.9145 | 6.6847 | 7.3089 | 7.9193 | 8.5661 | 9.4575 | 10.5463 | 11.5886 | 12.6701 | 13.6406 | 14.7533 | 15.8839 | 17.0189 | 18.1502 | 19.2486 | 20.3268 | 21.4196 | 22.4148 | 23.4532 | 24.3633 | 25.1942 | 26.0176 | 26.7512 | 27.5272
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 0.51005 | 1.2931 | 2.6978 | 4.596 | 6.2447 | 7.7664 | 8.9096 | 10.1693 | 11.3826 | 12.6034 | 13.9484 | 15.2674 | 16.823 | 18.3081 | 19.8066 | 21.2911 | 23.0178 | 24.7024 | 26.4419 | 27.9505 | 29.4004 | 30.6674 | 32.0298 | 33.3371 | 34.7508 | 35.9627 | 37.2339 | 37.8904 | 38.3219 | 38.5243 | 38.8891
QLD | 0.78304 | 1.9803 | 3.5106 | 4.7421 | 5.8312 | 7.257 | 8.8055 | 10.1921 | 11.4086 | 12.7305 | 14.033 | 14.9854 | 16.7634 | 18.455 | 20.2989 | 21.571 | 23.2033 | 24.804 | 26.4014 | 27.7417 | 29.0074 | 30.1191 | 31.2233 | 32.5467 | 33.6025 | 34.4126 | 35.1439 | 35.889 | 36.8013 | 37.5645 | 38.3744
SA | 0.057216 | 0.14233 | 0.40382 | 0.78281 | 1.1693 | 1.6011 | 1.9748 | 2.3913 | 2.6709 | 2.942 | 3.2743 | 3.751 | 4.302 | 4.8715 | 5.2988 | 5.7131 | 6.075 | 6.5008 | 6.9224 | 7.3298 | 7.6771 | 7.986 | 8.2376 | 8.4167 | 8.6164 | 8.7641 | 8.9599 | 9.0159 | 9.0668 | 9.0767 | 9.1667
TAS | 0.035867 | 0.10758 | 0.20382 | 0.26947 | 0.28955 | 0.31803 | 0.36302 | 0.56902 | 1.0112 | 1.4478 | 1.7721 | 1.8774 | 1.9896 | 2.0976 | 2.2233 | 2.3512 | 2.4653 | 2.564 | 2.6831 | 2.8177 | 2.9539 | 3.0702 | 3.1609 | 3.237 | 3.3064 | 3.3326 | 3.3429 | 3.1685 | 2.894 | 2.6234 | 2.5149
VIC | 0.23865 | 0.57828 | 1.164 | 1.9732 | 2.9907 | 4.1301 | 5.1628 | 6.3286 | 7.7457 | 9.2465 | 11.1144 | 12.9883 | 15.0196 | 16.8867 | 18.6235 | 20.2964 | 21.8241 | 23.2722 | 24.809 | 26.3413 | 28.0208 | 29.5026 | 31.0046 | 32.3894 | 33.9073 | 35.287 | 36.5416 | 37.1957 | 37.4909 | 37.5928 | 37.8042
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 0.9015 | 1.6205 | 2.6124 | 3.5813 | 5.1695 | 7.0453 | 8.9955 | 11.3212 | 13.5364 | 15.7504 | 17.5212 | 19.2219 | 21.0557 | 22.9614 | 25.09 | 27.2213 | 29.4637 | 31.4268 | 33.2019 | 34.7935 | 36.5018 | 38.2216 | 39.4284 | 39.9978 | 40.5515 | 40.8581 | 41.2215 | 41.5341 | 42.0595 | 42.4608 | 43.2194
QLD | 0.89164 | 1.7086 | 2.5811 | 3.172 | 4.4904 | 6.6745 | 9.638 | 12.6436 | 15.0606 | 16.6772 | 18.1423 | 19.9624 | 22.0908 | 24.1424 | 26.1466 | 28.2188 | 30.2558 | 32.1601 | 34.2008 | 36.1977 | 38.0497 | 39.4752 | 40.6243 | 41.3854 | 42.1838 | 42.592 | 42.6513 | 42.7229 | 43.6614 | 44.906 | 46.3286
SA | 0.24071 | 0.40759 | 0.67481 | 1.2191 | 1.4253 | 1.6613 | 2.0371 | 2.8251 | 3.5343 | 4.2322 | 4.7356 | 5.1679 | 5.5529 | 6.0588 | 6.5807 | 7.0883 | 7.7677 | 8.4068 | 9.0623 | 9.4271 | 9.8171 | 10.1514 | 10.4294 | 10.5627 | 10.7248 | 10.7261 | 10.7329 | 10.6502 | 10.6027 | 10.5314 | 10.5695
TAS | 0.070883 | 0.11406 | 0.33267 | 0.55046 | 0.78817 | 0.88156 | 0.9789 | 1.1931 | 1.616 | 2.0503 | 2.388 | 2.4659 | 2.5506 | 2.7007 | 2.8867 | 3.0734 | 3.2327 | 3.3891 | 3.5473 | 3.654 | 3.761 | 3.8394 | 3.9106 | 3.954 | 4.0077 | 4.0438 | 4.0788 | 4.0135 | 3.8127 | 3.571 | 3.4291
VIC | 0.81828 | 1.4266 | 2.5482 | 4.5449 | 7.6704 | 10.6166 | 12.8739 | 14.7523 | 16.9436 | 19.3081 | 21.5547 | 23.2899 | 24.8743 | 26.5322 | 28.5236 | 30.452 | 32.4137 | 34.1978 | 36.0208 | 37.709 | 39.471 | 41.0641 | 41.9739 | 42.3289 | 42.4649 | 42.7071 | 43.0196 | 43.1028 | 42.7179 | 42.1383 | 42.1502
Electrification Alternatives (Sensitivity)
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 0.44551 | 1.0483 | 1.9643 | 3.0132 | 4.0339 | 5.0709 | 6.1018 | 7.2369 | 8.4592 | 10.0352 | 11.7414 | 13.4205 | 15.0402 | 16.569 | 18.1775 | 19.7654 | 21.472 | 23.0595 | 24.687 | 26.2584 | 27.8294 | 29.2399 | 30.7186 | 32.1244 | 33.61 | 34.9124 | 36.2484 | 36.973 | 37.4362 | 37.6758 | 38.0712
QLD | 0.53458 | 1.2341 | 2.0442 | 2.758 | 3.3471 | 4.1787 | 5.1182 | 6.2826 | 7.5535 | 9.2353 | 10.8222 | 12.3552 | 13.9565 | 15.7002 | 17.3412 | 18.809 | 20.3438 | 21.7894 | 23.2956 | 24.6828 | 26.0063 | 27.1782 | 28.3484 | 29.7182 | 30.8322 | 31.6696 | 32.3926 | 33.0751 | 33.9057 | 34.6089 | 35.3652
SA | 0.05718 | 0.14228 | 0.32635 | 0.54029 | 0.7918 | 1.0364 | 1.2895 | 1.5528 | 1.829 | 2.1423 | 2.5044 | 2.9906 | 3.565 | 4.1681 | 4.657 | 5.0549 | 5.4262 | 5.8328 | 6.2544 | 6.6496 | 6.993 | 7.3061 | 7.5588 | 7.7401 | 7.941 | 8.0883 | 8.2827 | 8.3351 | 8.3833 | 8.3963 | 8.4921
TAS | 0.035365 | 0.092328 | 0.16598 | 0.20501 | 0.20949 | 0.23498 | 0.27743 | 0.48942 | 0.91324 | 1.2054 | 1.5357 | 1.6677 | 1.9305 | 2.0405 | 2.1554 | 2.2764 | 2.3855 | 2.4816 | 2.5973 | 2.7284 | 2.8634 | 2.9811 | 3.074 | 3.1524 | 3.2231 | 3.2489 | 3.2571 | 3.078 | 2.7999 | 2.5262 | 2.4149
VIC | 0.23371 | 0.56476 | 1.1424 | 1.9371 | 2.9471 | 4.0727 | 5.0943 | 6.2488 | 7.6605 | 9.1595 | 11.0114 | 12.8693 | 14.9003 | 16.7749 | 18.5029 | 20.1586 | 21.6623 | 23.1037 | 24.6187 | 26.1392 | 27.8046 | 29.2821 | 30.7793 | 32.1623 | 33.6769 | 35.0507 | 36.294 | 36.9285 | 37.2113 | 37.3014 | 37.5022

## Embedded energy storages
Go to Assumptions Summary
Distributed Energy Resources: Total embedded energy storage systems (aggregated and non-aggregated) | [16 empty] | Note: | Further information is available at https://forecasting.aemo.com.au
Embedded energy storage forecasts based on 2022 CSIRO and Green Energy Markets (GEM) trajectories developed for AEMO
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | CSIRO Progressive Change | Average CSIRO/GEM Step Change | Average CSIRO/GEM Hydrogen Export
Embedded energy storages (small-scale batteries, MW)
Embedded battery installations by NEM region. The use of batteries in managing consumer demand is 'netted' off the operational demand forecasts if 'non-aggregated', whereas the 'aggregated' share is modelled like a Virtual Power Plant, operated by a retailer / aggregator as an alternative supply source for arbitrage or emergency response.
Battery power (MW) of Embedded battery installations by NEM region.
Embedded battery storages are the cumulative total of "aggregated" and "non-aggregated" battery installations in the NEM.
Progressive Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 270.529 | 307.906 | 341.985 | 374.955 | 407.134 | 441.31 | 478.174 | 523.932 | 563.352 | 605.611 | 649.282 | 696.521 | 746.245 | 798.425 | 850.258 | 904.824 | 959.293 | 1010.86 | 1058.994 | 1105.309 | 1149.03 | 1190.8939 | 1240.371 | 1292.442 | 1346.895 | 1403.9131 | 1456.9299 | 1506.0089 | 1554.983 | 1598.967 | 1635.313 | 1672.338
QLD | 121.043 | 132.077 | 152.677 | 173.283 | 194.2 | 216.866 | 241.838 | 273.224 | 301.35 | 332.019 | 364.305 | 399.759 | 437.692 | 478.137 | 518.797 | 562.003 | 605.385 | 646.45 | 684.2921 | 721.2939 | 757.648 | 793.529 | 835.46 | 879.712 | 926.143 | 974.914 | 1020.895 | 1064.072 | 1103.778 | 1139.626 | 1169.38 | 1199.654
SA | 192.519 | 227.111 | 248.182 | 268.399 | 287.79 | 307.915 | 329.127 | 354.556 | 376.291 | 399.083 | 422.136 | 446.525 | 471.617 | 497.356 | 522.285 | 547.894 | 572.752 | 595.545 | 616.056 | 635.599 | 654.356 | 672.466 | 693.189 | 714.528 | 736.39 | 758.832 | 779.437 | 798.31 | 815.957 | 831.577 | 844.2939 | 857.074
TAS | 15.925 | 17.079 | 19.22 | 21.315 | 23.359 | 25.553 | 27.951 | 31.112 | 33.683 | 36.439 | 39.293 | 42.409 | 45.702 | 49.166 | 52.571 | 56.155 | 59.677 | 62.898 | 65.774 | 68.491 | 71.079 | 73.562 | 76.535 | 79.642 | 82.873 | 86.248 | 89.286 | 91.997 | 94.927 | 97.462 | 99.409 | 101.375
VIC | 231.216 | 280.428 | 316.66 | 352.627 | 388.55 | 427.171 | 469.349 | 522.314 | 568.576 | 618.5489 | 670.738 | 727.558 | 787.801 | 851.488 | 915.161 | 982.497 | 1049.891 | 1113.654 | 1172.893 | 1230.7401 | 1287.3779 | 1343.2009 | 1407.631 | 1475.2019 | 1545.829 | 1619.825 | 1689.522 | 1754.9901 | 1818.287 | 1876.042 | 1925.057 | 1975.15
Step Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 261.652 | 313.9765 | 507.034 | 794.6675 | 1107.3995 | 1457.168 | 1817.457 | 2359.4146 | 2850.386 | 3332.8884 | 3843.5469 | 4378.4448 | 4962.1787 | 5568.2974 | 6087.8608 | 6633.3013 | 7204.2832 | 7661.0713 | 8095.1831 | 8512.1123 | 8932.4141 | 9343.0693 | 9778.2666 | 10219.1895 | 10597.792 | 10977.7529 | 11334.3047 | 11667.5283 | 11990.2031 | 12304.875 | 12598.166 | 12890.7471
QLD | 138.099 | 164.284 | 265.1535 | 464.773 | 653.0545 | 878.694 | 1126.397 | 1533.2886 | 1909.3921 | 2273.8379 | 2651.0015 | 3044.1665 | 3442.9539 | 3884.2944 | 4237.6382 | 4611.9404 | 5011.0601 | 5351.2803 | 5685.5195 | 6009.7646 | 6329.5581 | 6643.5435 | 6966.8901 | 7304.8555 | 7601.4766 | 7900.3887 | 8195.1543 | 8474.583 | 8731.8623 | 8983.1377 | 9218.8984 | 9454.2539
SA | 165.3635 | 199.899 | 271.558 | 358.737 | 449.3785 | 553.743 | 662.754 | 831.2 | 978.8075 | 1119.9425 | 1265.5126 | 1415.4105 | 1576.8099 | 1736.6475 | 1873.1536 | 2021.793 | 2182.4695 | 2317.5625 | 2441.29 | 2556.5835 | 2670.667 | 2780.2275 | 2895.4641 | 3009.9302 | 3106.3464 | 3202.3955 | 3294.5469 | 3381.0696 | 3463.4036 | 3543.1526 | 3617.2046 | 3690.886
TAS | 17.17 | 20.004 | 28.5005 | 41.4245 | 55.8125 | 72.305 | 90.4755 | 118.1715 | 144.516 | 171.3825 | 199.4575 | 228.961 | 259.72 | 292.023 | 320.3725 | 350.968 | 384.284 | 412.6545 | 440.3395 | 467.606 | 494.9425 | 522.0595 | 550.5185 | 579.414 | 604.549 | 630.101 | 654.774 | 678.3285 | 700.4195 | 721.859 | 741.783 | 761.6515
VIC | 203.4595 | 263.112 | 417.1795 | 635.899 | 867.0375 | 1121.3785 | 1363.5815 | 1724.3915 | 2059.323 | 2392.2795 | 2742.344 | 3114.8464 | 3530.0759 | 3980.2595 | 4382.0107 | 4807.5586 | 5237.1924 | 5609.9424 | 5974.3428 | 6334.4595 | 6695.4932 | 7058.2935 | 7450.814 | 7863.4023 | 8229.0215 | 8601.6816 | 8963.5527 | 9317.666 | 9650.5371 | 9975.0762 | 10278.6328 | 10583.0996
Green Energy Exports
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 260.9465 | 311.0095 | 455.6215 | 764.8255 | 1113.458 | 1536.412 | 1985.043 | 2668.2715 | 3294.9126 | 3934.8088 | 4582.3125 | 5229.2456 | 5819.6885 | 6445.8462 | 6973.5835 | 7524.3003 | 8107.7583 | 8568.9053 | 9009.5684 | 9431.5957 | 9850.3418 | 10246.9395 | 10647.9756 | 11065.5713 | 11444.5371 | 11833.8516 | 12195.6631 | 12533.6885 | 12846.751 | 13145.2441 | 13407.8896 | 13671.2295
QLD | 134.4635 | 158.319 | 218.157 | 439.094 | 686.123 | 995.143 | 1340.666 | 1865.0099 | 2365.042 | 2864.7473 | 3365.5295 | 3866.897 | 4284.8115 | 4754.5488 | 5141.8628 | 5566.2046 | 6019.5747 | 6376.6328 | 6714.7822 | 7042.5703 | 7368.5981 | 7684.0854 | 7993.2539 | 8330.0068 | 8630.8691 | 8940.2637 | 9234.0195 | 9507.9082 | 9763.2168 | 10009.248 | 10228.9453 | 10449.4766
SA | 166.237 | 200.977 | 286.7375 | 393.233 | 504.8725 | 642.0845 | 789.4145 | 1005.6609 | 1194.6289 | 1378.3885 | 1552.572 | 1720.8115 | 1885.4775 | 2036.915 | 2164.4604 | 2309.1748 | 2469.3035 | 2596.4189 | 2714.9343 | 2826.606 | 2936.0032 | 3038.603 | 3147.8979 | 3255.0195 | 3354.7205 | 3456.6677 | 3552.3369 | 3641.1165 | 3726.772 | 3808.79 | 3881.5879 | 3954.6301
TAS | 17.322 | 20.2115 | 27.272 | 41.293 | 57.4375 | 77.9595 | 102.229 | 139.0675 | 173.775 | 208.0745 | 241.7735 | 275.143 | 304.758 | 335.6055 | 361.9135 | 390.668 | 422.602 | 448.6075 | 474.031 | 499.0575 | 524.4415 | 549.215 | 574.3235 | 600.2935 | 623.9895 | 648.4805 | 671.617 | 693.1201 | 713.9885 | 733.894 | 751.246 | 768.601
VIC | 205.577 | 256.0635 | 405.0475 | 649.444 | 917.4495 | 1230.61 | 1576.4945 | 2095.498 | 2575.1799 | 3036.5146 | 3487.886 | 3936.7344 | 4368.9819 | 4821.1909 | 5222.7827 | 5645.8242 | 6094.1606 | 6472.3208 | 6841.9497 | 7205.1304 | 7573.6001 | 7938.1509 | 8328.5566 | 8732.0977 | 9111.0225 | 9506.8604 | 9889.3076 | 10257.7324 | 10607.5186 | 10946.8691 | 11249.9766 | 11555.4609
Embedded energy storages (small-scale batteries, degraded MWh)
Storage capacity (degraded MWh) of Embedded battery installations by NEM region.
Embedded battery storages are the cumulative total of "aggregated" and "non-aggregated" battery installations in the NEM.
Progressive Change
Progressive Change | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 573.665 | 647.99 | 712.275 | 773.103 | 831.214 | 892.763 | 959.215 | 1044.038 | 1113.665 | 1188.389 | 1264.988 | 1348.155 | 1435.412 | 1526.626 | 1615.5929 | 1709.11 | 1800.8981 | 1884.855 | 1959.988 | 2029.9131 | 2093.0081 | 2151.009 | 2224.793 | 2303.1052 | 2385.3828 | 2471.9629 | 2548.396 | 2614.979 | 2680.2888 | 2733.6179 | 2769.374 | 2806.0491
QLD | 252.483 | 272.861 | 312.919 | 352.367 | 391.836 | 434.455 | 481.36 | 541.29 | 593.291 | 649.935 | 709.096 | 774.106 | 843.352 | 916.817 | 989.481 | 1066.407 | 1142.4241 | 1212.1791 | 1274.0911 | 1333.093 | 1389.678 | 1444.2529 | 1511.137 | 1581.9829 | 1656.4041 | 1734.6631 | 1805.5751 | 1869.2371 | 1924.276 | 1970.101 | 2002.08 | 2034.746
SA | 405.446 | 473.992 | 512.033 | 547.606 | 580.779 | 614.998 | 650.988 | 695.39 | 731.192 | 768.6721 | 806.047 | 845.651 | 886.065 | 927.143 | 965.7401 | 1005.128 | 1042.215 | 1074.239 | 1100.885 | 1124.9801 | 1146.957 | 1167.147 | 1192.703 | 1219.196 | 1246.3929 | 1274.385 | 1297.984 | 1317.4921 | 1334.0699 | 1346.0699 | 1351.718 | 1357.437
TAS | 33.502 | 35.647 | 39.728 | 43.642 | 47.383 | 51.387 | 55.774 | 61.738 | 66.331 | 71.255 | 76.309 | 81.849 | 87.682 | 93.791 | 99.665 | 105.835 | 111.767 | 116.951 | 121.301 | 125.235 | 128.821 | 132.12 | 136.441 | 140.985 | 145.731 | 150.709 | 154.879 | 158.268 | 162.099 | 165.008 | 166.599 | 168.205
VIC | 487.876 | 586.679 | 656.208 | 724.054 | 790.693 | 862.139 | 940.174 | 1040.35 | 1124.429 | 1215.223 | 1309.322 | 1411.963 | 1520.343 | 1634.4091 | 1746.5331 | 1864.7839 | 1981.214 | 2087.8401 | 2183.0349 | 2273.5959 | 2360.0281 | 2443.25 | 2543.97 | 2649.946 | 2760.884 | 2877.364 | 2982.6021 | 3076.928 | 3164.9978 | 3239.5789 | 3293.9512 | 3349.8152
Step Change
Step Change | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 562.6285 | 668.144 | 1116.9399 | 1782.2565 | 2484.7915 | 3253.396 | 4007.9973 | 5181.394 | 6182.5947 | 7120.0811 | 8086.481 | 9073.7803 | 10261.3193 | 11538.917 | 12565.1855 | 13645.4121 | 14739.7998 | 15672.0439 | 16472.9043 | 17187.5703 | 17906.3203 | 18597.9023 | 19486.6582 | 20455.084 | 21160.5352 | 21896.9727 | 22569.9668 | 23217.6133 | 23766.127 | 24247.791 | 24692.1211 | 25134.9258
QLD | 297.689 | 350.0015 | 582.357 | 1049.662 | 1467.052 | 1960.4449 | 2484.6001 | 3381.9595 | 4167.9595 | 4892.8008 | 5616.6641 | 6349.6792 | 7120.7065 | 8055.665 | 8710.8486 | 9422.0293 | 10178.5088 | 10905.7432 | 11568.0215 | 12166.2109 | 12738.1865 | 13288.0967 | 13893.3809 | 14638.7764 | 15140.9863 | 15677.9053 | 16222.1445 | 16799.4395 | 17282.5254 | 17710.5723 | 18092.1855 | 18467.5273
SA | 356.769 | 425.4785 | 583.2685 | 773.088 | 964.292 | 1183.4469 | 1407.4285 | 1775.0089 | 2078.6851 | 2352.2334 | 2625.8606 | 2900.0542 | 3221.9236 | 3538.4634 | 3784.5034 | 4063.1528 | 4365.2524 | 4651.8745 | 4886.1509 | 5082.0532 | 5271.9521 | 5448.9614 | 5673.1826 | 5895.6895 | 6042.1685 | 6206.2124 | 6372.292 | 6554.7915 | 6700.0596 | 6818.2495 | 6923.7231 | 7026.3701
TAS | 37.242 | 42.8545 | 61.728 | 90.775 | 122.3135 | 158.2 | 196.6395 | 257.103 | 312.4215 | 366.8885 | 422.0075 | 478.4235 | 539.1015 | 604.8435 | 658.812 | 718.0135 | 782.453 | 840.375 | 894.447 | 945.8 | 996.2325 | 1045.5225 | 1100.354 | 1158.8829 | 1202.4399 | 1249.168 | 1295.6261 | 1341.3169 | 1381.8684 | 1419.4535 | 1453.299 | 1486.9945
VIC | 439.217 | 565.1825 | 919.717 | 1418.401 | 1925.6949 | 2471.2915 | 2960.489 | 3722.8086 | 4399.3652 | 5046.7231 | 5709.5508 | 6412.4414 | 7270.6387 | 8234.2656 | 9038.3096 | 9884.2158 | 10681.5146 | 11408.6699 | 12080.3408 | 12713.3701 | 13337.0078 | 13973.8086 | 14770.9199 | 15667.4209 | 16361.0635 | 17079.6875 | 17724.2891 | 18374.9844 | 18944.957 | 19467.5859 | 19937.9746 | 20427.1152
Green Energy Exports
Green Energy Exports | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 559.47 | 658.5925 | 976.85 | 1696.168 | 2485.7036 | 3429.0815 | 4390.4546 | 5894.8486 | 7202.0957 | 8487.917 | 9741.4121 | 10939.959 | 11990.9814 | 13247.873 | 14232.3594 | 15296.3975 | 16405.7461 | 17381.1934 | 18223.3105 | 18999.5293 | 19751.6875 | 20418.9961 | 21052.2227 | 21897.9648 | 22538.9844 | 23274.4414 | 23959.5117 | 24665.0957 | 25225.1035 | 25732.8418 | 26151.3672 | 26535.3594
QLD | 288.2675 | 334.8075 | 459.4465 | 983.498 | 1547.2939 | 2239.1069 | 2985.3835 | 4141.4927 | 5190.3555 | 6197.5078 | 7170.1279 | 8104.8374 | 8794.3906 | 9749.2021 | 10468.5947 | 11295.5762 | 12173.2451 | 12930.0791 | 13582.2197 | 14188.1328 | 14778.8477 | 15326.5596 | 15754.5 | 16454.6914 | 16962.582 | 17551.0742 | 18122.957 | 18689.9863 | 19148.8535 | 19567.9727 | 19923.4434 | 20264.1152
SA | 358.3815 | 427.1665 | 614.4675 | 846.2555 | 1082.7305 | 1374.3154 | 1682.8325 | 2155.467 | 2545.5898 | 2906.2825 | 3230.7896 | 3528.5549 | 3834.2542 | 4112.1636 | 4320.5659 | 4583.0737 | 4884.7876 | 5161.396 | 5388.7676 | 5585.854 | 5766.0024 | 5919.8066 | 6110.313 | 6295.5371 | 6431.5376 | 6604.2642 | 6783.3228 | 6977.999 | 7133.582 | 7265.7783 | 7367.5303 | 7457.5127
TAS | 37.564 | 43.2735 | 57.8995 | 89.559 | 125.1055 | 170.31 | 222.7305 | 304.0765 | 377.5385 | 447.411 | 513.51 | 576.4665 | 627.8765 | 687.5265 | 734.1295 | 788.0965 | 849.88 | 905.005 | 955.206 | 1002.4705 | 1049.308 | 1093.4775 | 1133.3715 | 1182.6765 | 1220.375 | 1264.002 | 1308.2054 | 1352.0864 | 1391.1765 | 1426.7305 | 1456.03 | 1484.3566
VIC | 443.711 | 546.0665 | 879.2465 | 1438.0349 | 2029.3364 | 2707.3713 | 3434.6189 | 4559.4004 | 5551.4351 | 6464.7578 | 7323.7998 | 8145.9956 | 8950.8877 | 9867.8037 | 10623.6768 | 11425.707 | 12268.3105 | 13048.3867 | 13750.6582 | 14399.084 | 15038.7998 | 15650.0586 | 16339.7236 | 17154.2227 | 17822.1719 | 18546.9785 | 19249.5508 | 19975.3828 | 20597.6465 | 21160.9805 | 21628.3984 | 22086.125

## Aggregated energy storages
Go to Assumptions Summary
Distributed Energy Resources: Aggregated embedded energy storage systems | [13 empty] | Note: | Further information is available at https://forecasting.aemo.com.au
Aggregated embedded energy storage (VPP) forecasts based using the Embedded energy storage forecast.
Aggregated embedded energy storages (small-scale batteries, MW)
The use of batteries in managing consumer demand is 'netted' off the operational demand forecasts if 'non-aggregated', whereas the 'aggregated' share is modelled like a Virtual Power Plant (VPP), operated by a retailer / aggregator as an alternative supply source for arbitrage or emergency response.
Progressive Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
NSW | 9.198 | 13.5479 | 18.1252 | 23.2472 | 29.3136 | 35.7461 | 43.5138 | 52.3932 | 59.152 | 66.6172 | 74.6674 | 83.5825 | 93.2806 | 103.7953 | 114.7849 | 126.6753 | 139.0975 | 151.629 | 164.144 | 176.8495 | 189.59 | 202.452 | 217.0649 | 232.6395 | 249.1756 | 266.7435 | 284.1013 | 301.2018 | 310.9966 | 319.7934
QLD | 4.5996 | 6.0755 | 8.3972 | 11.0901 | 14.1766 | 17.783 | 22.0073 | 27.3224 | 31.6418 | 36.5221 | 41.8951 | 47.9711 | 54.7115 | 62.1578 | 70.0376 | 78.6804 | 87.7808 | 96.9675 | 106.0653 | 115.4071 | 125.0119 | 134.8999 | 146.2055 | 158.3481 | 171.3365 | 185.2337 | 199.0745 | 212.8144 | 220.7556 | 227.9252
SA | 47.5522 | 57.9133 | 65.0237 | 72.4677 | 79.7178 | 87.7558 | 96.1051 | 106.3668 | 114.7688 | 123.7157 | 132.9728 | 142.888 | 153.2755 | 164.1274 | 174.9655 | 186.284 | 197.5994 | 208.4407 | 218.6999 | 228.8156 | 238.8399 | 248.8125 | 259.9459 | 271.5207 | 283.5102 | 295.9445 | 307.8776 | 319.324 | 326.3828 | 332.6308
TAS | 0.36628 | 0.58069 | 0.8649 | 1.1936 | 1.5651 | 1.9931 | 2.4876 | 3.1112 | 3.5367 | 4.0083 | 4.5187 | 5.0891 | 5.7127 | 6.3916 | 7.0971 | 7.8617 | 8.6532 | 9.4347 | 10.195 | 10.9586 | 11.728 | 12.5055 | 13.3936 | 14.3356 | 15.3315 | 16.3871 | 17.4108 | 18.3994 | 18.9854 | 19.4924
VIC | 6.2428 | 10.6563 | 15.1997 | 20.805 | 26.81 | 33.7465 | 42.2414 | 52.2314 | 59.7005 | 68.0404 | 77.1349 | 87.307 | 98.4751 | 110.6934 | 123.5468 | 137.5496 | 152.2342 | 167.0481 | 181.7985 | 196.9184 | 212.4173 | 228.3442 | 246.3354 | 265.5363 | 285.9784 | 307.7668 | 329.4568 | 350.998 | 363.6574 | 375.2084
Step Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
NSW | 36.6327 | 63.9029 | 154.9386 | 300.3544 | 482.6633 | 712.1225 | 976.8226 | 1396.8087 | 1737.2329 | 2079.9289 | 2452.2793 | 2852.0663 | 3299.5765 | 3773.3866 | 4193.5355 | 4642.7098 | 5123.8947 | 5523.634 | 5918.1289 | 6305.3334 | 6705.9892 | 7106.9246 | 7532.974 | 7966.0728 | 8355.0044 | 8746.1317 | 9128.4208 | 9498.9618 | 9749.4507 | 9995.9376
QLD | 22.1712 | 38.4553 | 86.4774 | 185.8998 | 294.3175 | 438.7656 | 614.2438 | 919.3758 | 1176.6012 | 1431.8433 | 1703.1988 | 1993.0237 | 2293.7744 | 2632.6734 | 2912.8231 | 3214.9545 | 3544.5216 | 3833.6187 | 4127.9361 | 4419.1522 | 4714.7009 | 5011.5494 | 5319.6086 | 5641.6879 | 5935.4712 | 6232.2302 | 6534.5715 | 6830.3094 | 7029.3777 | 7225.4424
SA | 51.8845 | 65.5112 | 96.9892 | 140.5023 | 189.623 | 250.8409 | 319.7175 | 434.7248 | 533.5624 | 630.724 | 734.5779 | 844.6098 | 966.4629 | 1089.7168 | 1199.047 | 1320.2428 | 1454.7558 | 1571.6712 | 1684.0846 | 1791.4889 | 1901.3509 | 2009.6168 | 2124.2514 | 2238.6657 | 2340.5872 | 2442.3376 | 2544.2996 | 2643.4359 | 2706.2135 | 2767.6991
TAS | 0.90883 | 1.5834 | 2.9955 | 6.3024 | 11.2404 | 18.1662 | 27.2134 | 41.7757 | 55.1218 | 70.0423 | 86.9863 | 106.0963 | 127.4478 | 151.1852 | 174.2747 | 200.1663 | 229.5419 | 257.1102 | 282.5331 | 308.5246 | 335.7091 | 363.7024 | 393.5399 | 424.3446 | 453.1212 | 482.6997 | 512.7009 | 542.716 | 560.1745 | 577.3073
VIC | 26.3337 | 51.2821 | 121.2397 | 227.7632 | 356.4866 | 514.7882 | 682.6875 | 948.1919 | 1166.7138 | 1389.1777 | 1630.4403 | 1894.1295 | 2196.1545 | 2530.1205 | 2836.3627 | 3167.2 | 3510.4818 | 3814.9192 | 4124.3851 | 4435.2786 | 4756.4181 | 5085.8518 | 5443.9125 | 5819.9969 | 6164.9017 | 6516.1322 | 6869.9351 | 7225.7406 | 7476.9435 | 7723.9808
Green Energy Exports
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
NSW | 34.8006 | 59.2944 | 115.0548 | 254.1215 | 434.6323 | 679.9621 | 973.4315 | 1460.9195 | 1869.7131 | 2302.8287 | 2759.1481 | 3228.8996 | 3670.0496 | 4152.4544 | 4570.3847 | 5024.0137 | 5514.3914 | 5922.3923 | 6319.2327 | 6711.1361 | 7105.4621 | 7493.0912 | 7879.1902 | 8282.8556 | 8655.1236 | 9038.0751 | 9404.2225 | 9761.4511 | 9979.3106 | 10190.613
QLD | 20.6537 | 35.1594 | 57.352 | 159.79 | 290.8398 | 472.5054 | 695.2024 | 1061.9893 | 1378.1344 | 1707.8786 | 2055.2889 | 2416.4143 | 2727.7754 | 3091.2926 | 3398.8125 | 3742.3488 | 4116.7565 | 4425.6614 | 4723.8896 | 5021.1439 | 5320.7306 | 5620.2459 | 5910.6155 | 6227.0777 | 6514.2107 | 6810.2772 | 7098.0542 | 7377.2063 | 7552.6235 | 7723.864
SA | 51.3615 | 64.4365 | 97.4581 | 144.4493 | 197.5895 | 268.5136 | 351.4953 | 487.7334 | 606.9216 | 728.1797 | 849.1967 | 970.9595 | 1095.1451 | 1215.1739 | 1319.211 | 1439.2857 | 1574.564 | 1688.2334 | 1796.5481 | 1902.1943 | 2007.4506 | 2110.579 | 2217.8846 | 2324.5612 | 2425.6774 | 2530.0395 | 2630.7266 | 2728.5725 | 2788.6809 | 2847.1528
TAS | 0.87463 | 1.5253 | 2.7416 | 5.9315 | 10.841 | 18.2781 | 28.6473 | 45.942 | 61.8513 | 79.3755 | 98.5202 | 119.4226 | 140.1524 | 163.4016 | 185.3644 | 210.2283 | 238.6872 | 264.9083 | 288.4855 | 312.7721 | 338.0314 | 363.9542 | 390.2383 | 417.8369 | 444.0527 | 471.3749 | 498.336 | 524.9718 | 539.9806 | 554.654
VIC | 25.7265 | 46.552 | 101.6785 | 208.3623 | 340.1751 | 509.4887 | 715.6307 | 1056.8391 | 1341.3233 | 1625.4052 | 1918.2533 | 2221.9259 | 2526.0663 | 2860.1348 | 3161.2433 | 3487.0053 | 3840.2576 | 4149.8088 | 4455.5921 | 4764.385 | 5080.6296 | 5404.1205 | 5742.5724 | 6094.7117 | 6426.4028 | 6773.8283 | 7116.0724 | 7457.9941 | 7689.1518 | 7916.7089
Aggregation trajectories (MW)
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
Progressive Change | 67.9589 | 88.7737 | 107.6107 | 128.8037 | 151.5831 | 177.0245 | 206.3552 | 241.425 | 268.7997 | 298.9037 | 331.1889 | 366.8377 | 405.4555 | 447.1655 | 490.4318 | 537.051 | 585.3651 | 633.5201 | 680.9026 | 728.9491 | 777.5872 | 827.014 | 882.9453 | 942.3802 | 1005.3322 | 1072.0755 | 1137.921 | 1202.7376 | 1240.7778 | 1275.0502
Step Change | 137.931 | 220.735 | 462.6404 | 860.8221 | 1334.3309 | 1934.6833 | 2620.6848 | 3740.8769 | 4669.2321 | 5601.7161 | 6607.4825 | 7689.9257 | 8883.4162 | 10177.0824 | 11316.043 | 12545.2735 | 13863.1958 | 15000.9533 | 16137.0678 | 17259.7775 | 18414.1682 | 19577.6449 | 20814.2864 | 22090.7679 | 23249.0856 | 24419.5315 | 25589.9279 | 26741.1637 | 27522.16 | 28290.3672
Green Energy Exports | 133.4168 | 206.9677 | 374.285 | 772.6546 | 1274.0777 | 1948.7479 | 2764.4073 | 4113.4232 | 5257.9436 | 6443.6677 | 7680.4072 | 8957.622 | 10159.1889 | 11482.4572 | 12635.0158 | 13902.8818 | 15284.6567 | 16451.0042 | 17583.748 | 18711.6314 | 19852.3042 | 20991.9908 | 22140.501 | 23347.0431 | 24465.4671 | 25623.595 | 26747.4117 | 27850.1958 | 28549.7474 | 29232.9926
Aggregated embedded energy storages (small-scale batteries, degraded MWh)
Amount of energy generated by aggregated battery installations by NEM region.
Progressive Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
NSW | 19.5046 | 28.5116 | 37.7506 | 47.9324 | 59.8474 | 72.3138 | 87.2886 | 104.4038 | 116.9348 | 130.7228 | 145.4737 | 161.7786 | 179.4265 | 198.4614 | 218.1051 | 239.2754 | 261.1302 | 282.7283 | 303.7981 | 324.786 | 345.3464 | 365.6715 | 389.3387 | 414.559 | 441.2958 | 469.6729 | 496.9372 | 522.9958 | 536.0578 | 546.7236
QLD | 9.5944 | 12.5516 | 17.2105 | 22.5515 | 28.604 | 35.6253 | 43.8038 | 54.129 | 62.2956 | 71.4928 | 81.546 | 92.8927 | 105.4189 | 119.1862 | 133.5799 | 149.297 | 165.6515 | 181.8269 | 197.4841 | 213.2949 | 229.2969 | 245.523 | 264.4489 | 284.7569 | 306.4348 | 329.5859 | 352.0871 | 373.8474 | 384.8552 | 394.0202
SA | 100.1452 | 120.8679 | 134.1526 | 147.8536 | 160.8758 | 175.2745 | 190.0885 | 208.617 | 223.0136 | 238.2883 | 253.9048 | 270.6083 | 287.9711 | 305.9573 | 323.5228 | 341.7436 | 359.5642 | 375.9837 | 390.8142 | 404.9928 | 418.6394 | 431.8444 | 447.2636 | 463.2945 | 479.8613 | 497.0101 | 512.7036 | 526.9968 | 533.628 | 538.428
TAS | 0.77055 | 1.212 | 1.7878 | 2.444 | 3.1747 | 4.0082 | 4.9639 | 6.1738 | 6.9648 | 7.838 | 8.7755 | 9.8219 | 10.9603 | 12.1928 | 13.4548 | 14.8169 | 16.2062 | 17.5426 | 18.8017 | 20.0376 | 21.2555 | 22.4604 | 23.8772 | 25.3773 | 26.9602 | 28.6347 | 30.2014 | 31.6536 | 32.4198 | 33.0016
VIC | 13.1727 | 22.2938 | 31.498 | 42.7192 | 54.5578 | 68.109 | 84.6157 | 104.035 | 118.065 | 133.6745 | 150.572 | 169.4356 | 190.0429 | 212.4732 | 235.782 | 261.0698 | 287.276 | 313.1761 | 338.3704 | 363.7753 | 389.4047 | 415.3525 | 445.1947 | 476.9903 | 510.7636 | 546.6991 | 581.6073 | 615.3856 | 632.9996 | 647.9158
Step Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
NSW | 78.8285 | 136.3157 | 341.732 | 674.0401 | 1083.3183 | 1590.0926 | 2154.1533 | 3067.2707 | 3767.8759 | 4443.3011 | 5159.5606 | 5911.2632 | 6823.9511 | 7820.208 | 8656.0867 | 9551.0597 | 10483.8028 | 11299.7652 | 12043.111 | 12732.45 | 13444.5382 | 14149.1708 | 15014.8093 | 15948.1362 | 16685.5865 | 17448.6197 | 18180.2728 | 18904.9596 | 19327.385 | 19701.2593
QLD | 47.7727 | 81.8953 | 189.8288 | 419.7206 | 660.9846 | 978.6575 | 1354.5319 | 2027.4461 | 2567.915 | 3080.5516 | 3608.0949 | 4156.7249 | 4743.4948 | 5459.2904 | 5986.8926 | 6567.2427 | 7198.7733 | 7811.6105 | 8397.5378 | 8944.8163 | 9487.0095 | 10022.7229 | 10607.1657 | 11304.3351 | 11821.0842 | 12365.8352 | 12933.1364 | 13537.51 | 13910.1809 | 14242.5915
SA | 111.9918 | 139.4263 | 208.2517 | 302.6715 | 406.727 | 535.8367 | 678.5795 | 927.8282 | 1132.5328 | 1324.0696 | 1523.5186 | 1729.8603 | 1974.0742 | 2219.5765 | 2421.802 | 2652.5078 | 2908.9712 | 3153.8152 | 3369.7058 | 3560.2554 | 3752.4239 | 3937.818 | 4161.191 | 4383.932 | 4551.6614 | 4732.1538 | 4920.0569 | 5123.4713 | 5233.9472 | 5324.7791
TAS | 1.9709 | 3.3918 | 6.4878 | 13.8105 | 24.6323 | 39.7438 | 59.1394 | 90.8801 | 119.1512 | 149.9256 | 184.0208 | 221.6657 | 264.5118 | 313.1007 | 358.3361 | 409.4549 | 467.3269 | 523.5494 | 573.8381 | 623.9687 | 675.6542 | 728.307 | 786.5055 | 848.6283 | 901.1476 | 956.8348 | 1014.3846 | 1073.0377 | 1105.0596 | 1135.0965
VIC | 56.9021 | 110.1292 | 267.181 | 507.9029 | 791.5721 | 1134.202 | 1481.796 | 2046.5201 | 2491.8745 | 2929.9139 | 3393.8263 | 3898.588 | 4522.1547 | 5232.8213 | 5848.6113 | 6509.8058 | 7158.1285 | 7756.5218 | 8338.1488 | 8900.4157 | 9473.5008 | 10068.0394 | 10791.1884 | 11594.3256 | 12255.1686 | 12936.277 | 13582.5757 | 14247.9546 | 14676.6638 | 15073.4949
Green Energy Exports
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
NSW | 74.597 | 125.5409 | 246.8567 | 564.0317 | 970.8808 | 1518.2039 | 2153.6301 | 3228.1114 | 4087.4569 | 4968.0919 | 5866.1085 | 6755.5139 | 7562.5805 | 8535.1287 | 9328.4812 | 10214.1668 | 11159.1326 | 12014.0638 | 12783.1772 | 13521.3755 | 14250.3269 | 14934.5377 | 15582.1474 | 16395.6776 | 17050.4878 | 17780.8142 | 18481.0638 | 19215.4809 | 19601.1969 | 19956.2327
QLD | 44.3851 | 74.4903 | 120.8828 | 358.0133 | 655.9063 | 1063.0887 | 1547.8498 | 2357.9129 | 3023.9099 | 3694.0582 | 4377.8958 | 5063.8072 | 5597.706 | 6337.5999 | 6918.6308 | 7593.1005 | 8323.8992 | 8972.6302 | 9553.7007 | 10114.1938 | 10669.9225 | 11208.3747 | 11647.9564 | 12298.5719 | 12800.2937 | 13366.8449 | 13927.78 | 14498.196 | 14809.6121 | 15096.46
SA | 110.8324 | 137.0371 | 208.8256 | 310.7285 | 423.4945 | 574.3278 | 748.7059 | 1044.5619 | 1292.3249 | 1534.2924 | 1765.9813 | 1989.7795 | 2225.8148 | 2451.9626 | 2632.0999 | 2855.3616 | 3113.6224 | 3354.7355 | 3564.5901 | 3757.7848 | 3941.1838 | 4110.604 | 4303.8063 | 4494.6077 | 4649.0831 | 4832.4477 | 5021.9843 | 5227.4748 | 5336.2238 | 5429.6713
TAS | 1.8966 | 3.2658 | 5.8205 | 12.8641 | 23.6104 | 39.9235 | 62.4011 | 100.4298 | 134.3426 | 170.6322 | 209.1942 | 250.1399 | 288.6713 | 334.6629 | 375.9151 | 423.9975 | 479.913 | 534.3031 | 581.2027 | 628.1582 | 676.2216 | 724.4992 | 769.9646 | 823.0574 | 868.3062 | 918.6227 | 970.4955 | 1023.8688 | 1051.9235 | 1078.0809
VIC | 55.5843 | 99.3231 | 220.6433 | 461.1516 | 752.1133 | 1120.3746 | 1558.3657 | 2298.4401 | 2890.3065 | 3458.9811 | 4026.1449 | 4595.506 | 5172.5077 | 5850.8566 | 6426.8348 | 7053.2081 | 7727.6135 | 8362.8416 | 8951.652 | 9518.744 | 10086.2596 | 10651.8934 | 11263.3995 | 11969.3316 | 12566.4448 | 13210.341 | 13846.8908 | 14518.7632 | 14926.4762 | 15299.6851
Aggregation trajectories (MWh)
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
Progressive Change | 143.1873 | 185.4369 | 222.3995 | 263.5007 | 307.0597 | 355.3308 | 410.7604 | 477.3586 | 527.2737 | 582.0165 | 640.2721 | 704.5371 | 773.8197 | 848.2709 | 924.4446 | 1006.2026 | 1089.8282 | 1171.2576 | 1249.2685 | 1326.8866 | 1403.9427 | 1480.8519 | 1570.1232 | 1664.9779 | 1765.3157 | 1871.6028 | 1973.5367 | 2070.8792 | 2119.9604 | 2160.0892
Step Change | 297.466 | 471.1583 | 1013.4813 | 1918.1457 | 2967.2342 | 4278.5326 | 5728.2001 | 8159.9452 | 10079.3493 | 11927.7618 | 13869.0212 | 15918.1021 | 18328.1867 | 21044.9969 | 23271.7286 | 25690.071 | 28217.0028 | 30545.262 | 32722.3415 | 34761.9061 | 36833.1265 | 38906.0581 | 41360.8599 | 44079.3572 | 46214.6483 | 48439.7204 | 50630.4264 | 52886.9333 | 54253.2365 | 55477.2213
Green Energy Exports | 287.2954 | 439.6571 | 803.0289 | 1706.7891 | 2826.0052 | 4315.9185 | 6070.9527 | 9029.4561 | 11428.3407 | 13826.0558 | 16245.3246 | 18654.7465 | 20847.2802 | 23510.2107 | 25681.9617 | 28139.8344 | 30804.1808 | 33238.5742 | 35434.3228 | 37540.2563 | 39623.9143 | 41629.909 | 43567.2742 | 45981.2462 | 47934.6155 | 50109.0706 | 52248.2144 | 54483.7837 | 55725.4326 | 56860.13

## Sub-regional demand allocation
Go to Assumptions Summary
Regional --> Sub-regional demand allocations
This data represents the assumptions applied from consultant forecasts to the regional forecast outcomes, to convert and apply within the sub-regional Capacity Outlook model.
The sub-regional representation is described further in the Network Representation tab. |  |  | Go to Network Representation
Sub-regional assumptions has been applied to the following categories. Other allocations follow the methods described in the ISP Methodology.
Rooftop PV
PVNSG
Battery forecasts (embedded and aggregated energy storages, equally)
EVs (battery and plug-in EVs, and Fuel cell EVs)
Rooftop PV (Capacity, % of regional allocation)
Capacity of behind-the-meter rooftop PV
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 15.99% | 15.8% | 15.5% | 15.18% | 14.88% | 14.62% | 14.38% | 14.25% | 14.11% | 13.99% | 13.88% | 13.79% | 13.71% | 13.67% | 13.64% | 13.63% | 13.61% | 13.6% | 13.58% | 13.57% | 13.56% | 13.55% | 13.55% | 13.54% | 13.53% | 13.53% | 13.52% | 13.52% | 13.5% | 13.48% | 13.45%
Central NSW (CNSW) | 9.454% | 9.362% | 9.23% | 9.122% | 9.023% | 8.934% | 8.851% | 8.816% | 8.78% | 8.735% | 8.691% | 8.646% | 8.607% | 8.585% | 8.57% | 8.563% | 8.559% | 8.554% | 8.552% | 8.549% | 8.547% | 8.547% | 8.547% | 8.547% | 8.548% | 8.548% | 8.547% | 8.546% | 8.542% | 8.529% | 8.516%
South NSW (SNSW) | 15% | 15% | 14.97% | 14.94% | 14.9% | 14.86% | 14.82% | 14.84% | 14.85% | 14.84% | 14.83% | 14.83% | 14.82% | 14.83% | 14.84% | 14.86% | 14.88% | 14.91% | 14.94% | 14.97% | 15% | 15.03% | 15.06% | 15.09% | 15.12% | 15.15% | 15.2% | 15.24% | 15.28% | 15.31% | 15.34%
Sydney, Newcastle and Wooloongong (SNW) | 59.56% | 59.83% | 60.29% | 60.76% | 61.2% | 61.58% | 61.95% | 62.1% | 62.26% | 62.44% | 62.6% | 62.74% | 62.86% | 62.91% | 62.94% | 62.95% | 62.95% | 62.94% | 62.93% | 62.91% | 62.89% | 62.87% | 62.85% | 62.82% | 62.8% | 62.77% | 62.74% | 62.7% | 62.67% | 62.68% | 62.69%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 10.87% | 10.83% | 10.85% | 10.87% | 10.9% | 10.93% | 10.96% | 10.99% | 11.01% | 11.02% | 11.03% | 11.03% | 11.02% | 11.01% | 11% | 10.99% | 10.99% | 10.98% | 10.97% | 10.97% | 10.96% | 10.96% | 10.96% | 10.95% | 10.95% | 10.94% | 10.94% | 10.95% | 10.95% | 10.95% | 10.95%
Central QLD (CQ) | 11.91% | 11.84% | 11.82% | 11.83% | 11.85% | 11.86% | 11.89% | 11.91% | 11.92% | 11.91% | 11.91% | 11.9% | 11.88% | 11.86% | 11.84% | 11.82% | 11.8% | 11.78% | 11.77% | 11.75% | 11.73% | 11.72% | 11.71% | 11.69% | 11.68% | 11.67% | 11.66% | 11.65% | 11.64% | 11.64% | 11.63%
Gladstone Grid (GG) | 1.088% | 1.08% | 1.081% | 1.085% | 1.09% | 1.095% | 1.1% | 1.105% | 1.109% | 1.109% | 1.109% | 1.108% | 1.105% | 1.101% | 1.097% | 1.094% | 1.091% | 1.088% | 1.085% | 1.082% | 1.079% | 1.077% | 1.074% | 1.072% | 1.07% | 1.068% | 1.066% | 1.066% | 1.066% | 1.065% | 1.064%
Southern QLD (SQ) | 76.13% | 76.25% | 76.25% | 76.21% | 76.16% | 76.11% | 76.05% | 76% | 75.97% | 75.96% | 75.96% | 75.97% | 75.99% | 76.03% | 76.06% | 76.09% | 76.12% | 76.15% | 76.18% | 76.2% | 76.22% | 76.25% | 76.26% | 76.28% | 76.3% | 76.32% | 76.33% | 76.34% | 76.34% | 76.35% | 76.35%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 96.51% | 96.49% | 96.46% | 96.4% | 96.34% | 96.29% | 96.24% | 96.2% | 96.17% | 96.14% | 96.12% | 96.1% | 96.1% | 96.09% | 96.09% | 96.09% | 96.09% | 96.08% | 96.08% | 96.08% | 96.07% | 96.07% | 96.07% | 96.07% | 96.06% | 96.06% | 96.06% | 96.06% | 96.05% | 96.04% | 96.03%
South East South Australia (SESA) | 3.485% | 3.505% | 3.54% | 3.602% | 3.661% | 3.712% | 3.762% | 3.796% | 3.828% | 3.858% | 3.885% | 3.898% | 3.902% | 3.905% | 3.909% | 3.911% | 3.915% | 3.918% | 3.921% | 3.923% | 3.926% | 3.928% | 3.931% | 3.932% | 3.935% | 3.936% | 3.938% | 3.945% | 3.951% | 3.958% | 3.966%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 15.92% | 15.44% | 14.95% | 14.57% | 14.25% | 13.98% | 13.76% | 13.66% | 13.57% | 13.49% | 13.41% | 13.34% | 13.28% | 13.21% | 13.15% | 13.09% | 13.04% | 12.99% | 12.95% | 12.92% | 12.9% | 12.88% | 12.86% | 12.84% | 12.82% | 12.8% | 12.79% | 12.77% | 12.76% | 12.74% | 12.73%
Central NSW (CNSW) | 9.413% | 9.192% | 9.001% | 8.845% | 8.711% | 8.602% | 8.508% | 8.477% | 8.455% | 8.437% | 8.422% | 8.41% | 8.401% | 8.392% | 8.382% | 8.366% | 8.353% | 8.334% | 8.319% | 8.308% | 8.304% | 8.308% | 8.314% | 8.323% | 8.331% | 8.339% | 8.345% | 8.35% | 8.354% | 8.357% | 8.36%
South NSW (SNSW) | 15.03% | 15% | 14.91% | 14.84% | 14.78% | 14.74% | 14.71% | 14.74% | 14.78% | 14.82% | 14.86% | 14.89% | 14.93% | 14.95% | 14.97% | 14.99% | 15.01% | 15.03% | 15.06% | 15.09% | 15.13% | 15.17% | 15.22% | 15.26% | 15.3% | 15.35% | 15.39% | 15.43% | 15.46% | 15.5% | 15.53%
Sydney, Newcastle and Wooloongong (SNW) | 59.64% | 60.36% | 61.14% | 61.75% | 62.26% | 62.67% | 63.02% | 63.13% | 63.2% | 63.26% | 63.31% | 63.35% | 63.4% | 63.45% | 63.5% | 63.55% | 63.59% | 63.64% | 63.67% | 63.68% | 63.67% | 63.64% | 63.61% | 63.58% | 63.54% | 63.51% | 63.48% | 63.45% | 63.43% | 63.4% | 63.38%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 10.86% | 10.88% | 10.9% | 10.93% | 10.94% | 10.95% | 10.94% | 10.96% | 10.97% | 10.99% | 11.02% | 11.04% | 11.07% | 11.09% | 11.11% | 11.13% | 11.15% | 11.17% | 11.18% | 11.19% | 11.2% | 11.22% | 11.25% | 11.27% | 11.3% | 11.32% | 11.34% | 11.36% | 11.38% | 11.39% | 11.41%
Central QLD (CQ) | 11.88% | 11.83% | 11.78% | 11.75% | 11.71% | 11.67% | 11.62% | 11.6% | 11.59% | 11.58% | 11.58% | 11.58% | 11.58% | 11.58% | 11.59% | 11.6% | 11.6% | 11.6% | 11.61% | 11.61% | 11.62% | 11.63% | 11.64% | 11.66% | 11.67% | 11.69% | 11.71% | 11.72% | 11.73% | 11.74% | 11.75%
Gladstone Grid (GG) | 1.086% | 1.087% | 1.087% | 1.089% | 1.087% | 1.086% | 1.083% | 1.084% | 1.085% | 1.086% | 1.087% | 1.088% | 1.089% | 1.09% | 1.092% | 1.092% | 1.092% | 1.09% | 1.09% | 1.089% | 1.088% | 1.088% | 1.088% | 1.09% | 1.091% | 1.092% | 1.092% | 1.093% | 1.093% | 1.094% | 1.094%
Southern QLD (SQ) | 76.17% | 76.21% | 76.23% | 76.23% | 76.27% | 76.3% | 76.35% | 76.36% | 76.36% | 76.34% | 76.32% | 76.29% | 76.26% | 76.23% | 76.2% | 76.17% | 76.15% | 76.14% | 76.13% | 76.11% | 76.09% | 76.06% | 76.02% | 75.98% | 75.94% | 75.89% | 75.86% | 75.82% | 75.8% | 75.77% | 75.74%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 96.5% | 96.46% | 96.36% | 96.28% | 96.21% | 96.15% | 96.09% | 96.05% | 96.02% | 95.98% | 95.95% | 95.92% | 95.89% | 95.87% | 95.85% | 95.82% | 95.81% | 95.81% | 95.81% | 95.81% | 95.81% | 95.8% | 95.79% | 95.78% | 95.77% | 95.77% | 95.76% | 95.75% | 95.75% | 95.75% | 95.74%
South East South Australia (SESA) | 3.498% | 3.541% | 3.637% | 3.718% | 3.789% | 3.85% | 3.905% | 3.945% | 3.982% | 4.016% | 4.048% | 4.078% | 4.106% | 4.131% | 4.153% | 4.177% | 4.189% | 4.191% | 4.195% | 4.195% | 4.193% | 4.199% | 4.208% | 4.219% | 4.226% | 4.234% | 4.241% | 4.246% | 4.25% | 4.254% | 4.257%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 15.9% | 15.11% | 14.52% | 14% | 13.53% | 13.14% | 12.83% | 12.73% | 12.63% | 12.54% | 12.47% | 12.43% | 12.41% | 12.41% | 12.42% | 12.43% | 12.44% | 12.46% | 12.48% | 12.5% | 12.52% | 12.55% | 12.57% | 12.6% | 12.64% | 12.67% | 12.7% | 12.73% | 12.75% | 12.76% | 12.78%
Central NSW (CNSW) | 9.395% | 9.137% | 8.933% | 8.742% | 8.549% | 8.377% | 8.221% | 8.185% | 8.145% | 8.099% | 8.061% | 8.039% | 8.032% | 8.038% | 8.049% | 8.063% | 8.081% | 8.1% | 8.122% | 8.145% | 8.17% | 8.195% | 8.223% | 8.252% | 8.282% | 8.314% | 8.343% | 8.371% | 8.398% | 8.421% | 8.443%
South NSW (SNSW) | 14.99% | 14.91% | 14.83% | 14.76% | 14.67% | 14.57% | 14.46% | 14.49% | 14.51% | 14.52% | 14.54% | 14.56% | 14.6% | 14.65% | 14.7% | 14.75% | 14.81% | 14.88% | 14.94% | 15.01% | 15.08% | 15.15% | 15.22% | 15.3% | 15.37% | 15.45% | 15.54% | 15.63% | 15.72% | 15.79% | 15.86%
Sydney, Newcastle and Wooloongong (SNW) | 59.71% | 60.85% | 61.72% | 62.5% | 63.26% | 63.92% | 64.48% | 64.59% | 64.71% | 64.84% | 64.93% | 64.97% | 64.96% | 64.9% | 64.83% | 64.75% | 64.66% | 64.57% | 64.46% | 64.35% | 64.23% | 64.11% | 63.98% | 63.85% | 63.71% | 63.57% | 63.42% | 63.27% | 63.14% | 63.03% | 62.92%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 10.87% | 10.98% | 11.05% | 11.1% | 11.14% | 11.16% | 11.16% | 11.17% | 11.17% | 11.16% | 11.15% | 11.14% | 11.13% | 11.13% | 11.13% | 11.13% | 11.13% | 11.14% | 11.14% | 11.15% | 11.16% | 11.17% | 11.18% | 11.19% | 11.19% | 11.2% | 11.22% | 11.23% | 11.24% | 11.26% | 11.27%
Central QLD (CQ) | 11.9% | 11.9% | 11.87% | 11.84% | 11.79% | 11.75% | 11.71% | 11.67% | 11.64% | 11.61% | 11.58% | 11.56% | 11.55% | 11.54% | 11.54% | 11.54% | 11.55% | 11.55% | 11.56% | 11.56% | 11.57% | 11.57% | 11.57% | 11.58% | 11.58% | 11.59% | 11.6% | 11.6% | 11.61% | 11.62% | 11.62%
Gladstone Grid (GG) | 1.091% | 1.104% | 1.11% | 1.114% | 1.114% | 1.111% | 1.107% | 1.104% | 1.102% | 1.099% | 1.095% | 1.092% | 1.09% | 1.089% | 1.088% | 1.086% | 1.085% | 1.084% | 1.082% | 1.081% | 1.081% | 1.08% | 1.079% | 1.078% | 1.079% | 1.081% | 1.082% | 1.082% | 1.082% | 1.083% | 1.083%
Southern QLD (SQ) | 76.13% | 76.02% | 75.97% | 75.94% | 75.96% | 75.98% | 76.02% | 76.06% | 76.09% | 76.14% | 76.18% | 76.21% | 76.23% | 76.24% | 76.24% | 76.24% | 76.23% | 76.23% | 76.22% | 76.2% | 76.19% | 76.18% | 76.17% | 76.16% | 76.15% | 76.13% | 76.11% | 76.09% | 76.06% | 76.04% | 76.02%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 96.5% | 96.37% | 96.23% | 96.1% | 95.98% | 95.89% | 95.83% | 95.79% | 95.76% | 95.75% | 95.74% | 95.74% | 95.74% | 95.74% | 95.74% | 95.75% | 95.75% | 95.75% | 95.75% | 95.75% | 95.76% | 95.76% | 95.76% | 95.76% | 95.76% | 95.77% | 95.77% | 95.77% | 95.78% | 95.78% | 95.78%
South East South Australia (SESA) | 3.5% | 3.633% | 3.774% | 3.904% | 4.019% | 4.108% | 4.17% | 4.207% | 4.236% | 4.249% | 4.255% | 4.26% | 4.26% | 4.259% | 4.258% | 4.254% | 4.254% | 4.251% | 4.249% | 4.246% | 4.244% | 4.243% | 4.241% | 4.238% | 4.236% | 4.233% | 4.231% | 4.229% | 4.225% | 4.22% | 4.215%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
PVNSG (Capacity, % of regional allocation)
Capacity of small-scale non-scheduled generating systems
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 14.37% | 15.05% | 16% | 16% | 15.77% | 18.01% | 19.7% | 19.64% | 19.2% | 18.53% | 17.88% | 17.19% | 16.66% | 15.94% | 15.49% | 14.91% | 14.39% | 14.01% | 13.62% | 13.33% | 13.29% | 13.04% | 12.51% | 12.17% | 11.95% | 11.73% | 11.38% | 11.31% | 11.32% | 11.32% | 11.32%
Central NSW (CNSW) | 17.72% | 17.48% | 16.55% | 16.08% | 15.78% | 14.8% | 15.07% | 14.7% | 14.74% | 14.73% | 15.22% | 15.1% | 14.81% | 14.56% | 14.94% | 14.67% | 14.5% | 14.39% | 14.75% | 14.62% | 14.31% | 14.05% | 14.45% | 14.19% | 14.03% | 14.06% | 14.44% | 14.33% | 14.21% | 14.05% | 13.88%
South NSW (SNSW) | 27.83% | 27.15% | 26.94% | 27.01% | 27.29% | 26.96% | 27.34% | 27.16% | 27.12% | 27.44% | 28.12% | 27.97% | 28.25% | 28.68% | 29.34% | 29.47% | 29.55% | 29.58% | 29.97% | 29.8% | 29.72% | 29.79% | 30.34% | 30.41% | 30.56% | 30.47% | 30.81% | 30.7% | 30.63% | 30.57% | 30.52%
Sydney, Newcastle and Wooloongong (SNW) | 40.09% | 40.31% | 40.51% | 40.91% | 41.16% | 40.23% | 37.89% | 38.51% | 38.94% | 39.3% | 38.78% | 39.74% | 40.29% | 40.82% | 40.23% | 40.95% | 41.57% | 42.02% | 41.66% | 42.25% | 42.67% | 43.12% | 42.7% | 43.23% | 43.46% | 43.74% | 43.37% | 43.66% | 43.85% | 44.06% | 44.28%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 15.14% | 16.64% | 18.56% | 18.34% | 17.7% | 20.74% | 21.27% | 20.55% | 20.19% | 19.48% | 18.8% | 17.97% | 17.59% | 16.82% | 16.2% | 15.52% | 14.93% | 14.63% | 14.32% | 13.76% | 13.72% | 13.32% | 13.05% | 12.65% | 12.64% | 12.32% | 12.2% | 11.93% | 11.93% | 11.78% | 11.62%
Central QLD (CQ) | 20.49% | 20.25% | 20.09% | 19.77% | 19.95% | 19.69% | 21.26% | 21.81% | 21.54% | 21.97% | 22.25% | 22.52% | 22.29% | 22.89% | 23.01% | 23.17% | 23.14% | 23.34% | 23.61% | 23.8% | 23.68% | 24% | 24.04% | 24.19% | 24.09% | 24.38% | 24.39% | 24.53% | 24.37% | 24.56% | 24.75%
Gladstone Grid (GG) | 0.5107% | 0.5638% | 0.5333% | 0.5299% | 0.5957% | 0.544% | 0.5476% | 0.5369% | 0.5315% | 0.5641% | 0.5813% | 0.5969% | 0.6112% | 0.6496% | 0.6712% | 0.6644% | 0.6912% | 0.703% | 0.7317% | 0.7623% | 0.7702% | 0.7729% | 0.7895% | 0.8102% | 0.8141% | 0.8147% | 0.8107% | 0.8306% | 0.8391% | 0.8298% | 0.8205%
Southern QLD (SQ) | 63.86% | 62.55% | 60.82% | 61.36% | 61.76% | 59.02% | 56.92% | 57.1% | 57.74% | 57.99% | 58.37% | 58.91% | 59.51% | 59.64% | 60.12% | 60.65% | 61.24% | 61.32% | 61.34% | 61.68% | 61.83% | 61.9% | 62.12% | 62.34% | 62.46% | 62.49% | 62.6% | 62.71% | 62.86% | 62.83% | 62.8%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 97.45% | 97.14% | 97.16% | 97.17% | 97.2% | 97.26% | 97.16% | 97.04% | 97.07% | 97.11% | 97.03% | 96.66% | 96.52% | 96.17% | 96.12% | 96.15% | 96.12% | 96.07% | 96.07% | 96.15% | 95.99% | 95.7% | 95.57% | 95.59% | 95.6% | 95.64% | 95.68% | 95.71% | 95.53% | 95.42% | 95.31%
South East South Australia (SESA) | 2.549% | 2.857% | 2.843% | 2.827% | 2.8% | 2.744% | 2.842% | 2.961% | 2.931% | 2.891% | 2.974% | 3.335% | 3.48% | 3.833% | 3.878% | 3.854% | 3.88% | 3.93% | 3.931% | 3.851% | 4.01% | 4.304% | 4.431% | 4.408% | 4.4% | 4.36% | 4.316% | 4.291% | 4.466% | 4.576% | 4.687%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 14.06% | 14.22% | 14.03% | 14% | 13.28% | 14.16% | 14.21% | 14.44% | 14.37% | 13.84% | 13.15% | 12.75% | 12.6% | 11.92% | 11.14% | 10.55% | 10.15% | 9.978% | 10.48% | 10.78% | 11.35% | 11.93% | 11.89% | 11.5% | 11.18% | 11% | 10.65% | 10.39% | 10.15% | 10.28% | 10.4%
Central NSW (CNSW) | 17.03% | 16.6% | 15.24% | 14.29% | 13.87% | 13.38% | 13.89% | 13.33% | 12.95% | 12.63% | 13.34% | 13.07% | 12.85% | 12.46% | 12.74% | 12.54% | 13.82% | 14.31% | 14.67% | 14.5% | 14.26% | 13.96% | 14.23% | 13.88% | 13.72% | 13.51% | 13.81% | 14.23% | 14.6% | 14.61% | 14.61%
South NSW (SNSW) | 28.08% | 27.58% | 27.8% | 28.05% | 28.37% | 28.24% | 28.77% | 28.45% | 28.62% | 29.9% | 30.44% | 30.61% | 30.56% | 31.8% | 33.44% | 34.2% | 33.59% | 33.15% | 33.18% | 32.87% | 32.57% | 32.27% | 32.65% | 33.21% | 33.68% | 34.06% | 34.48% | 34.16% | 34.01% | 33.76% | 33.51%
Sydney, Newcastle and Wooloongong (SNW) | 40.84% | 41.6% | 42.93% | 43.66% | 44.49% | 44.22% | 43.13% | 43.78% | 44.05% | 43.63% | 43.07% | 43.56% | 43.99% | 43.82% | 42.67% | 42.71% | 42.45% | 42.55% | 41.66% | 41.85% | 41.82% | 41.84% | 41.23% | 41.41% | 41.42% | 41.44% | 41.05% | 41.22% | 41.24% | 41.36% | 41.48%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 14.29% | 14.72% | 15.35% | 15.87% | 15.22% | 16.06% | 15% | 14.38% | 13.57% | 12.6% | 12.39% | 11.95% | 11.69% | 11.13% | 10.84% | 10.23% | 10.72% | 11.58% | 11.49% | 11.17% | 10.84% | 10.46% | 10.35% | 10.04% | 10.31% | 10.89% | 11% | 10.77% | 10.54% | 10.28% | 10.02%
Central QLD (CQ) | 21.21% | 20.82% | 20.57% | 20.81% | 21.02% | 21.16% | 22.33% | 23.41% | 24.15% | 25.66% | 25.57% | 25.56% | 25.26% | 24.92% | 24.64% | 24.35% | 23.85% | 23.82% | 24.82% | 25.56% | 25.21% | 25.08% | 24.93% | 24.85% | 24.56% | 24.52% | 24.84% | 25.38% | 25.48% | 25.39% | 25.3%
Gladstone Grid (GG) | 0.5449% | 0.5973% | 0.6305% | 0.6896% | 0.7141% | 0.7325% | 0.7208% | 0.7174% | 0.7653% | 1.166% | 1.15% | 1.125% | 1.104% | 1.08% | 1.04% | 1.004% | 0.978% | 0.9582% | 0.9287% | 1.119% | 1.097% | 1.074% | 1.047% | 1.042% | 1.035% | 1.018% | 0.9969% | 1.117% | 1.107% | 1.09% | 1.073%
Southern QLD (SQ) | 63.96% | 63.87% | 63.45% | 62.63% | 63.04% | 62.06% | 61.95% | 61.49% | 61.51% | 60.57% | 60.89% | 61.36% | 61.95% | 62.86% | 63.48% | 64.41% | 64.45% | 63.64% | 62.77% | 62.15% | 62.85% | 63.38% | 63.67% | 64.07% | 64.1% | 63.57% | 63.16% | 62.73% | 62.87% | 63.23% | 63.6%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 97.19% | 97.07% | 96.77% | 96.3% | 95.94% | 96.05% | 96.07% | 96.1% | 96.05% | 95.72% | 95.64% | 95.73% | 95.7% | 95.76% | 95.49% | 95.52% | 95.62% | 95.64% | 94.86% | 94.6% | 94.68% | 94.78% | 94.74% | 94.73% | 94.77% | 94.83% | 94.86% | 94.8% | 94.84% | 94.91% | 94.98%
South East South Australia (SESA) | 2.812% | 2.934% | 3.226% | 3.702% | 4.062% | 3.955% | 3.926% | 3.901% | 3.953% | 4.281% | 4.357% | 4.275% | 4.303% | 4.24% | 4.511% | 4.481% | 4.379% | 4.362% | 5.137% | 5.404% | 5.317% | 5.22% | 5.26% | 5.275% | 5.228% | 5.171% | 5.142% | 5.205% | 5.156% | 5.089% | 5.021%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 10.81% | 11.25% | 10.59% | 10.17% | 11.03% | 15.2% | 15.47% | 16.85% | 16.36% | 15.52% | 14.58% | 16.29% | 17.45% | 17.03% | 15.76% | 16.7% | 16.68% | 17.63% | 17.3% | 18.01% | 17.45% | 17.05% | 17.87% | 17.9% | 17.44% | 17.68% | 18.31% | 17.82% | 17.41% | 18.09% | 18.78%
Central NSW (CNSW) | 19.74% | 17.38% | 14.67% | 11.54% | 10.04% | 8.622% | 9.409% | 9.2% | 9.232% | 10.79% | 10.64% | 9.26% | 8.912% | 9.691% | 10.14% | 9.597% | 9.316% | 9.148% | 9.844% | 9.737% | 10.36% | 9.812% | 9.867% | 10.22% | 10.14% | 9.711% | 9.822% | 10.37% | 10.01% | 9.65% | 9.293%
South NSW (SNSW) | 28.27% | 28.45% | 31.3% | 36.31% | 37.59% | 35.49% | 35.22% | 33.73% | 33.59% | 32.99% | 35.22% | 35.77% | 34.95% | 34.43% | 36.6% | 36.15% | 35.91% | 35.17% | 36.62% | 35.79% | 35.71% | 36.68% | 36.43% | 35.8% | 36.28% | 36.51% | 36.29% | 35.96% | 36.74% | 36.43% | 36.13%
Sydney, Newcastle and Wooloongong (SNW) | 41.18% | 42.92% | 43.44% | 41.99% | 41.34% | 40.69% | 39.9% | 40.22% | 40.82% | 40.7% | 39.57% | 38.68% | 38.69% | 38.85% | 37.49% | 37.54% | 38.09% | 38.04% | 36.24% | 36.46% | 36.48% | 36.46% | 35.84% | 36.08% | 36.14% | 36.1% | 35.57% | 35.85% | 35.84% | 35.82% | 35.8%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 13.01% | 12.55% | 12.28% | 11.18% | 10.73% | 10.52% | 12.39% | 13.82% | 13.49% | 13.04% | 12.56% | 14.06% | 13.62% | 13.15% | 14.34% | 13.83% | 13.7% | 13.14% | 13.7% | 14.19% | 14.05% | 13.68% | 14.44% | 14.03% | 13.73% | 14.28% | 14.06% | 13.76% | 14.27% | 13.98% | 13.69%
Central QLD (CQ) | 20.44% | 19.96% | 19.73% | 19.19% | 19.39% | 23.69% | 23.24% | 22.58% | 22.29% | 22% | 22.26% | 23.36% | 22.81% | 22.56% | 23.73% | 23.41% | 23.26% | 23.8% | 23.73% | 24.31% | 23.81% | 24.06% | 24.27% | 24.04% | 24.33% | 24.32% | 24.07% | 24.69% | 24.31% | 24.11% | 23.92%
Gladstone Grid (GG) | 0.5243% | 0.5641% | 0.5743% | 0.5241% | 0.5357% | 1.008% | 0.9509% | 0.8857% | 0.8862% | 0.8326% | 0.7911% | 0.9591% | 0.927% | 0.9011% | 1.004% | 0.97% | 0.9731% | 1.082% | 0.9726% | 1.064% | 1.036% | 1.109% | 1.068% | 1.035% | 1.105% | 1.078% | 1.046% | 1.1% | 1.076% | 1.051% | 1.027%
Southern QLD (SQ) | 66.03% | 66.93% | 67.41% | 69.1% | 69.34% | 64.78% | 63.42% | 62.71% | 63.33% | 64.12% | 64.4% | 61.62% | 62.65% | 63.38% | 60.93% | 61.8% | 62.07% | 61.98% | 61.6% | 60.44% | 61.1% | 61.15% | 60.22% | 60.89% | 60.83% | 60.33% | 60.83% | 60.44% | 60.34% | 60.86% | 61.37%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 97.27% | 97.09% | 96.91% | 96.39% | 96.37% | 96.4% | 96.38% | 95.3% | 94.81% | 94.78% | 94.99% | 95.23% | 95.36% | 95.25% | 95.32% | 95.45% | 95.44% | 95.53% | 94.9% | 95% | 95.12% | 95.2% | 95.13% | 95.21% | 95.17% | 94.93% | 94.91% | 94.96% | 95.03% | 95.1% | 95.17%
South East South Australia (SESA) | 2.727% | 2.906% | 3.086% | 3.612% | 3.625% | 3.604% | 3.615% | 4.696% | 5.19% | 5.218% | 5.009% | 4.768% | 4.639% | 4.752% | 4.684% | 4.552% | 4.557% | 4.468% | 5.1% | 4.997% | 4.879% | 4.797% | 4.874% | 4.789% | 4.832% | 5.074% | 5.094% | 5.037% | 4.97% | 4.899% | 4.829%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Aggregated BEV and PHEV (Energy, % of regional allocation)
Amount of energy consumed by these electric vehicles
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 5.373% | 7.43% | 9.217% | 10% | 10.47% | 10.76% | 10.95% | 11.06% | 11.11% | 11.15% | 11.16% | 11.16% | 11.16% | 11.16% | 11.15% | 11.14% | 11.13% | 11.12% | 11.11% | 11.1% | 11.09% | 11.09% | 11.08% | 11.07% | 11.06% | 11.04% | 11.03% | 11.02% | 11.02% | 11.01% | 11%
Central NSW (CNSW) | 3.807% | 4.993% | 6.282% | 6.776% | 7.065% | 7.244% | 7.371% | 7.441% | 7.481% | 7.505% | 7.519% | 7.526% | 7.529% | 7.529% | 7.527% | 7.524% | 7.52% | 7.516% | 7.512% | 7.507% | 7.503% | 7.505% | 7.5% | 7.495% | 7.489% | 7.484% | 7.478% | 7.473% | 7.469% | 7.465% | 7.461%
South NSW (SNSW) | 12.11% | 10.49% | 9.099% | 8.229% | 7.719% | 7.461% | 7.594% | 7.838% | 8.122% | 8.41% | 8.689% | 8.95% | 9.192% | 9.415% | 9.62% | 9.809% | 9.984% | 10.15% | 10.3% | 10.44% | 10.57% | 10.69% | 10.81% | 10.92% | 11.03% | 11.14% | 11.25% | 11.34% | 11.42% | 11.49% | 11.56%
Sydney, Newcastle and Wooloongong (SNW) | 78.71% | 77.09% | 75.4% | 74.99% | 74.75% | 74.54% | 74.08% | 73.66% | 73.28% | 72.94% | 72.63% | 72.36% | 72.12% | 71.9% | 71.71% | 71.53% | 71.37% | 71.22% | 71.08% | 70.96% | 70.84% | 70.71% | 70.61% | 70.52% | 70.42% | 70.33% | 70.24% | 70.16% | 70.1% | 70.04% | 69.98%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 3.349% | 5.889% | 7.863% | 8.644% | 9.084% | 9.357% | 9.539% | 9.662% | 9.748% | 9.81% | 9.856% | 9.891% | 9.917% | 9.937% | 9.953% | 9.966% | 9.977% | 9.985% | 9.993% | 9.999% | 10% | 10.02% | 10.02% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.04%
Central QLD (CQ) | 2.705% | 6.197% | 8.933% | 10.01% | 10.62% | 10.99% | 11.23% | 11.41% | 11.53% | 11.61% | 11.68% | 11.73% | 11.77% | 11.8% | 11.82% | 11.84% | 11.86% | 11.87% | 11.88% | 11.89% | 11.9% | 11.92% | 11.93% | 11.93% | 11.94% | 11.94% | 11.94% | 11.94% | 11.95% | 11.95% | 11.95%
Gladstone Grid (GG) | 0.1482% | 0.5334% | 0.8316% | 0.9506% | 1.017% | 1.059% | 1.083% | 1.101% | 1.113% | 1.122% | 1.128% | 1.133% | 1.136% | 1.139% | 1.141% | 1.143% | 1.144% | 1.145% | 1.145% | 1.146% | 1.147% | 1.149% | 1.149% | 1.149% | 1.149% | 1.149% | 1.15% | 1.15% | 1.15% | 1.15% | 1.15%
Southern QLD (SQ) | 93.8% | 87.38% | 82.37% | 80.39% | 79.28% | 78.59% | 78.14% | 77.83% | 77.61% | 77.45% | 77.33% | 77.25% | 77.18% | 77.13% | 77.08% | 77.05% | 77.02% | 77% | 76.98% | 76.96% | 76.95% | 76.91% | 76.9% | 76.89% | 76.89% | 76.88% | 76.88% | 76.87% | 76.87% | 76.87% | 76.86%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 99.25% | 97.84% | 96.71% | 96.24% | 95.98% | 95.82% | 95.71% | 95.63% | 95.57% | 95.53% | 95.5% | 95.48% | 95.46% | 95.45% | 95.44% | 95.43% | 95.42% | 95.41% | 95.41% | 95.4% | 95.4% | 95.39% | 95.38% | 95.38% | 95.38% | 95.38% | 95.37% | 95.37% | 95.37% | 95.37% | 95.37%
South East South Australia (SESA) | 0.7461% | 2.163% | 3.286% | 3.755% | 4.021% | 4.185% | 4.295% | 4.371% | 4.425% | 4.465% | 4.495% | 4.518% | 4.536% | 4.551% | 4.562% | 4.572% | 4.58% | 4.586% | 4.592% | 4.597% | 4.602% | 4.614% | 4.616% | 4.619% | 4.621% | 4.623% | 4.625% | 4.627% | 4.628% | 4.629% | 4.63%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 5.387% | 7.963% | 9.683% | 10.25% | 10.61% | 10.8% | 10.91% | 10.97% | 11.01% | 11.04% | 11.06% | 11.07% | 11.09% | 11.09% | 11.1% | 11.11% | 11.11% | 11.12% | 11.12% | 11.12% | 11.13% | 11.13% | 11.13% | 11.13% | 11.13% | 11.14% | 11.14% | 11.14% | 11.14% | 11.15% | 11.15%
Central NSW (CNSW) | 3.778% | 5.251% | 6.537% | 6.904% | 7.131% | 7.253% | 7.32% | 7.367% | 7.396% | 7.445% | 7.482% | 7.509% | 7.531% | 7.548% | 7.562% | 7.574% | 7.584% | 7.592% | 7.599% | 7.605% | 7.61% | 7.617% | 7.621% | 7.625% | 7.628% | 7.631% | 7.634% | 7.64% | 7.646% | 7.653% | 7.659%
South NSW (SNSW) | 13.51% | 13.37% | 12.42% | 11.55% | 10.62% | 10.19% | 10.04% | 10.04% | 10.11% | 10.42% | 10.65% | 10.82% | 10.95% | 11.06% | 11.14% | 11.22% | 11.28% | 11.33% | 11.38% | 11.42% | 11.45% | 11.49% | 11.51% | 11.54% | 11.56% | 11.58% | 11.61% | 11.63% | 11.65% | 11.67% | 11.69%
Sydney, Newcastle and Wooloongong (SNW) | 77.32% | 73.41% | 71.36% | 71.29% | 71.64% | 71.76% | 71.73% | 71.62% | 71.49% | 71.1% | 70.82% | 70.6% | 70.43% | 70.3% | 70.19% | 70.1% | 70.02% | 69.96% | 69.9% | 69.85% | 69.81% | 69.77% | 69.73% | 69.7% | 69.67% | 69.65% | 69.62% | 69.59% | 69.56% | 69.53% | 69.5%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 3.652% | 6.922% | 8.792% | 9.313% | 9.568% | 9.712% | 9.801% | 9.859% | 9.897% | 9.903% | 9.908% | 9.912% | 9.915% | 9.917% | 9.919% | 9.92% | 9.92% | 9.921% | 9.921% | 9.921% | 9.921% | 9.924% | 9.924% | 9.924% | 9.923% | 9.923% | 9.923% | 9.926% | 9.929% | 9.932% | 9.934%
Central QLD (CQ) | 3.225% | 7.489% | 10.1% | 10.85% | 11.23% | 11.45% | 11.59% | 11.68% | 11.73% | 11.75% | 11.76% | 11.77% | 11.77% | 11.78% | 11.78% | 11.78% | 11.78% | 11.78% | 11.78% | 11.78% | 11.78% | 11.79% | 11.79% | 11.79% | 11.79% | 11.78% | 11.79% | 11.79% | 11.79% | 11.8% | 11.8%
Gladstone Grid (GG) | 0.1802% | 0.6787% | 0.9637% | 1.046% | 1.086% | 1.11% | 1.125% | 1.132% | 1.138% | 1.138% | 1.137% | 1.137% | 1.137% | 1.137% | 1.137% | 1.137% | 1.136% | 1.136% | 1.136% | 1.136% | 1.136% | 1.136% | 1.136% | 1.136% | 1.136% | 1.135% | 1.135% | 1.136% | 1.136% | 1.136% | 1.136%
Southern QLD (SQ) | 92.94% | 84.91% | 80.15% | 78.79% | 78.12% | 77.73% | 77.48% | 77.33% | 77.23% | 77.21% | 77.19% | 77.18% | 77.18% | 77.17% | 77.17% | 77.16% | 77.16% | 77.16% | 77.16% | 77.16% | 77.16% | 77.15% | 77.15% | 77.15% | 77.16% | 77.16% | 77.16% | 77.15% | 77.14% | 77.13% | 77.13%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 99.18% | 97.21% | 96.12% | 95.82% | 95.67% | 95.59% | 95.53% | 95.5% | 95.48% | 95.39% | 95.33% | 95.28% | 95.25% | 95.22% | 95.2% | 95.18% | 95.16% | 95.15% | 95.13% | 95.12% | 95.11% | 95.1% | 95.1% | 95.09% | 95.09% | 95.08% | 95.07% | 95.07% | 95.06% | 95.06% | 95.05%
South East South Australia (SESA) | 0.8206% | 2.786% | 3.881% | 4.183% | 4.33% | 4.414% | 4.465% | 4.499% | 4.522% | 4.609% | 4.671% | 4.717% | 4.753% | 4.782% | 4.805% | 4.824% | 4.84% | 4.854% | 4.866% | 4.877% | 4.886% | 4.896% | 4.903% | 4.909% | 4.915% | 4.92% | 4.925% | 4.931% | 4.936% | 4.942% | 4.948%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 6.123% | 8.305% | 9.298% | 9.846% | 10.19% | 10.42% | 10.58% | 10.73% | 10.84% | 10.91% | 10.97% | 11.01% | 11.05% | 11.07% | 11.09% | 11.11% | 11.12% | 11.14% | 11.15% | 11.15% | 11.16% | 11.17% | 11.18% | 11.19% | 11.2% | 11.2% | 11.21% | 11.22% | 11.23% | 11.24% | 11.25%
Central NSW (CNSW) | 4.113% | 5.568% | 6.217% | 6.581% | 6.812% | 6.974% | 7.09% | 7.239% | 7.34% | 7.413% | 7.469% | 7.512% | 7.545% | 7.57% | 7.591% | 7.607% | 7.621% | 7.633% | 7.643% | 7.652% | 7.66% | 7.668% | 7.678% | 7.689% | 7.699% | 7.71% | 7.721% | 7.733% | 7.745% | 7.758% | 7.771%
South NSW (SNSW) | 14.6% | 13.6% | 12.77% | 12.25% | 11.92% | 11.68% | 11.56% | 11.51% | 11.49% | 11.48% | 11.47% | 11.46% | 11.46% | 11.45% | 11.44% | 11.44% | 11.43% | 11.43% | 11.43% | 11.42% | 11.42% | 11.42% | 11.43% | 11.45% | 11.47% | 11.48% | 11.5% | 11.52% | 11.53% | 11.55% | 11.57%
Sydney, Newcastle and Wooloongong (SNW) | 75.17% | 72.53% | 71.71% | 71.32% | 71.08% | 70.92% | 70.77% | 70.51% | 70.33% | 70.2% | 70.09% | 70.01% | 69.95% | 69.91% | 69.87% | 69.84% | 69.82% | 69.8% | 69.79% | 69.77% | 69.76% | 69.75% | 69.71% | 69.67% | 69.64% | 69.6% | 69.57% | 69.53% | 69.49% | 69.45% | 69.41%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 5.648% | 7.819% | 8.629% | 9.056% | 9.325% | 9.512% | 9.634% | 9.699% | 9.75% | 9.791% | 9.824% | 9.85% | 9.869% | 9.883% | 9.893% | 9.9% | 9.907% | 9.911% | 9.915% | 9.919% | 9.921% | 9.926% | 9.933% | 9.941% | 9.947% | 9.953% | 9.959% | 9.965% | 9.971% | 9.977% | 9.983%
Central QLD (CQ) | 8.024% | 10.45% | 11.2% | 11.51% | 11.65% | 11.73% | 11.79% | 11.79% | 11.8% | 11.8% | 11.8% | 11.8% | 11.81% | 11.81% | 11.81% | 11.81% | 11.81% | 11.81% | 11.81% | 11.81% | 11.81% | 11.81% | 11.82% | 11.82% | 11.83% | 11.84% | 11.84% | 11.85% | 11.86% | 11.87% | 11.88%
Gladstone Grid (GG) | 0.8333% | 1.057% | 1.126% | 1.151% | 1.159% | 1.162% | 1.165% | 1.158% | 1.153% | 1.15% | 1.147% | 1.145% | 1.143% | 1.142% | 1.141% | 1.141% | 1.14% | 1.139% | 1.139% | 1.139% | 1.138% | 1.138% | 1.139% | 1.139% | 1.139% | 1.139% | 1.14% | 1.14% | 1.141% | 1.141% | 1.142%
Southern QLD (SQ) | 85.5% | 80.67% | 79.04% | 78.29% | 77.86% | 77.59% | 77.41% | 77.35% | 77.3% | 77.26% | 77.23% | 77.2% | 77.18% | 77.17% | 77.16% | 77.15% | 77.14% | 77.14% | 77.14% | 77.13% | 77.13% | 77.12% | 77.11% | 77.1% | 77.08% | 77.07% | 77.06% | 77.04% | 77.03% | 77.01% | 77%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 98.62% | 96.82% | 96.16% | 95.87% | 95.71% | 95.62% | 95.56% | 95.42% | 95.33% | 95.27% | 95.22% | 95.19% | 95.16% | 95.14% | 95.13% | 95.11% | 95.1% | 95.09% | 95.08% | 95.08% | 95.07% | 95.06% | 95.05% | 95.05% | 95.04% | 95.03% | 95.02% | 95.01% | 95.01% | 95% | 94.99%
South East South Australia (SESA) | 1.379% | 3.178% | 3.836% | 4.13% | 4.287% | 4.381% | 4.439% | 4.58% | 4.669% | 4.731% | 4.776% | 4.811% | 4.837% | 4.857% | 4.874% | 4.888% | 4.899% | 4.909% | 4.918% | 4.925% | 4.931% | 4.938% | 4.946% | 4.953% | 4.961% | 4.969% | 4.977% | 4.985% | 4.994% | 5.003% | 5.013%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
FCEV (Uptake, % of regional allocation)
Number of FCEVs in use.
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 3.02% | 10.05% | 11.16% | 11.57% | 11.73% | 11.82% | 11.9% | 11.97% | 12.03% | 12.1% | 12.17% | 12.23% | 12.3% | 12.37% | 12.45% | 12.52% | 12.59% | 12.67% | 12.75% | 12.83% | 12.92% | 13.02% | 13.11% | 13.2% | 13.31% | 13.41% | 13.53% | 13.65% | 13.75% | 13.84% | 13.94%
Central NSW (CNSW) | 2.044% | 6.808% | 7.537% | 7.813% | 7.917% | 7.986% | 8.103% | 8.243% | 8.396% | 8.562% | 8.739% | 8.924% | 9.117% | 9.315% | 9.52% | 9.732% | 9.951% | 10.18% | 10.41% | 10.65% | 10.9% | 11.17% | 11.44% | 11.72% | 12.03% | 12.36% | 12.71% | 13.05% | 13.35% | 13.64% | 13.92%
South NSW (SNSW) | 74.9% | 24.03% | 15% | 11.95% | 10.65% | 10.02% | 9.817% | 9.791% | 9.857% | 9.982% | 10.15% | 10.34% | 10.56% | 10.8% | 11.06% | 11.32% | 11.61% | 11.9% | 12.21% | 12.53% | 12.87% | 13.15% | 13.51% | 13.9% | 14.33% | 14.78% | 15.26% | 15.73% | 16.16% | 16.55% | 16.94%
Sydney, Newcastle and Wooloongong (SNW) | 20.04% | 59.11% | 66.3% | 68.66% | 69.7% | 70.17% | 70.18% | 70% | 69.71% | 69.36% | 68.95% | 68.5% | 68.01% | 67.51% | 66.98% | 66.42% | 65.85% | 65.25% | 64.63% | 63.98% | 63.31% | 62.67% | 61.95% | 61.17% | 60.34% | 59.45% | 58.5% | 57.58% | 56.74% | 55.97% | 55.2%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 5.474% | 8.642% | 9.635% | 10.07% | 10.26% | 10.37% | 10.44% | 10.49% | 10.53% | 10.56% | 10.6% | 10.63% | 10.66% | 10.69% | 10.72% | 10.74% | 10.77% | 10.8% | 10.83% | 10.86% | 10.89% | 10.92% | 10.96% | 10.99% | 11.02% | 11.06% | 11.1% | 11.13% | 11.16% | 11.19% | 11.22%
Central QLD (CQ) | 20.12% | 15.24% | 13.52% | 12.83% | 12.51% | 12.34% | 12.3% | 12.31% | 12.35% | 12.41% | 12.48% | 12.56% | 12.65% | 12.74% | 12.84% | 12.94% | 13.05% | 13.15% | 13.27% | 13.38% | 13.5% | 13.62% | 13.73% | 13.86% | 14.01% | 14.16% | 14.32% | 14.47% | 14.61% | 14.74% | 14.87%
Gladstone Grid (GG) | 3.398% | 2.006% | 1.532% | 1.336% | 1.248% | 1.2% | 1.173% | 1.154% | 1.141% | 1.129% | 1.119% | 1.11% | 1.102% | 1.094% | 1.087% | 1.079% | 1.072% | 1.065% | 1.058% | 1.051% | 1.044% | 1.037% | 1.025% | 1.018% | 1.01% | 1.003% | 0.9944% | 0.9865% | 0.9794% | 0.9729% | 0.9663%
Southern QLD (SQ) | 71.01% | 74.11% | 75.31% | 75.77% | 75.99% | 76.09% | 76.09% | 76.04% | 75.98% | 75.89% | 75.8% | 75.7% | 75.59% | 75.47% | 75.36% | 75.24% | 75.11% | 74.98% | 74.85% | 74.71% | 74.57% | 74.43% | 74.29% | 74.13% | 73.96% | 73.78% | 73.59% | 73.41% | 73.25% | 73.1% | 72.95%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 99.25% | 97.83% | 96.71% | 96.24% | 95.98% | 95.81% | 95.7% | 95.63% | 95.57% | 95.53% | 95.5% | 95.48% | 95.46% | 95.45% | 95.43% | 95.42% | 95.42% | 95.41% | 95.4% | 95.4% | 95.39% | 95.38% | 95.38% | 95.37% | 95.37% | 95.37% | 95.37% | 95.37% | 95.36% | 95.36% | 95.36%
South East South Australia (SESA) | 0.7467% | 2.167% | 3.289% | 3.758% | 4.023% | 4.186% | 4.296% | 4.373% | 4.427% | 4.468% | 4.498% | 4.522% | 4.54% | 4.555% | 4.567% | 4.576% | 4.585% | 4.592% | 4.598% | 4.603% | 4.608% | 4.62% | 4.623% | 4.625% | 4.628% | 4.63% | 4.632% | 4.634% | 4.635% | 4.637% | 4.638%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 3.652% | 10.2% | 11.16% | 11.51% | 11.61% | 11.66% | 11.66% | 11.67% | 11.67% | 12.31% | 12.51% | 12.6% | 12.66% | 12.69% | 12.72% | 12.74% | 12.75% | 12.76% | 12.77% | 12.78% | 12.79% | 12.79% | 12.8% | 12.8% | 12.81% | 12.81% | 12.81% | 12.82% | 12.83% | 12.84% | 12.85%
Central NSW (CNSW) | 2.556% | 6.896% | 7.527% | 7.756% | 7.828% | 7.862% | 7.864% | 8.095% | 8.303% | 10.47% | 11.1% | 11.4% | 11.58% | 11.7% | 11.78% | 11.84% | 11.89% | 11.92% | 11.95% | 11.98% | 12% | 12.02% | 12.03% | 12.05% | 12.06% | 12.07% | 12.08% | 12.1% | 12.13% | 12.15% | 12.17%
South NSW (SNSW) | 66.81% | 22.15% | 14.58% | 12.17% | 11.22% | 10.85% | 10.82% | 11.2% | 11.55% | 14.34% | 15.15% | 15.53% | 15.76% | 15.9% | 16.01% | 16.09% | 16.14% | 16.19% | 16.23% | 16.26% | 16.29% | 16.31% | 16.33% | 16.35% | 16.37% | 16.38% | 16.39% | 16.42% | 16.46% | 16.49% | 16.52%
Sydney, Newcastle and Wooloongong (SNW) | 26.98% | 60.74% | 66.72% | 68.57% | 69.34% | 69.63% | 69.65% | 69.04% | 68.48% | 62.87% | 61.24% | 60.46% | 60.01% | 59.71% | 59.5% | 59.34% | 59.22% | 59.12% | 59.04% | 58.98% | 58.92% | 58.87% | 58.83% | 58.8% | 58.77% | 58.74% | 58.72% | 58.65% | 58.58% | 58.52% | 58.45%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 10.09% | 10.59% | 10.53% | 10.55% | 10.54% | 10.56% | 10.57% | 10.53% | 10.48% | 10.44% | 10.43% | 10.42% | 10.42% | 10.42% | 10.42% | 10.42% | 10.42% | 10.42% | 10.41% | 10.41% | 10.41% | 10.41% | 10.41% | 10.41% | 10.41% | 10.41% | 10.41% | 10.42% | 10.42% | 10.42% | 10.42%
Central QLD (CQ) | 18.74% | 12.92% | 12.38% | 12.24% | 12.19% | 12.18% | 12.22% | 12.34% | 12.45% | 13% | 13.15% | 13.22% | 13.26% | 13.29% | 13.3% | 13.32% | 13.33% | 13.33% | 13.34% | 13.35% | 13.35% | 13.36% | 13.36% | 13.36% | 13.37% | 13.37% | 13.37% | 13.38% | 13.39% | 13.4% | 13.4%
Gladstone Grid (GG) | 2.008% | 1.166% | 1.122% | 1.112% | 1.113% | 1.115% | 1.117% | 1.117% | 1.115% | 1.069% | 1.055% | 1.048% | 1.043% | 1.041% | 1.039% | 1.037% | 1.036% | 1.035% | 1.035% | 1.034% | 1.033% | 1.033% | 1.033% | 1.032% | 1.032% | 1.032% | 1.032% | 1.031% | 1.031% | 1.031% | 1.031%
Southern QLD (SQ) | 69.17% | 75.32% | 75.97% | 76.1% | 76.16% | 76.15% | 76.09% | 76.01% | 75.96% | 75.49% | 75.37% | 75.31% | 75.28% | 75.26% | 75.24% | 75.23% | 75.22% | 75.22% | 75.21% | 75.2% | 75.2% | 75.2% | 75.19% | 75.19% | 75.19% | 75.19% | 75.18% | 75.17% | 75.16% | 75.15% | 75.14%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 99.18% | 97.21% | 96.12% | 95.82% | 95.67% | 95.59% | 95.53% | 95.5% | 95.48% | 95.37% | 95.3% | 95.24% | 95.2% | 95.16% | 95.14% | 95.11% | 95.09% | 95.08% | 95.06% | 95.05% | 95.04% | 95.03% | 95.02% | 95.01% | 95% | 95% | 94.99% | 94.99% | 94.98% | 94.97% | 94.97%
South East South Australia (SESA) | 0.8218% | 2.788% | 3.882% | 4.184% | 4.331% | 4.414% | 4.466% | 4.5% | 4.525% | 4.629% | 4.704% | 4.759% | 4.802% | 4.837% | 4.864% | 4.887% | 4.907% | 4.923% | 4.938% | 4.95% | 4.961% | 4.973% | 4.981% | 4.989% | 4.995% | 5.002% | 5.009% | 5.015% | 5.021% | 5.027% | 5.034%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 8.469% | 9.88% | 10.38% | 10.74% | 10.98% | 11.17% | 11.22% | 11.57% | 11.65% | 11.68% | 11.69% | 11.7% | 11.71% | 11.71% | 11.72% | 11.72% | 11.72% | 11.72% | 11.72% | 11.72% | 11.73% | 11.73% | 11.74% | 11.75% | 11.76% | 11.77% | 11.78% | 11.79% | 11.81% | 11.82% | 11.83%
Central NSW (CNSW) | 4.35% | 5.555% | 6.123% | 6.575% | 6.893% | 7.151% | 7.693% | 8.729% | 8.908% | 8.983% | 9.024% | 9.049% | 9.064% | 9.075% | 9.083% | 9.089% | 9.094% | 9.098% | 9.101% | 9.104% | 9.106% | 9.108% | 9.128% | 9.149% | 9.17% | 9.192% | 9.215% | 9.24% | 9.265% | 9.291% | 9.318%
South NSW (SNSW) | 23.31% | 14.88% | 12.83% | 11.99% | 11.6% | 11.37% | 11.44% | 12.59% | 12.76% | 12.84% | 12.88% | 12.9% | 12.92% | 12.93% | 12.94% | 12.94% | 12.95% | 12.95% | 12.95% | 12.96% | 12.96% | 12.96% | 12.99% | 13.02% | 13.04% | 13.07% | 13.1% | 13.13% | 13.16% | 13.19% | 13.22%
Sydney, Newcastle and Wooloongong (SNW) | 63.88% | 69.68% | 70.67% | 70.7% | 70.54% | 70.31% | 69.65% | 67.11% | 66.68% | 66.5% | 66.41% | 66.35% | 66.31% | 66.28% | 66.26% | 66.25% | 66.24% | 66.23% | 66.22% | 66.21% | 66.21% | 66.2% | 66.15% | 66.09% | 66.03% | 65.97% | 65.91% | 65.84% | 65.77% | 65.7% | 65.63%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 9.346% | 9.541% | 9.668% | 9.821% | 9.953% | 10.09% | 10.14% | 10.07% | 10.09% | 10.09% | 10.1% | 10.1% | 10.1% | 10.1% | 10.1% | 10.1% | 10.1% | 10.1% | 10.1% | 10.1% | 10.1% | 10.1% | 10.1% | 10.11% | 10.11% | 10.12% | 10.12% | 10.13% | 10.13% | 10.14% | 10.15%
Central QLD (CQ) | 30.74% | 28.05% | 25.73% | 23.45% | 21.38% | 19.42% | 14.01% | 12.87% | 12.61% | 12.49% | 12.42% | 12.38% | 12.36% | 12.35% | 12.34% | 12.33% | 12.33% | 12.32% | 12.32% | 12.32% | 12.31% | 12.31% | 12.32% | 12.33% | 12.34% | 12.34% | 12.35% | 12.36% | 12.38% | 12.39% | 12.4%
Gladstone Grid (GG) | 3.442% | 3.093% | 2.806% | 2.524% | 2.268% | 2.027% | 1.366% | 1.189% | 1.15% | 1.132% | 1.123% | 1.117% | 1.114% | 1.112% | 1.11% | 1.109% | 1.109% | 1.108% | 1.107% | 1.107% | 1.107% | 1.106% | 1.106% | 1.106% | 1.106% | 1.106% | 1.106% | 1.107% | 1.107% | 1.107% | 1.107%
Southern QLD (SQ) | 56.47% | 59.31% | 61.8% | 64.2% | 66.4% | 68.46% | 74.49% | 75.87% | 76.16% | 76.29% | 76.36% | 76.4% | 76.43% | 76.44% | 76.45% | 76.46% | 76.47% | 76.47% | 76.48% | 76.48% | 76.48% | 76.48% | 76.47% | 76.46% | 76.45% | 76.43% | 76.42% | 76.4% | 76.38% | 76.36% | 76.35%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 98.62% | 96.82% | 96.16% | 95.87% | 95.71% | 95.62% | 95.56% | 95.39% | 95.28% | 95.21% | 95.16% | 95.12% | 95.09% | 95.07% | 95.05% | 95.03% | 95.02% | 95.01% | 95% | 94.99% | 94.99% | 94.98% | 94.97% | 94.96% | 94.95% | 94.94% | 94.94% | 94.93% | 94.92% | 94.91% | 94.9%
South East South Australia (SESA) | 1.383% | 3.18% | 3.837% | 4.131% | 4.287% | 4.382% | 4.442% | 4.613% | 4.718% | 4.789% | 4.841% | 4.879% | 4.909% | 4.932% | 4.951% | 4.966% | 4.979% | 4.99% | 4.999% | 5.008% | 5.015% | 5.022% | 5.031% | 5.039% | 5.047% | 5.056% | 5.065% | 5.074% | 5.084% | 5.094% | 5.104%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Embedded energy storages (small-scale batteries, % of regional allocation)
Embeddded customer battery installations
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 16.21% | 16.03% | 15.9% | 15.81% | 15.58% | 15.4% | 15.29% | 15.25% | 15.24% | 15.22% | 15.23% | 15.21% | 15.2% | 15.16% | 15.13% | 15.09% | 15.05% | 15.02% | 15% | 14.99% | 14.99% | 14.97% | 14.94% | 14.91% | 14.87% | 14.83% | 14.79% | 14.76% | 14.72% | 14.69% | 14.66%
Central NSW (CNSW) | 6.768% | 6.731% | 6.698% | 6.729% | 6.714% | 6.65% | 6.63% | 6.639% | 6.681% | 6.718% | 6.751% | 6.801% | 6.83% | 6.864% | 6.886% | 6.906% | 6.932% | 6.962% | 6.985% | 7.008% | 7.025% | 7.042% | 7.059% | 7.072% | 7.08% | 7.09% | 7.092% | 7.092% | 7.092% | 7.089% | 7.086%
South NSW (SNSW) | 13.54% | 13.52% | 13.56% | 13.69% | 13.86% | 13.96% | 14.04% | 14.1% | 14.15% | 14.22% | 14.28% | 14.33% | 14.38% | 14.44% | 14.49% | 14.53% | 14.56% | 14.59% | 14.61% | 14.65% | 14.69% | 14.73% | 14.77% | 14.81% | 14.84% | 14.87% | 14.89% | 14.91% | 14.93% | 14.96% | 14.98%
Sydney, Newcastle and Wooloongong (SNW) | 63.48% | 63.71% | 63.84% | 63.77% | 63.85% | 63.99% | 64.04% | 64.01% | 63.93% | 63.84% | 63.74% | 63.66% | 63.59% | 63.53% | 63.49% | 63.47% | 63.45% | 63.43% | 63.4% | 63.35% | 63.29% | 63.26% | 63.23% | 63.21% | 63.2% | 63.21% | 63.22% | 63.24% | 63.25% | 63.26% | 63.27%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 14.7% | 14.59% | 14.47% | 14.39% | 14.29% | 14.28% | 14.16% | 14.07% | 14.02% | 13.95% | 13.89% | 13.83% | 13.8% | 13.74% | 13.69% | 13.64% | 13.59% | 13.57% | 13.55% | 13.53% | 13.52% | 13.49% | 13.46% | 13.43% | 13.41% | 13.38% | 13.36% | 13.34% | 13.33% | 13.32% | 13.31%
Central QLD (CQ) | 13.54% | 13.42% | 13.4% | 13.29% | 13.31% | 13.25% | 13.14% | 13.12% | 13.07% | 13.06% | 13.06% | 13.05% | 13.03% | 13.03% | 13% | 12.99% | 12.98% | 12.98% | 12.99% | 12.99% | 13% | 13% | 12.99% | 12.98% | 12.97% | 12.96% | 12.95% | 12.93% | 12.91% | 12.9% | 12.89%
Gladstone Grid (GG) | 0.8075% | 0.8014% | 0.7982% | 0.7925% | 0.8016% | 0.7949% | 0.7953% | 0.7917% | 0.7911% | 0.7954% | 0.7989% | 0.8017% | 0.8029% | 0.8051% | 0.8064% | 0.8066% | 0.8083% | 0.8098% | 0.8125% | 0.8151% | 0.8166% | 0.8179% | 0.8196% | 0.8209% | 0.8212% | 0.8213% | 0.8211% | 0.8216% | 0.8217% | 0.8213% | 0.8209%
Southern QLD (SQ) | 70.95% | 71.18% | 71.34% | 71.53% | 71.59% | 71.68% | 71.9% | 72.02% | 72.12% | 72.19% | 72.25% | 72.31% | 72.37% | 72.43% | 72.5% | 72.57% | 72.62% | 72.64% | 72.65% | 72.67% | 72.67% | 72.69% | 72.73% | 72.77% | 72.8% | 72.83% | 72.87% | 72.91% | 72.94% | 72.96% | 72.98%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 96.58% | 96.55% | 96.53% | 96.5% | 96.48% | 96.46% | 96.43% | 96.41% | 96.4% | 96.4% | 96.39% | 96.36% | 96.35% | 96.32% | 96.32% | 96.32% | 96.32% | 96.32% | 96.32% | 96.33% | 96.32% | 96.3% | 96.29% | 96.29% | 96.28% | 96.28% | 96.28% | 96.28% | 96.27% | 96.26% | 96.25%
South East South Australia (SESA) | 3.418% | 3.449% | 3.473% | 3.498% | 3.518% | 3.537% | 3.568% | 3.589% | 3.595% | 3.599% | 3.612% | 3.644% | 3.652% | 3.679% | 3.682% | 3.68% | 3.681% | 3.683% | 3.681% | 3.675% | 3.683% | 3.701% | 3.71% | 3.712% | 3.715% | 3.717% | 3.718% | 3.721% | 3.734% | 3.743% | 3.752%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 16.35% | 15.39% | 15.07% | 14.93% | 14.84% | 14.81% | 14.79% | 14.82% | 14.81% | 14.79% | 14.78% | 14.8% | 14.81% | 14.79% | 14.76% | 14.74% | 14.72% | 14.7% | 14.68% | 14.65% | 14.64% | 14.62% | 14.6% | 14.57% | 14.53% | 14.49% | 14.46% | 14.43% | 14.41% | 14.4% | 14.39%
Central NSW (CNSW) | 7.052% | 6.624% | 6.504% | 6.481% | 6.512% | 6.579% | 6.637% | 6.709% | 6.785% | 6.856% | 6.939% | 7.006% | 7.061% | 7.105% | 7.141% | 7.182% | 7.22% | 7.251% | 7.282% | 7.313% | 7.347% | 7.381% | 7.416% | 7.44% | 7.468% | 7.49% | 7.509% | 7.524% | 7.537% | 7.548% | 7.559%
South NSW (SNSW) | 13.56% | 13.51% | 13.56% | 13.66% | 13.74% | 13.82% | 13.9% | 13.96% | 14.01% | 14.06% | 14.1% | 14.15% | 14.19% | 14.22% | 14.25% | 14.28% | 14.31% | 14.34% | 14.37% | 14.41% | 14.44% | 14.47% | 14.48% | 14.5% | 14.51% | 14.51% | 14.53% | 14.55% | 14.57% | 14.61% | 14.64%
Sydney, Newcastle and Wooloongong (SNW) | 63.04% | 64.48% | 64.87% | 64.93% | 64.91% | 64.78% | 64.67% | 64.52% | 64.39% | 64.3% | 64.19% | 64.04% | 63.94% | 63.88% | 63.84% | 63.79% | 63.76% | 63.71% | 63.67% | 63.63% | 63.58% | 63.53% | 63.5% | 63.49% | 63.5% | 63.51% | 63.5% | 63.49% | 63.48% | 63.45% | 63.42%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 14.59% | 14.14% | 13.88% | 13.69% | 13.51% | 13.34% | 13.18% | 13.1% | 13.02% | 12.96% | 12.91% | 12.87% | 12.82% | 12.78% | 12.73% | 12.69% | 12.66% | 12.64% | 12.61% | 12.6% | 12.58% | 12.56% | 12.55% | 12.53% | 12.5% | 12.49% | 12.47% | 12.47% | 12.46% | 12.46% | 12.46%
Central QLD (CQ) | 13.54% | 13.18% | 12.96% | 12.87% | 12.79% | 12.73% | 12.67% | 12.65% | 12.67% | 12.68% | 12.69% | 12.71% | 12.71% | 12.71% | 12.71% | 12.71% | 12.71% | 12.72% | 12.72% | 12.73% | 12.74% | 12.74% | 12.75% | 12.76% | 12.75% | 12.75% | 12.76% | 12.76% | 12.76% | 12.76% | 12.77%
Gladstone Grid (GG) | 0.8097% | 0.7933% | 0.7869% | 0.7886% | 0.7893% | 0.7931% | 0.7945% | 0.7984% | 0.8047% | 0.8091% | 0.8142% | 0.8187% | 0.8219% | 0.8249% | 0.8272% | 0.8295% | 0.8317% | 0.8337% | 0.8357% | 0.8379% | 0.8396% | 0.8413% | 0.8432% | 0.8448% | 0.8456% | 0.8465% | 0.8474% | 0.8478% | 0.8484% | 0.8493% | 0.8501%
Southern QLD (SQ) | 71.06% | 71.88% | 72.38% | 72.66% | 72.9% | 73.14% | 73.36% | 73.45% | 73.51% | 73.55% | 73.58% | 73.61% | 73.65% | 73.69% | 73.73% | 73.77% | 73.8% | 73.82% | 73.83% | 73.83% | 73.84% | 73.85% | 73.86% | 73.87% | 73.9% | 73.91% | 73.92% | 73.93% | 73.93% | 73.92% | 73.92%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 96.6% | 96.49% | 96.45% | 96.38% | 96.34% | 96.34% | 96.35% | 96.36% | 96.36% | 96.34% | 96.34% | 96.36% | 96.36% | 96.36% | 96.34% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.36% | 96.36% | 96.36% | 96.36% | 96.36%
South East South Australia (SESA) | 3.403% | 3.514% | 3.549% | 3.622% | 3.663% | 3.655% | 3.646% | 3.64% | 3.64% | 3.657% | 3.656% | 3.644% | 3.642% | 3.641% | 3.655% | 3.653% | 3.647% | 3.646% | 3.652% | 3.655% | 3.652% | 3.648% | 3.648% | 3.647% | 3.646% | 3.645% | 3.643% | 3.642% | 3.641% | 3.64% | 3.639%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 16.31% | 15.73% | 15.22% | 15.06% | 14.93% | 14.86% | 14.77% | 14.76% | 14.74% | 14.71% | 14.69% | 14.63% | 14.56% | 14.47% | 14.47% | 14.47% | 14.47% | 14.45% | 14.44% | 14.42% | 14.41% | 14.38% | 14.35% | 14.3% | 14.26% | 14.22% | 14.18% | 14.15% | 14.13% | 14.11% | 14.1%
Central NSW (CNSW) | 6.792% | 6.722% | 6.504% | 6.494% | 6.537% | 6.607% | 6.668% | 6.763% | 6.851% | 6.935% | 7.022% | 7.079% | 7.137% | 7.192% | 7.228% | 7.271% | 7.302% | 7.332% | 7.359% | 7.389% | 7.415% | 7.437% | 7.464% | 7.485% | 7.509% | 7.529% | 7.546% | 7.559% | 7.572% | 7.581% | 7.59%
South NSW (SNSW) | 13.1% | 13.31% | 13.42% | 13.56% | 13.67% | 13.78% | 13.9% | 13.99% | 14.07% | 14.13% | 14.14% | 14.13% | 14.09% | 14.07% | 14.11% | 14.15% | 14.19% | 14.24% | 14.29% | 14.33% | 14.37% | 14.4% | 14.43% | 14.46% | 14.46% | 14.48% | 14.51% | 14.54% | 14.58% | 14.63% | 14.68%
Sydney, Newcastle and Wooloongong (SNW) | 63.79% | 64.24% | 64.85% | 64.88% | 64.86% | 64.75% | 64.67% | 64.49% | 64.34% | 64.22% | 64.15% | 64.16% | 64.21% | 64.27% | 64.19% | 64.11% | 64.04% | 63.98% | 63.91% | 63.86% | 63.81% | 63.79% | 63.75% | 63.76% | 63.77% | 63.77% | 63.77% | 63.75% | 63.73% | 63.68% | 63.63%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 14.42% | 14% | 13.92% | 13.84% | 13.74% | 13.55% | 13.32% | 13.02% | 12.86% | 12.78% | 12.73% | 12.7% | 12.68% | 12.66% | 12.64% | 12.62% | 12.6% | 12.59% | 12.58% | 12.57% | 12.56% | 12.54% | 12.53% | 12.51% | 12.49% | 12.47% | 12.46% | 12.46% | 12.45% | 12.45% | 12.45%
Central QLD (CQ) | 13.37% | 13.32% | 12.98% | 12.92% | 12.85% | 12.83% | 12.71% | 12.62% | 12.55% | 12.54% | 12.57% | 12.6% | 12.63% | 12.65% | 12.67% | 12.68% | 12.7% | 12.71% | 12.72% | 12.73% | 12.74% | 12.74% | 12.75% | 12.75% | 12.75% | 12.76% | 12.76% | 12.76% | 12.76% | 12.77% | 12.77%
Gladstone Grid (GG) | 0.8093% | 0.822% | 0.7794% | 0.7758% | 0.777% | 0.7881% | 0.811% | 0.8169% | 0.8097% | 0.8093% | 0.8135% | 0.8169% | 0.821% | 0.8236% | 0.8261% | 0.8294% | 0.8319% | 0.8341% | 0.8361% | 0.8383% | 0.8403% | 0.8413% | 0.8431% | 0.8441% | 0.8454% | 0.8467% | 0.8476% | 0.8481% | 0.8486% | 0.8498% | 0.8511%
Southern QLD (SQ) | 71.4% | 71.86% | 72.33% | 72.46% | 72.63% | 72.83% | 73.16% | 73.54% | 73.78% | 73.87% | 73.89% | 73.88% | 73.86% | 73.87% | 73.87% | 73.87% | 73.87% | 73.87% | 73.86% | 73.87% | 73.86% | 73.87% | 73.88% | 73.89% | 73.91% | 73.92% | 73.93% | 73.93% | 73.94% | 73.93% | 73.93%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 96.61% | 96.52% | 96.47% | 96.37% | 96.35% | 96.34% | 96.34% | 96.35% | 96.34% | 96.34% | 96.35% | 96.36% | 96.36% | 96.36% | 96.36% | 96.37% | 96.37% | 96.38% | 96.37% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.39% | 96.39% | 96.39%
South East South Australia (SESA) | 3.394% | 3.48% | 3.526% | 3.627% | 3.646% | 3.656% | 3.657% | 3.648% | 3.659% | 3.663% | 3.651% | 3.643% | 3.638% | 3.644% | 3.638% | 3.634% | 3.629% | 3.625% | 3.627% | 3.625% | 3.623% | 3.621% | 3.62% | 3.619% | 3.619% | 3.618% | 3.617% | 3.616% | 3.615% | 3.614% | 3.613%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Aggregated embedded energy storages (small-scale batteries, % of regional allocation)
Batteries that are coordinated in a VPP-style operating arrangement
Progressive Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 16.21% | 16.03% | 15.9% | 15.81% | 15.58% | 15.4% | 15.29% | 15.25% | 15.24% | 15.22% | 15.23% | 15.21% | 15.2% | 15.16% | 15.13% | 15.09% | 15.05% | 15.02% | 15% | 14.99% | 14.99% | 14.97% | 14.94% | 14.91% | 14.87% | 14.83% | 14.79% | 14.76% | 14.72% | 14.69% | 14.66%
Central NSW (CNSW) | 6.768% | 6.731% | 6.698% | 6.729% | 6.714% | 6.65% | 6.63% | 6.639% | 6.681% | 6.718% | 6.751% | 6.801% | 6.83% | 6.864% | 6.886% | 6.906% | 6.932% | 6.962% | 6.985% | 7.008% | 7.025% | 7.042% | 7.059% | 7.072% | 7.08% | 7.09% | 7.092% | 7.092% | 7.092% | 7.089% | 7.086%
South NSW (SNSW) | 13.54% | 13.52% | 13.56% | 13.69% | 13.86% | 13.96% | 14.04% | 14.1% | 14.15% | 14.22% | 14.28% | 14.33% | 14.38% | 14.44% | 14.49% | 14.53% | 14.56% | 14.59% | 14.61% | 14.65% | 14.69% | 14.73% | 14.77% | 14.81% | 14.84% | 14.87% | 14.89% | 14.91% | 14.93% | 14.96% | 14.98%
Sydney, Newcastle and Wooloongong (SNW) | 63.48% | 63.71% | 63.84% | 63.77% | 63.85% | 63.99% | 64.04% | 64.01% | 63.93% | 63.84% | 63.74% | 63.66% | 63.59% | 63.53% | 63.49% | 63.47% | 63.45% | 63.43% | 63.4% | 63.35% | 63.29% | 63.26% | 63.23% | 63.21% | 63.2% | 63.21% | 63.22% | 63.24% | 63.25% | 63.26% | 63.27%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 14.7% | 14.59% | 14.47% | 14.39% | 14.29% | 14.28% | 14.16% | 14.07% | 14.02% | 13.95% | 13.89% | 13.83% | 13.8% | 13.74% | 13.69% | 13.64% | 13.59% | 13.57% | 13.55% | 13.53% | 13.52% | 13.49% | 13.46% | 13.43% | 13.41% | 13.38% | 13.36% | 13.34% | 13.33% | 13.32% | 13.31%
Central QLD (CQ) | 13.54% | 13.42% | 13.4% | 13.29% | 13.31% | 13.25% | 13.14% | 13.12% | 13.07% | 13.06% | 13.06% | 13.05% | 13.03% | 13.03% | 13% | 12.99% | 12.98% | 12.98% | 12.99% | 12.99% | 13% | 13% | 12.99% | 12.98% | 12.97% | 12.96% | 12.95% | 12.93% | 12.91% | 12.9% | 12.89%
Gladstone Grid (GG) | 0.8075% | 0.8014% | 0.7982% | 0.7925% | 0.8016% | 0.7949% | 0.7953% | 0.7917% | 0.7911% | 0.7954% | 0.7989% | 0.8017% | 0.8029% | 0.8051% | 0.8064% | 0.8066% | 0.8083% | 0.8098% | 0.8125% | 0.8151% | 0.8166% | 0.8179% | 0.8196% | 0.8209% | 0.8212% | 0.8213% | 0.8211% | 0.8216% | 0.8217% | 0.8213% | 0.8209%
Southern QLD (SQ) | 70.95% | 71.18% | 71.34% | 71.53% | 71.59% | 71.68% | 71.9% | 72.02% | 72.12% | 72.19% | 72.25% | 72.31% | 72.37% | 72.43% | 72.5% | 72.57% | 72.62% | 72.64% | 72.65% | 72.67% | 72.67% | 72.69% | 72.73% | 72.77% | 72.8% | 72.83% | 72.87% | 72.91% | 72.94% | 72.96% | 72.98%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 96.58% | 96.55% | 96.53% | 96.5% | 96.48% | 96.46% | 96.43% | 96.41% | 96.4% | 96.4% | 96.39% | 96.36% | 96.35% | 96.32% | 96.32% | 96.32% | 96.32% | 96.32% | 96.32% | 96.33% | 96.32% | 96.3% | 96.29% | 96.29% | 96.28% | 96.28% | 96.28% | 96.28% | 96.27% | 96.26% | 96.25%
South East South Australia (SESA) | 3.418% | 3.449% | 3.473% | 3.498% | 3.518% | 3.537% | 3.568% | 3.589% | 3.595% | 3.599% | 3.612% | 3.644% | 3.652% | 3.679% | 3.682% | 3.68% | 3.681% | 3.683% | 3.681% | 3.675% | 3.683% | 3.701% | 3.71% | 3.712% | 3.715% | 3.717% | 3.718% | 3.721% | 3.734% | 3.743% | 3.752%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Step Change
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 16.35% | 15.39% | 15.07% | 14.93% | 14.84% | 14.81% | 14.79% | 14.82% | 14.81% | 14.79% | 14.78% | 14.8% | 14.81% | 14.79% | 14.76% | 14.74% | 14.72% | 14.7% | 14.68% | 14.65% | 14.64% | 14.62% | 14.6% | 14.57% | 14.53% | 14.49% | 14.46% | 14.43% | 14.41% | 14.4% | 14.39%
Central NSW (CNSW) | 7.052% | 6.624% | 6.504% | 6.481% | 6.512% | 6.579% | 6.637% | 6.709% | 6.785% | 6.856% | 6.939% | 7.006% | 7.061% | 7.105% | 7.141% | 7.182% | 7.22% | 7.251% | 7.282% | 7.313% | 7.347% | 7.381% | 7.416% | 7.44% | 7.468% | 7.49% | 7.509% | 7.524% | 7.537% | 7.548% | 7.559%
South NSW (SNSW) | 13.56% | 13.51% | 13.56% | 13.66% | 13.74% | 13.82% | 13.9% | 13.96% | 14.01% | 14.06% | 14.1% | 14.15% | 14.19% | 14.22% | 14.25% | 14.28% | 14.31% | 14.34% | 14.37% | 14.41% | 14.44% | 14.47% | 14.48% | 14.5% | 14.51% | 14.51% | 14.53% | 14.55% | 14.57% | 14.61% | 14.64%
Sydney, Newcastle and Wooloongong (SNW) | 63.04% | 64.48% | 64.87% | 64.93% | 64.91% | 64.78% | 64.67% | 64.52% | 64.39% | 64.3% | 64.19% | 64.04% | 63.94% | 63.88% | 63.84% | 63.79% | 63.76% | 63.71% | 63.67% | 63.63% | 63.58% | 63.53% | 63.5% | 63.49% | 63.5% | 63.51% | 63.5% | 63.49% | 63.48% | 63.45% | 63.42%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 14.59% | 14.14% | 13.88% | 13.69% | 13.51% | 13.34% | 13.18% | 13.1% | 13.02% | 12.96% | 12.91% | 12.87% | 12.82% | 12.78% | 12.73% | 12.69% | 12.66% | 12.64% | 12.61% | 12.6% | 12.58% | 12.56% | 12.55% | 12.53% | 12.5% | 12.49% | 12.47% | 12.47% | 12.46% | 12.46% | 12.46%
Central QLD (CQ) | 13.54% | 13.18% | 12.96% | 12.87% | 12.79% | 12.73% | 12.67% | 12.65% | 12.67% | 12.68% | 12.69% | 12.71% | 12.71% | 12.71% | 12.71% | 12.71% | 12.71% | 12.72% | 12.72% | 12.73% | 12.74% | 12.74% | 12.75% | 12.76% | 12.75% | 12.75% | 12.76% | 12.76% | 12.76% | 12.76% | 12.77%
Gladstone Grid (GG) | 0.8097% | 0.7933% | 0.7869% | 0.7886% | 0.7893% | 0.7931% | 0.7945% | 0.7984% | 0.8047% | 0.8091% | 0.8142% | 0.8187% | 0.8219% | 0.8249% | 0.8272% | 0.8295% | 0.8317% | 0.8337% | 0.8357% | 0.8379% | 0.8396% | 0.8413% | 0.8432% | 0.8448% | 0.8456% | 0.8465% | 0.8474% | 0.8478% | 0.8484% | 0.8493% | 0.8501%
Southern QLD (SQ) | 71.06% | 71.88% | 72.38% | 72.66% | 72.9% | 73.14% | 73.36% | 73.45% | 73.51% | 73.55% | 73.58% | 73.61% | 73.65% | 73.69% | 73.73% | 73.77% | 73.8% | 73.82% | 73.83% | 73.83% | 73.84% | 73.85% | 73.86% | 73.87% | 73.9% | 73.91% | 73.92% | 73.93% | 73.93% | 73.92% | 73.92%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 96.6% | 96.49% | 96.45% | 96.38% | 96.34% | 96.34% | 96.35% | 96.36% | 96.36% | 96.34% | 96.34% | 96.36% | 96.36% | 96.36% | 96.34% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.35% | 96.36% | 96.36% | 96.36% | 96.36% | 96.36%
South East South Australia (SESA) | 3.403% | 3.514% | 3.549% | 3.622% | 3.663% | 3.655% | 3.646% | 3.64% | 3.64% | 3.657% | 3.656% | 3.644% | 3.642% | 3.641% | 3.655% | 3.653% | 3.647% | 3.646% | 3.652% | 3.655% | 3.652% | 3.648% | 3.648% | 3.647% | 3.646% | 3.645% | 3.643% | 3.642% | 3.641% | 3.64% | 3.639%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Green Energy Exports
| 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Northern NSW (NNSW) | 16.31% | 15.73% | 15.22% | 15.06% | 14.93% | 14.86% | 14.77% | 14.76% | 14.74% | 14.71% | 14.69% | 14.63% | 14.56% | 14.47% | 14.47% | 14.47% | 14.47% | 14.45% | 14.44% | 14.42% | 14.41% | 14.38% | 14.35% | 14.3% | 14.26% | 14.22% | 14.18% | 14.15% | 14.13% | 14.11% | 14.1%
Central NSW (CNSW) | 6.792% | 6.722% | 6.504% | 6.494% | 6.537% | 6.607% | 6.668% | 6.763% | 6.851% | 6.935% | 7.022% | 7.079% | 7.137% | 7.192% | 7.228% | 7.271% | 7.302% | 7.332% | 7.359% | 7.389% | 7.415% | 7.437% | 7.464% | 7.485% | 7.509% | 7.529% | 7.546% | 7.559% | 7.572% | 7.581% | 7.59%
South NSW (SNSW) | 13.1% | 13.31% | 13.42% | 13.56% | 13.67% | 13.78% | 13.9% | 13.99% | 14.07% | 14.13% | 14.14% | 14.13% | 14.09% | 14.07% | 14.11% | 14.15% | 14.19% | 14.24% | 14.29% | 14.33% | 14.37% | 14.4% | 14.43% | 14.46% | 14.46% | 14.48% | 14.51% | 14.54% | 14.58% | 14.63% | 14.68%
Sydney, Newcastle and Wooloongong (SNW) | 63.79% | 64.24% | 64.85% | 64.88% | 64.86% | 64.75% | 64.67% | 64.49% | 64.34% | 64.22% | 64.15% | 64.16% | 64.21% | 64.27% | 64.19% | 64.11% | 64.04% | 63.98% | 63.91% | 63.86% | 63.81% | 63.79% | 63.75% | 63.76% | 63.77% | 63.77% | 63.77% | 63.75% | 63.73% | 63.68% | 63.63%
QLD | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
North QLD (NQ) | 14.42% | 14% | 13.92% | 13.84% | 13.74% | 13.55% | 13.32% | 13.02% | 12.86% | 12.78% | 12.73% | 12.7% | 12.68% | 12.66% | 12.64% | 12.62% | 12.6% | 12.59% | 12.58% | 12.57% | 12.56% | 12.54% | 12.53% | 12.51% | 12.49% | 12.47% | 12.46% | 12.46% | 12.45% | 12.45% | 12.45%
Central QLD (CQ) | 13.37% | 13.32% | 12.98% | 12.92% | 12.85% | 12.83% | 12.71% | 12.62% | 12.55% | 12.54% | 12.57% | 12.6% | 12.63% | 12.65% | 12.67% | 12.68% | 12.7% | 12.71% | 12.72% | 12.73% | 12.74% | 12.74% | 12.75% | 12.75% | 12.75% | 12.76% | 12.76% | 12.76% | 12.76% | 12.77% | 12.77%
Gladstone Grid (GG) | 0.8093% | 0.822% | 0.7794% | 0.7758% | 0.777% | 0.7881% | 0.811% | 0.8169% | 0.8097% | 0.8093% | 0.8135% | 0.8169% | 0.821% | 0.8236% | 0.8261% | 0.8294% | 0.8319% | 0.8341% | 0.8361% | 0.8383% | 0.8403% | 0.8413% | 0.8431% | 0.8441% | 0.8454% | 0.8467% | 0.8476% | 0.8481% | 0.8486% | 0.8498% | 0.8511%
Southern QLD (SQ) | 71.4% | 71.86% | 72.33% | 72.46% | 72.63% | 72.83% | 73.16% | 73.54% | 73.78% | 73.87% | 73.89% | 73.88% | 73.86% | 73.87% | 73.87% | 73.87% | 73.87% | 73.87% | 73.86% | 73.87% | 73.86% | 73.87% | 73.88% | 73.89% | 73.91% | 73.92% | 73.93% | 73.93% | 73.94% | 73.93% | 73.93%
SA | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Central South Australia (CSA) | 96.61% | 96.52% | 96.47% | 96.37% | 96.35% | 96.34% | 96.34% | 96.35% | 96.34% | 96.34% | 96.35% | 96.36% | 96.36% | 96.36% | 96.36% | 96.37% | 96.37% | 96.38% | 96.37% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.38% | 96.39% | 96.39% | 96.39%
South East South Australia (SESA) | 3.394% | 3.48% | 3.526% | 3.627% | 3.646% | 3.656% | 3.657% | 3.648% | 3.659% | 3.663% | 3.651% | 3.643% | 3.638% | 3.644% | 3.638% | 3.634% | 3.629% | 3.625% | 3.627% | 3.625% | 3.623% | 3.621% | 3.62% | 3.619% | 3.619% | 3.618% | 3.617% | 3.616% | 3.615% | 3.614% | 3.613%
TAS | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
VIC | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%

## Network representation
Go to Assumptions Summary
Existing network sub-regional topology representation in the Capacity Outlook market model |  |  | Sub-regional representation
Flow path definition | Definition of interconnector or Flow path boundaries
CQ - NQ | Strathmore - Ross 275 kV line (2 circuits) Strathmore - Haughton River 275 kV line (1 circuit) Strathmore - Clare South 132 kV (1 circuit) King Creek - Clare South 132 kV line (1 circuit)
CQ – GG | Bouldercombe – Calliope River 275 kV (1 circuit) Raglan – Larcom Creek 275 kV (1 circuit) Calvale – Wurdong 275 kV (1 circuit) Gin Gin – Calliope River 275 kV (2 circuits) Teebar Creek – Wurdong 275 kV (1 circuit)
CQ – SQ | Woolooga – Teebar Creek 275 kV (1 circuit) Woolooga – Gin Gin 275 kV (2 circuits) Halys – Calvale 275 kV (2 circuits)
NNSW – SQ (Queensland – New South Wales interconnector, or QNI ) | Dumaresq – Bulli Creek 330 kV (2 circuits)
NNSW – SQ (Terranora) | Terranora – Mudgeeraba 110 kV (2 circuits)
CNSW – NNSW | Muswellbrook – Tamworth 330 kV (1 circuit) Liddell – Tamworth 330 kV (1 circuit) Haws Nest Tee – Taree 132 kV line (1 circuit) Stroud – Taree 132 kV line (1 circuit)
SNSW – CNSW | Crookwell – Bannaby 330 kV (1 circuit) Yass – Marulan 330 kV (1 circuit) Collector - Marulan 330 kV (1 circuit) Capital – Kangaroo Valley 330 kV (1 circuit) Yass – Cowra 132 kV (2 circuits)
CNSW – SNW | Wallerawang – Ingleburn 330 kV (1 circuit) Wallerawang – Sydney South 330 kV (1 circuit) Bayswater – Sydney West ­330 kV (1 circuit) Bayswater – Regentville 330 kV (1 circuit) Liddell – Newcastle 330 kV (1 circuit) Liddell – Tomago 330 kV (1 circuit) Bannaby – Sydney West 330 kV (1 circuit) Marulan – Avon 330 kV (1 circuit) Marulan – Dapto 330 kV (1 circuit) Kangaroo Valley – Dapto 330 kV (1 circuit) Stroud – Brandy Hill 132 kV (1 circuit) Stroud – Tomago 132 kV (1 circuit) Hawks Nest tee – Tomago 132 kV (1 circuit) Singleton - Rothbury 132 kV (1 circuit which is normally open)
VIC – SNSW | Murray – Upper Tumut 330 kV (1 circuit) Murray – Lower Tumut 330 kV (1 circuit) Wodonga – Jindera 330 kV (1 circuit) Red Cliffs – Buronga 220 kV line (circuit) Jindabyne - Guthega 132 kV line (1 circuit) Geehi Dam - Guthega 132 kV line (1 circuit)
SNSW – CSA | Buronga - Bundy 330 kV (2 circuits)
VIC – SESA (Heywood) | Heywood – South East 275 kV (2 circuits)
SESA- CSA | Black Range – Tailem Bend 275 kV (2 circuits) Keith – Tailem Bend 132 kV (1 circuit)
VIC – CSA (Murraylink) | Red Cliffs – Monash HVDC cable
VIC-TAS | George Town – Loy Yang HVDC cable
Sub-regional Reference Nodes
NEM Region | ISP Sub-region | Sub-region Reference Node
Queensland | Northern Queensland (NQ) | Chalumbin 275 kV
| Central Queensland (CQ) | Broadsound 275 kV
| Gladstone Grid (GG) | Calliope River 275 kV
| South Queensland (SQ) | South Pine 275 kV
New South Wales | Northern New South Wales (NNSW) | Armidale 330 kV
| Central New South Wales (CNSW) | Wellington 330 kV
| South NSW (SNSW) | Canberra 330 kV
| Sydney, New Castle, Wollongong (SNW) | Sydney West 330 kV
Victoria | Victoria (VIC) | Thomastown 66 kV
South Australia | Central South Australia (SA) | Torrens Island 66 kV
| South East South Australia (CESA) | South East 132 kV
Tasmania | Tasmania (TAS) | George Town 220 kV
Note: The Capacity Outlook Model represents flow path transfer limits (between sub regions) as the transfer between reference nodes
Regional topology representation
The time-sequential model uses detailed transmission constraint equations to represent the capability of the network to flow (intra- and inter-regionally)
Interconnector | Definition of interconnector in NEM operations | Interconnector representation in PLEXOS Capacity outlook model
Queensland-New South Wales (QNI) | Two 330 kV lines between Bulli Creek in Queensland and Dumaresq in New South Wales. | South Pine in Queensland and Sydney West in New South Wales
Queensland-New South Wales (Terranora) | Two 110 kV lines between Mudgeeraba in Queensland and Terranora in New South Wales. | South Pine in Queensland and Sydney West in New South Wales
Victoria-New South Wales (VNI) (Existing network) | The 330 kV line between Murray and Upper Tumut. The 330 kV line between Murray and Lower Tumut. The 330 kV line between Jindera and Wodonga. The 220 kV line between Buronga and Red Cliffs. Jindabyne - Guthega 132 kV line (1 circuit) Geehi Dam - Guthega 132 kV line (1 circuit) | Thomastown in Victoria and Sydney West in New South Wales.
Victoria-New South Wales (VNI) (With Project EnergyConnect) | The 330 kV line between Murray and Upper Tumut. The 330 kV line between Murray and Lower Tumut. The 330 kV line between Jindera and Wodonga. Two 330 kV lines between Buronga and Dinawan The 220 kV line between Buronga and Broken Hill The 220 kV line between Buronga and Balranald Jindabyne - Guthega 132 kV line (1 circuit) Geehi Dam - Guthega 132 kV line (1 circuit) | Thomastown in Victoria and Sydney West in New South Wales.
Victoria to South Australia (Heywood) (Existing network) | Two 275 kV lines between Heywood in Victoria and South East in South Australia. | Thomastown in Victoria and Torrens Island in South Australia.
Victoria to South Australia (with Project EnergyConnect) | Two 275 kV lines between Heywood in Victoria and South East in South Australia. Two 330 kV lines between Buronga and Bundy. | Thomastown in Victoria and Torrens Island in South Australia.
Victoria to South Australia (Murraylink) | HVDC cable between Red Cliffs in Victoria and Monash in South Australia. | Thomastown in Victoria and Torrens Island in South Australia.
Victoria-Tasmania (Basslink) | HVDC cable between Loy Yang in Victoria and George Town in Tasmania. | Thomastown in Victoria and Georgetown in Tasmania.
Regional Reference Nodes
NEM Region | ISP Sub-region | Regional Reference Node
Queensland | South Queensland (SQ) | South Pine 275 kV
New South Walks | Sydney, New Castle, Wollongong (SNW) | Sydney West 330 kV
Victoria | Victoria (VIC) | Thomastown 66 kV
South Australia | Central South Australia (CSA) | Torrens Island 66 kV
Tasmania | Tasmania (TAS) | George Town 220 kV
Note: The Capacity Outlook Model represents Flow path transfer limits as the transfer between reference nodes
Load and generation representation within the sub-regional model
NEM Region / Sub-region | Reference Node | Load and generation representation
North Queensland (NQ) | Chalumbin 275 kV | All load and generation including and north of Ross, Clare South, and Haughton River.
Central Queensland (CQ) | Broadsound 275 kV | All load and generation including and north of Calvale, Gin Gin, Teebar Creek substations, except load and generation in NQ and GG sub-regions.
Gladstone grid (GG) | Calliope River 275 kV | All load and generation at Calliope River, Boyne Island, Larcom Creek and Wurdong substations.
South Queensland (SQ) | South Pine 275 kV | All Queensland load and generation except load and generation in NQ, CQ and GG sub-regions.
Northern New South Wales (NNSW) | Armidale 330 kV | Within NSW, all load and generation including and north of Tamworth substation.
Central New South Wales (CNSW) | Wellington 330 kV | Within NSW, all load and generation including west of Wallerawang and Wollar substations. Load and generation at Bayswater, Liddell and Muswellbrook substations. Load and generation at Bannaby substation.
South NSW (SNSW) | Canberra 330 kV | Within NSW, all load and generation including and south of Gullen Range, Marulan and Kangaroo Valley substations. All load and generation in South West NSW.
Sydney, Newcastle and Wollongong (SNW) | Sydney West 330 kV | All NSW region load and generation except CNSW, SNSW and NNSW sub-region load and generation.
Victoria (VIC) | Thomastown 66 kV | All load and generation within Victoria
South Australia (CSA) | Torrens Island 66 kV | All load and generation within South Australia except in SESA sub-region.
South East South Australia (SESA) | South East 132 kV | All load and generation south of Tailem Bend within South Australia.
Tasmania (TAS) | George Town 220 kV | All load and generation within Tasmania

## Network losses
Go to Assumptions Summary
Network loss equations for Inter-Regional Losses
Losses due to interconnector flow are assigned asymmetrically to regions either side of the interconnector1
Existing Flow Paths
This table describes the loss equations and proportioning factors for the existing flow paths. These have been calculated according to section 2.3.6 of the ISP Methodology.
Flow Path | Interconnector/Flow path Name | Interconnector | From region/sub-region | Loss Equation | MLF Equation | From region loss proportion | To region loss proportion
NNSW – SQ (“QNI”) | Queensland - New South Wales (QNI) | NSW1-QLD1 | NSW1 | = (-0.1464 + 1.4428e-05*Qd + 9.7051e-06*Nd)*NQt + 9.4250e-05*NQt^2 | = 0.8536 + 1.8850e-04*NQt + 1.4428e-05*Qd + 9.7051e-06*Nd | 0.62 | 0.38
NNSW – SQ (“Terranora”) | Queensland - New South Wales (Terranora) | N-Q-MNSP1 | NSW1 | Losses between Mullumbimby 132 kV and Terranora 132 kV: = (-0.0013 * Flow + 2.7372 * 10-4 * Flow²) | = 1.0538 + 3.0511E-03*Flow | 0.5959 | 0.4041
VIC – NSW | Victoria - New South Wales (VNI) | VIC1-NSW1 | VIC1 | = ( 0.0793 + -8.7111E-06*Vd + 8.6242E-06*Nd + -4.9347E-05*Sd)*VNt + 8.3797E-05*(VNt)2 | = 1.0793 + 1.6759e-04*VNt + -8.7111e-06*Vd + 8.6242e-06*Nd + -4.9347e-05*Sd | 0.54 | 0.46
VIC – SESA ("Heywood") | Victoria - South Australia (Heywood) | V-SA | VIC1 | = (0.0166 + -1.2753e-06*Vd + -1.5712e-06*Sd)*VSAt + 1.7132e-04*VSAt^2 | = 1.0166 + 3.4264e-04*VSAt + -1.2753e-06*Vd + -1.5712e-06*Sd | 0.68 | 0.32
VIC – CSA ("Murraylink") | Victoria - South Australia (Murraylink) | V-S-MNSP1 | VIC1 | Losses between Red Cliffs 220 kV and Monash 132 kV = (0.0039 * Flow + 2.8177 * 10-4 * Flow²) | = 0.9449 + 2.0094E-03*Flow | 0.6593 | 0.3407
TAS – VIC | Tasmania - Victoria (Basslink) | T-V-MNSP1 | TAS1 | P(send) = P(receive) + [ (-3.92x10-3) * P(receive) + (1.0393x10-4) * P(receive)2 + 4] | George Town 220 kV MLF referred to Tasmania RRN = 1.0000 Basslink (Loy Yang Power Station [PS] Switchyard) 500 kV MLF referred to Victorian RRN is 0.9826 when exporting power to Tasmania and 0.9755 when importing power from Tasmania | 0.5 | 0.5
CQ-NQ | Central - North Queensland | - | CQ | =0.0088*(CQ-NQt) + 1.0052e-04*(CQ-NQt)^2 | =1.0088 + 2.0104e-04*(CQ-NQt) | 0.43 | 0.57
SQ – CQ | South - Central Queensland | - | SQ | = -0.0418*(SQ-CQt) + 5.0411e-05*(SQ-CQt)^2 | = 0.9582 + 1.0082e-04*(SQ-CQt) | 0.43 | 0.57
CQ-GG |  |  | These flow paths do not cross regional boundaries and have been assigned no loss equation and no loss factors.
CNSW – NNSW | - | -
CNSW ­– SNW | - | -
SNSW – CNSW | - | -
SESA-CSA | - | -
Notes:
1. Loss factors for existing interconnectors were sourced from Marginal Loss Factors: Financial Year 2023-24. Refer to the AEMO website for the latest Marginal Loss Factors. |  | https://aemo.com.au/-/media/files/electricity/nem/security_and_reliability/loss_factors_and_regional_boundaries/2023-24/marginal-loss-factors-for-the-2023-24-financia-year-pdf.pdf?la=en
The following notation is used in equations: Qd = Queensland demand Vd = Victorian demand Nd = New South Wales demand Sd = South Australia demand NQd = North Queensland demand CQd = Central Queensland demand NQt = transfer from New South Wales to Queensland VNt = transfer from Victoria to New South Wales VSAt = transfer from Victoria to South Australia CQ-NQt = transfer from Central QLD to Northern QLD P(receive) = Power in MW measured at the receiving end P(send) = Power in MW measured at the sending end
Committed/Anticipated Projects
This table describes the loss equations and proportioning factors that are applied to the flow paths following the completion of an anticipated project. These have been calculated according to section 2.3.6 of the ISP Methodology.
Flow Path | Interconnector Name | Interconnector | From region | Loss Equation | MLF Equation | From region loss proportion | To region loss proportion
Western Victoria Transmission Network Project | Victoria - New South Wales (VNI) | VIC1-NSW1 | VIC1 | = (0.0592 + -8.2284e-06*Vd + 4.6665e-06*Nd + -4.6779e-05*Sd)*VNt + 8.5659e-05*VNt^2 | = 1.0592 + 1.7132e-04*VNt + -8.2284e-06*Vd + 4.6665e-06*Nd + -4.6779e-05*Sd | 0.3413 | 0.6587
Project EnergyConnect (Note 1) | Victoria - New South Wales (VNI) | VIC1-NSW1 | VIC1 | = (0.0899 + -9.8738e-06*Vd + 9.7753e-06*Nd + -5.5933e-05*Sd)*VNt + 9.4981e-05*VNt^2 | = 1.0899 + 1.8996e-04*VNt + -9.8738e-06*Vd + 9.7753e-06*Nd + -5.5933e-05*Sd | 0.61 | 0.39
Project EnergyConnect (Note 1) | Victoria - South Australia (Heywood) | V-SA | VIC1 | =(0.0092 + -7.0871e-07*Vd + -8.7315e-07*Sd)*VSAt + 9.5206e-05*VSAt^2 | = 1.0092 + 1.9041e-04*VSAt + -7.0871e-07*Vd + -8.7315e-07*Sd | 0.9 | 0.1
Project EnergyConnect (Note 2) | Project EnergyConnect | SA-NSW | SA1 | =(-0.1078 - 8.825e-07*Nd + 2.192e-06*Vd + 3.254e-05*Sd) * SNt + 1.277e-04*SNt^2 | =0.8922 + 2.5540e-04*SNt + -8.8250e-07*Nd + 2.1920e-06*Vd + 3.2540e-05*Sd | 0.46 | 0.54
Notes:
1) These equations apply if Project EnergyConnect is modelled as an expanded VIC-SA interconnector, with a boundary shift at Buronga.
2) This equation applies if Project EnergyConnect is modelled as a SA-NSW interconnector. AEMO intends to model Project EnergyConnect in this way for the capacity outlook model. The additional term (SNt) refers to transfer from South Australia to New South Wales.
Development Options
This table describes the loss equations and proportioning factors that are applied to the flow paths for the various candidate development options. These have been calculated according to section 2.3.6 of the ISP Methodology. (Source 2023 Transmission Expansion Options Report).
Development Option | Included Option | Interconnector | From region | Loss Equation | MLF Equation | From region loss proportion | To region loss proportion
CQ-NQ Option 1 | - | CQ-NQ | CQ | = 0.0075*(CQ-NQt) + 8.5283e-05*(CQ-NQt)^2 | = 1.0075 + 1.7057e-04*(CQ-NQt) | 0.42 | 0.58
CQ-NQ Option 2 | - | CQ-NQ | CQ | =0.0065*(CQ-NQt) + 7.4281e-05*(CQ-NQt)^2 | = 1.0065 + 1.4856e-04*(CQ-NQt) | 0.41 | 0.59
SQ-CQ Option 1 | - | SQ-CQ | SQ | = -0.0350*(SQ-CQt) + 4.2253e-05*(SQ-CQt)^2 | = 0.9650 + 8.4506e-05*(SQ-CQt) | 0.49 | 0.51
SQ-CQ Option 2 | - | SQ-CQ | SQ | =-0.0397*(SQ-CQt) + 4.7858e-05*(SQ-CQt)^2 | = 0.9603 + 9.5717e-05*(SQ-CQt) | 0.49 | 0.51
| SQ-CQ Option 1 | SQ-CQ | SQ | = -0.0346*(SQ-CQt) + 4.1697e-05*(SQ-CQt)^2 | = 0.9654 + 8.3395e-05*(SQ-CQt) | 0.54 | 0.46
| SQ-CQ Option 4 | SQ-CQ | SQ | = -0.0332*(SQ-CQt) + 3.9985e-05*(SQ-CQt)^2 | =0.9668 + 7.9970e-05*(SQ-CQt) | 0.57 | 0.43
| SQ-CQ Option 5 | SQ-CQ | SQ | = -0.0264*(SQ-CQt) + 3.1792e-05*(SQ-CQt)^2 | = 0.9736 + 6.3583e-05*(SQ-CQt) | 0.61 | 0.39
SQ-CQ Option 4(HVDC) | - | SQ-CQ | SQ | =-0.0335*(SQ-CQt) + 4.0422e-05*(SQ-CQt)^2 | =0.9665 + 8.0844e-05*(SQ-CQt) | 0.53 | 0.47
SQ-CQ Option 5 | - | SQ-CQ | SQ | =-0.0266*(SQ-CQt) + 3.2021e-05*(SQ-CQt)^2 | = 0.9734 + 6.4042e-05*(SQ-CQt) | 0.6 | 0.4
CQ-GG Option 1
NNSW-SQ Option 4 | CNSW-NNSW Option 1 | NSW1-QLD1 | NSW1 | = (-0.0810 + 7.9797e-06*Qd + 5.3676e-06*Nd)*NQt + 5.2127e-05*NQt^2 | = 0.9190 + 1.0425e-04*NQt + 7.9797e-06*Qd + 5.3676e-06*Nd | 0.53 | 0.47
| CNSW-NNSW Option 1 (NE) | NSW1-QLD1 | NSW1 | =(-0.0813 + 8.0106e-06*Qd + 5.3884e-06*Nd)*NQt + 5.2329e-05*NQt^2 | 0.9187 + 1.0466e-04*NQt + 8.0106e-06*Qd + 5.3884e-06*Nd | 0.53 | 0.47
| CNSW-NNSW Option 2 | NSW1-QLD1 | NSW1 | = (-0.0802 + 7.9047e-06*Qd + 5.3171e-06*Nd)*NQt + 5.1637e-05*NQt^2 | =0.9198 + 1.0327e-04*NQt + 7.9047e-06*Qd + 5.3171e-06*Nd | 0.53 | 0.47
| CNSW-NNSW Option 3 | NSW1-QLD1 | NSW1 | = (-0.0731 + 7.2012e-06*Qd + 4.8439e-06*Nd)*NQt + 4.7041e-05*NQt^2 | = 0.9269 + 9.4082e-05*NQt + 7.2012e-06*Qd + 4.8439e-06*Nd | 0.53 | 0.47
| CNSW-NNSW Option 4 (HVDC) | NSW1-QLD1 | NSW1 | =(-0.0827 + 8.1503e-06*Qd + 5.4823e-06*Nd)*NQt + 5.3241e-05*NQt^2 | =0.9173 + 1.0648e-04*NQt + 8.1503e-06*Qd + 5.4823e-06*Nd | 0.54 | 0.46
NNSW-SQ Option 1 | CNSW-NNSW Option 1 | NSW1-QLD1 | NSW1 | = (-0.0958 + 9.4431e-06*Qd + 6.3520e-06*Nd)*NQt + 6.1686e-05*NQt^2 | = 0.9042 + 1.2337e-04*NQt + 9.4431e-06*Qd + 6.3520e-06*Nd | 0.59 | 0.41
| CNSW-NNSW Option 1 (NE) | NSW1-QLD1 | NSW1 | = (-0.0964 + 9.5051e-06*Qd + 6.3937e-06*Nd)*NQt + 6.2091e-05*NQt^2 | = 0.9036 + 1.2418e-04*NQt + 9.5051e-06*Qd + 6.3937e-06*Nd | 0.59 | 0.41
| CNSW-NNSW Option 2 | NSW1-QLD1 | NSW1 | = (-0.0950 + 9.3594e-06*Qd + 6.2956e-06*Nd)*NQt + 6.1139e-05*NQt^2 | = 0.9050 + 1.2228e-04*NQt + 9.3594e-06*Qd + 6.2956e-06*Nd | 0.59 | 0.41
| CNSW-NNSW Option 3 | NSW1-QLD1 | NSW1 | = (-0.0844 + 8.3144e-06*Qd + 5.5928e-06*Nd)*NQt + 5.4313e-05*NQt^2 | = 0.9156 + 1.0863e-04*NQt + 8.3144e-06*Qd + 5.5928e-06*Nd | 0.58 | 0.42
| CNSW-NNSW Option 4 (HVDC) | NSW1-QLD1 | NSW1 | = (-0.0888 + 8.7520e-06*Qd + 5.8871e-06*Nd)*NQt + 5.7172e-05*NQt^2 | = 0.9112 + 1.1434e-04*NQt + 8.7520e-06*Qd + 5.8871e-06*Nd | 0.58 | 0.42
NNSW-SQ Option 2 | CNSW-NNSW Option 1 | NSW1-QLD1 | NSW1 | = (-0.0958 + 9.4405e-06*Qd + 6.3502e-06*Nd)*NQt + 6.1669e-05*NQt^2 | = 0.9042 + 1.2334e-04*NQt + 9.4405e-06*Qd + 6.3502e-06*Nd | 0.59 | 0.41
| CNSW-NNSW Option 1 (NE) | NSW1-QLD1 | NSW1 | = (-0.0964 + 9.5041e-06*Qd + 6.3930e-06*Nd)*NQt + 6.2085e-05*NQt^2 | = 0.9036 + 1.2417e-04*NQt + 9.5041e-06*Qd + 6.3930e-06*Nd | 0.59 | 0.41
| CNSW-NNSW Option 2 | NSW1-QLD1 | NSW1 | = (-0.0964 + 9.5041e-06*Qd + 6.3930e-06*Nd)*NQt + 6.2085e-05*NQt^2 | = 0.9036 + 1.2417e-04*NQt + 9.5041e-06*Qd + 6.3930e-06*Nd | 0.58 | 0.42
| CNSW-NNSW Option 3 | NSW1-QLD1 | NSW1 | = (-0.0844 + 8.3138e-06*Qd + 5.5923e-06*Nd)*NQt + 5.4309e-05*NQt^2 | = 0.9156 + 1.0862e-04*NQt + 8.3138e-06*Qd + 5.5923e-06*Nd | 0.58 | 0.42
| CNSW-NNSW Option 4 (HVDC) | NSW1-QLD1 | NSW1 | = (-0.0891 + 8.7807e-06*Qd + 5.9064e-06*Nd)*NQt + 5.7359e-05*NQt^2 | = 0.9109 + 1.1472e-04*NQt + 8.7807e-06*Qd + 5.9064e-06*Nd | 0.57 | 0.43
NNSW-SQ Option 5 | - | NSW1-QLD1 | NSW1 | = (-0.0450 + 4.4305e-06*Qd + 2.9802e-06*Nd)*NQt + 2.8942e-05*NQt^2 | = 0.9550 + 5.7883e-05*NQt + 4.4305e-06*Qd + 2.9802e-06*Nd | 0.43 | 0.57
CNSW-NNSW Option 2 | - | NSW1-QLD1 | NSW1 | = (-0.1163 + 1.1457e-05*Qd + 7.7065e-06*Nd)*NQt + 7.4841e-05*NQt^2 | = 0.8837 + 1.4968e-04*NQt + 1.1457e-05*Qd + 7.7065e-06*Nd | 0.6 | 0.4
CNSW-NNSW Option 3 | - | NSW1-QLD1 | NSW1 | = (-0.0995 + 9.8030e-06*Qd + 6.5940e-06*Nd)*NQt + 6.4037e-05*NQt^2 | = 0.9005 + 1.2807e-04*NQt + 9.8030e-06*Qd + 6.5940e-06*Nd | 0.58 | 0.42
CNSW-SNW Option 1 (Actionable) | - | NSW1-QLD1 | NSW1 | = (-0.1429 + 1.4088e-05*Qd + 9.4761e-06*Nd)*NQt + 9.2027e-05*NQt^2 | = 0.8571 + 1.8405e-04*NQt + 1.4088e-05*Qd + 9.4761e-06*Nd | 0.62 | 0.38
| CNSW-NNSW Option 1 | NSW1-QLD1 | NSW1 | = (-0.1176 + 1.1590e-05*Qd + 7.7963e-06*Nd)*NQt + 7.5713e-05*NQt^2 | = 0.8824 + 1.5143e-04*NQt + 1.1590e-05*Qd + 7.7963e-06*Nd | 0.6 | 0.4
SA-NSW Option 1 (Project EnergyConnect) | - | VIC1-NSW1 | VIC1 | = (0.0899 + -9.8738e-06*Vd + 9.7753e-06*Nd + -5.5933e-05*Sd)*VNt + 9.4981e-05*VNt^2 | = '= 1.0899 + 1.8996e-04*VNt + -9.8738e-06*Vd + 9.7753e-06*Nd + -5.5933e-05*Sd | 0.61 | 0.39
CNSW-SNW Option 2 | - | VIC1-NSW1 | VIC1 | = (0.0891 + -9.7829e-06*Vd + 9.6853e-06*Nd + -5.5419e-05*Sd)*VNt + 9.4107e-05*VNt^2 | = 1.0891 + 1.8821e-04*VNt + -9.7829e-06*Vd + 9.6853e-06*Nd + -5.5419e-05*Sd | 0.34 | 0.66
| SNSW-CNSW Option 1 (HumeLink) | VIC1-NSW1 | VIC1 | = (0.0779 + -8.5528e-06*Vd + 8.4675e-06*Nd + -4.8450e-05*Sd)*VNt + 8.2274e-05*VNt^2 | = 1.0779 + 1.6455e-04*VNt + -8.5528e-06*Vd + 8.4675e-06*Nd + -4.8450e-05*Sd | 0.88 | 0.12
| SNSW-CNSW Option 1 (HumeLink) and VNI West | VIC1-NSW1 | VIC1 | = (0.0503 + -5.5242e-06*Vd + 5.4691e-06*Nd + -3.1294e-05*Sd)*VNt + 5.3140e-05*VNt^2 | = 1.0503 + 1.0628e-04*VNt + -5.5242e-06*Vd + 5.4691e-06*Nd + -3.1294e-05*Sd | 0.89 | 0.11
CNSW-SNW Option 2b | - | VIC1-NSW1 | VIC1 | = (0.0894 + -9.8209e-06*Vd + 9.7230e-06*Nd + -5.5634e-05*Sd)*VNt + 9.4473e-05*VNt^2 | = 1.0894 + 1.8895e-04*VNt + -9.8209e-06*Vd + 9.7230e-06*Nd + -5.5634e-05*Sd | 0.63 | 0.37
| SNSW-CNSW Option 1 (HumeLink) | VIC1-NSW1 | VIC1 | = (0.0786 + -8.6299e-06*Vd + 8.5438e-06*Nd + -4.8887e-05*Sd)*VNt + 8.3015e-05*VNt^2 | = 1.0786 + 1.6603e-04*VNt + -8.6299e-06*Vd + 8.5438e-06*Nd + -4.8887e-05*Sd | 0.75 | 0.25
| SNSW-CNSW Option 1 (HumeLink) and VNI West | VIC1-NSW1 | VIC1 | = (0.0511 + -5.6120e-06*Vd + 5.5560e-06*Nd + -3.1791e-05*Sd)*VNt + 5.3985e-05*VNt^2 | = 1.0511 + 1.0797e-04*VNt + -5.6120e-06*Vd + 5.5560e-06*Nd + -3.1791e-05*Sd | 0.73 | 0.27
SNSW-CNSW Option 1 (HumeLink)-(Actionable) | - | VIC1-NSW1 | VIC1 | = (0.0788 + -8.6590e-06*Vd + 8.5726e-06*Nd + -4.9052e-05*Sd)*VNt + 8.3296e-05*VNt^2 | = 1.0788 + 1.6659e-04*VNt + -8.6590e-06*Vd + 8.5726e-06*Nd + -4.9052e-05*Sd | 0.71 | 0.29
SNSW-CNSW Option 2 | - | VIC1-NSW1 | VIC1 | = (0.0772 + -8.4845e-06*Vd + 8.3999e-06*Nd + -4.8063e-05*Sd)*VNt + 8.1617e-05*VNt^2 | = 1.0772 + 1.6323e-04*VNt + -8.4845e-06*Vd + 8.3999e-06*Nd + -4.8063e-05*Sd | 0.7 | 0.3
| VNI West | VIC1-NSW1 | VIC1 | = (0.0499 + -5.4846e-06*Vd + 5.4299e-06*Nd + -3.1070e-05*Sd)*VNt + 5.2760e-05*VNt^2 | = 1.0499 + 1.0552e-04*VNt + -5.4846e-06*Vd + 5.4299e-06*Nd + -3.1070e-05*Sd | 0.65 | 0.35
SNSW-CNSW Option 3 | - | VIC1-NSW1 | VIC1 | = (0.0474 + -5.2058e-06*Vd + 5.1538e-06*Nd + -2.9490e-05*Sd)*VNt + 5.0077e-05*VNt^2 | = 1.0474 + 1.0015e-04*VNt + -5.2058e-06*Vd + 5.1538e-06*Nd + -2.9490e-05*Sd | 0.67 | 0.33
SNSW-CNSW Option 4 | - | VIC1-NSW1 | VIC1 | = (0.0487 + -5.3459e-06*Vd + 5.2926e-06*Nd + -3.0284e-05*Sd)*VNt + 5.1425e-05*VNt^2 | = 1.0487 + 1.0285e-04*VNt + -5.3459e-06*Vd + 5.2926e-06*Nd + -3.0284e-05*Sd | 0.67 | 0.33
CNSW-SNW H-Dapto | - | VIC1-NSW1 | VIC1 | = (0.0893 + -9.8088e-06*Vd + 9.7109e-06*Nd + -5.5565e-05*Sd)*VNt + 9.4356e-05*VNt^2 | = 1.0893 + 1.8871e-04*VNt + -9.8088e-06*Vd + 9.7109e-06*Nd + -5.5565e-05*Sd | 0.62 | 0.38
| SNSW-CNSW Option 1 (HumeLink) | VIC1-NSW1 | VIC1 | = (0.0784 + -8.6070e-06*Vd + 8.5211e-06*Nd + -4.8757e-05*Sd)*VNt + 8.2796e-05*VNt^2 | = 1.0784 + 1.6559e-04*VNt + -8.6070e-06*Vd + 8.5211e-06*Nd + -4.8757e-05*Sd | 0.77 | 0.23
| SNSW-CNSW Option 1 (HumeLink) and VNI West | VIC1-NSW1 | VIC1 | = (0.0508 + -5.5805e-06*Vd + 5.5248e-06*Nd + -3.1613e-05*Sd)*VNt + 5.3682e-05*VNt^2 | = 1.0508 + 1.0736e-04*VNt + -5.5805e-06*Vd + 5.5248e-06*Nd + -3.1613e-05*Sd | 0.75 | 0.25
VIC-SNSW Option 1(VNI West)(Actionable) | - | VIC1-NSW1 | VIC1 | = (0.0514 + -5.6417e-06*Vd + 5.5854e-06*Nd + -3.1959e-05*Sd)*VNt + 5.4271e-05*VNt^2 | = 1.0514 + 1.0854e-04*VNt + -5.6417e-06*Vd + 5.5854e-06*Nd + -3.1959e-05*Sd | 0.67 | 0.33
TAS-VIC Option 1 (Marinus Link Stage 1)(Actionable) | - | T-V-MNSP1 | TAS | = 9 + 0.01 * Flow + 2.85645E-05*Flow^2 | = 1.01 + 0.000057129 * Flow | 0.5 | 0.5
TAS-VIC Option 2 (Marinus Link Stage 2)(Actionable) | - | T-V-MNSP1 | TAS | = 18 + 0.01 * Flow + 1.42822E-05*Flow^2 | = 1.01 + 0.000028564 * Flow | 0.5 | 0.5
SA-NSW Option 1 (Project EnergyConnect)(Actionable) | - | SA-NSW | SA1 | = (-0.1078 + -8.8250e-07*Nd + 2.1920e-06*Vd + 3.2540e-05*Sd)*SNt + 1.2770e-04*SNt^2 | = 0.8922 + 2.5540e-04*SNt + -8.8250e-07*Nd + 2.1920e-06*Vd + 3.2540e-05*Sd | 0.46 | 0.54
CNSW-SNW Option 2 (Southern Loop) | - | SA-NSW | SA1 | = (-0.1080 + -8.8451e-07*Nd + 2.1970e-06*Vd + 3.2614e-05*Sd)*SNt + 1.2799e-04*SNt^2 | = 0.8920 + 2.5598e-04*SNt + -8.8451e-07*Nd + 2.1970e-06*Vd + 3.2614e-05*Sd | 0.46 | 0.54
| SNSW-CNSW Option 1 (HumeLink) | SA-NSW | SA1 | = (-0.0892 + -7.3025e-07*Nd + 1.8138e-06*Vd + 2.6926e-05*Sd)*SNt + 1.0567e-04*SNt^2 | = 0.9108 + 2.1134e-04*SNt + -7.3025e-07*Nd + 1.8138e-06*Vd + 2.6926e-05*Sd | 0.51 | 0.49
CNSW-SNW Option 2b | - | SA-NSW | SA1 | = (-0.1079 + -8.8309e-07*Nd + 2.1935e-06*Vd + 3.2562e-05*Sd)*SNt + 1.2779e-04*SNt^2 | = 0.8921 + 2.5557e-04*SNt + -8.8309e-07*Nd + 2.1935e-06*Vd + 3.2562e-05*Sd | 0.46 | 0.54
| SNSW-CNSW Option 1 (HumeLink) | SA-NSW | SA1 | = (-0.0895 + -7.3299e-07*Nd + 1.8206e-06*Vd + 2.7027e-05*Sd)*SNt + 1.0606e-04*SNt^2 | = 0.9105 + 2.1213e-04*SNt + -7.3299e-07*Nd + 1.8206e-06*Vd + 2.7027e-05*Sd | 0.51 | 0.49
SNSW-CNSW Option 3 | - | SA-NSW | SA1 | = (-0.0892 + -7.2996e-07*Nd + 1.8131e-06*Vd + 2.6915e-05*Sd)*SNt + 1.0563e-04*SNt^2 | = 0.9108 + 2.1125e-04*SNt + -7.2996e-07*Nd + 1.8131e-06*Vd + 2.6915e-05*Sd | 0.51 | 0.49
SNSW-CNSW H-Dapto | - | SA-NSW | SA1 | = (-0.0894 + -7.3162e-07*Nd + 1.8172e-06*Vd + 2.6977e-05*Sd)*SNt + 1.0587e-04*SNt^2 | = 0.9106 + 2.1174e-04*SNt + -7.3162e-07*Nd + 1.8172e-06*Vd + 2.6977e-05*Sd | 0.51 | 0.49
SESA-CSA Option 1 | - | SA-NSW | SA1 | = (-0.1010 + -8.2701e-07*Nd + 2.0542e-06*Vd + 3.0494e-05*Sd)*SNt + 1.1967e-04*SNt^2 | = 0.8990 + 2.3934e-04*SNt + -8.2701e-07*Nd + 2.0542e-06*Vd + 3.0494e-05*Sd | 0.45 | 0.55
SNSW-CNSW Option 1 (HumeLink) | - | SA-NSW | SA1 | = (-0.0896 + -7.3376e-07*Nd + 1.8225e-06*Vd + 2.7056e-05*Sd)*SNt + 1.0618e-04*SNt^2 | = 0.9104 + 2.1235e-04*SNt + -7.3376e-07*Nd + 1.8225e-06*Vd + 2.7056e-05*Sd | 0.51 | 0.49
SNSW-CNSW Option 3 | - | SA-NSW | SA1 | = (-0.0782 + -6.4018e-07*Nd + 1.5901e-06*Vd + 2.3605e-05*Sd)*SNt + 9.2635e-05*SNt^2 | = 0.9218 + 1.8527e-04*SNt + -6.4018e-07*Nd + 1.5901e-06*Vd + 2.3605e-05*Sd | 0.54 | 0.46
SNSW-CNSW Option 4 | - | SA-NSW | SA1 | = (-0.0814 + -6.6646e-07*Nd + 1.6554e-06*Vd + 2.4574e-05*Sd)*SNt + 9.6438e-05*SNt^2 | = 0.9186 + 1.9288e-04*SNt + -6.6646e-07*Nd + 1.6554e-06*Vd + 2.4574e-05*Sd | 0.54 | 0.46
SA-NSW Option 1 (Project EnergyConnect | - | V-SA | VIC1 | = (0.0092 + -7.0871e-07*Vd + -8.7315e-07*Sd)*VSAt + 9.5206e-05*VSAt^2 | = 1.0092 + 1.9041e-04*VSAt + -7.0871e-07*Vd + -8.7315e-07*Sd | 0.9 | 0.1
VIC-SESA Option 1 | Without PEC | V-SA | VIC1 | = (0.0165 + -1.2643e-06*Vd + -1.5577e-06*Sd)*VSAt + 1.6984e-04*VSAt^2 | = 1.0165 + 3.3969e-04*VSAt + -1.2643e-06*Vd + -1.5577e-06*Sd | 0.68 | 0.32
| - | V-SA | VIC1 | = (0.0092 + -7.1045e-07*Vd + -8.7529e-07*Sd)*VSAt + 9.5440e-05*VSAt^2 | = 1.0092 + 1.9088e-04*VSAt + -7.1045e-07*Vd + -8.7529e-07*Sd | 0.9 | 0.1
| Dummy Generator | V-SA | VIC1 | = (0.0073 + -5.6193e-07*Vd + -6.9232e-07*Sd)*VSAt + 7.5488e-05*VSAt^2 | = 1.0073 + 1.5098e-04*VSAt + -5.6193e-07*Vd + -6.9232e-07*Sd | 0.64 | 0.36
VIC-SESA Option 2 | Without PEC | V-SA | VIC1 | = (0.0160 + -1.2321e-06*Vd + -1.5180e-06*Sd)*VSA + 1.6552e-04*VSAt^2 | = 1.0160 + 3.3104e-04*VSAt + -1.2321e-06*Vd + -1.5180e-06*Sd | 0.68 | 0.32
| - | V-SA | VIC1 | = (0.0091 + -7.0141e-07*Vd + -8.6416e-07*Sd)*VSAt + 9.4226e-05*VSAt^2 | = 1.0091 + 1.8845e-04*VSAt + -7.0141e-07*Vd + -8.6416e-07*Sd | 0.9 | 0.1
| Dummy Generator | V-SA | VIC1 | = (0.0071 + -5.4837e-07*Vd + -6.7561e-07*Sd)*VSAt + 7.3667e-05*VSAt^2 | = 1.0071 + 1.4733e-04*VSAt + -5.4837e-07*Vd + -6.7561e-07*Sd | 0.6 | 0.4
SESA-CSA Option 1 (Heywood) | With PEC & VIC-SESA Option 2(500kV) | V-SA | VIC1 | (0.0091 + -7.0141e-07*Vd + -8.6416e-07*Sd)*VSAt + 9.4226e-05*VSAt^2 | = 1.0091 + 1.8845e-04*VSAt + -7.0141e-07*Vd + -8.6416e-07*Sd | 0.902 | 0.098
Notes:
1. For CQ-NQ option 2 , Karana Downs Option 2, SQ-CQ Option 5 & CQ-GG Option 1 are considered already built
2. All NSW1-QLD1 upgrade loss equation calculations consider QNI Minor, Central-West Orana and CNSW-SNW Option 1 (Northern loop) to be already built.
3. In NSW1-QLD1 (NNSW-SQ Option5) additional projects considered- CQ-GG Option 1, SQ-CQ Optipn 5, CNSW-NNSW Option 1, CNSW-NNSW Option 2 to be already built.The REZ augmentation of N2 Option 1 has also been considered to be built for NSW1-QLD1 when considering option CNSW-NNSW Option 1 (NE)
4. All VIC1-NSW1 upgrade loss equation calculations consider VNI Minor, Project EnergyConnect, Western Victoria Transmission Network Project and SNSW-CNSW Option 1 (HumeLink) to be already built.
5. Loss equation calculations with VIC-SNSW Options 3, 4, 6 & 7 assume VIC-SNSW Option 2 (VNI West Kerang) is built.
6. To represent an interconnector upgrade for QNI, two flow path upgrades are required in combination. I.e. An augmentation to NNSW-SQ and an augmentation to CNSW-NNSW. This could be any option 1-4 from NNSW-SQ and any option 1-5 for CNSW-NNSW. The combinations and corresponding loss equations will be evaluated in following iterations of this input and assumption workbook.
7. HumeLink is assumed to be in service for all VIC1-NSW1 upgrades, except where stated.
8. All SA-NSW upgrade loss equation calculations consider VNI Minor, Project EnergyConnect, Western Victoria Transmission Network Project and SNSW-CNSW Option 1 (HumeLink) to be already built.
9. All SA-NSW upgrade loss equation calculations include the same build assumptions as the VIC-NSW loss equation.
10. SA-NSW upgrade loss equations are only applicable if Project EnergyConnect is modelled as a SA-NSW interconnector. AEMO intends to model Project EnergyConnect in this way for the capacity outlook model.

## Network Capability
Go to Assumptions Summary
Flow Path Transfer Capability (MW)
This table describes the transfer capability along the flow paths for Capacity Outlook Model under different system conditions. Please note that some flow paths are the same as the regional model. Refer to the section 2.3.1 of the ISP Methodology for more information.
Transfer capability represent the transmission network from 1 July 2023. All committed projects with full service from 1 July 2023 are taken into account in transfer limits.
Flow paths (Forward power flow direction) | Forward direction capability approximation (MW) - Notes 1,2&3 |  |  | Reverse direction capability approximation (MW) - Notes 1,2&3 |  |  | Dominant constraints
| Peak demand | Summer Typical | Winter Reference | Peak demand | Summer Typical | Winter Reference | Forward direction | Reverse direction
CQ - NQ (Note 10) | 1200 | 1200 | 1400 | 1200 | 1200 | 1400 | Voltage stability in NQ for the loss of NQ or CQ transmission network elements. | Thermal capability of Strathmore to Ross 275 kV line for the loss of the Haughton River to Strathmore 275 kV line.
CQ ­– GG (Note 4) | 700 | 700 | 1050 | 750 | 750 | 1100 | Thermal overload of Calvale to Wurdong 275 kV line | Thermal capacity of Calliope River-Woolooga for the loss of one of the parallel lines
SQ – CQ | 1100 | 1100 | 1100 | 2100 | 2100 | 2100 | Thermal capability of Blackwall -South Pine 275 kV line. | Transient stability or voltage stability for a contingency of the Calvale-Halys 275 kV circuit.
NNSW – SQ (Northern part of "QNI") | 685 (with QNI Minor) | 745 (with QNI Minor) | 745 (with QNI Minor) | 1,205 (with QNI minor) (Note 5) | 1,165 (with QNI minor) (Note 5 | 1,170 (with QNI minor) (Note 5) | Voltage stability or transient stability for the loss of Kogan Creek generator. | Thermal capability of Armidale-Sapphire and Armidale-Dumaresq 330 kV circuits and dispatch of generation at Sapphire.
NNSW – SQ (“Terranora”) | 0 | 50 | 50 | 130 | 150 | 200 | Thermal capability of Lismore 132 kV lines (9U9). | Thermal capability of Mudgeeraba 275/110 kV transformers
CNSW – NNSW (Southern part of "QNI") | 910 (with QNI minor) | 910 (with QNI minor) | 910 (with QNI minor) | 930 (with QN Minor) | 930 (with QN Minor) | 1,025 (with QNI Minor) | Voltage stability for an outage of Kogan Creek generator. | Thermal capability of Tamworth-Armidale 330 kV circuits.
CNSW ­– SNW Northern limit | 4,490 (Note 6)(Note 7) | 4,490 (Note 6)(Note 7) | 4,730 (Note 6)(Note 7) | 4,490 (Note 7) | 4,490 (Note 7) | 4,730 (Note 7) | Maximum transfer capability is limited by several 330 kV lines and the most limiting elements are Liddell-Newcastle and Liddell-Tomago 330 kV lines. | -
CNSW ­– SNW Southern limit | 2,540 (Note 6)(Note 7) | 2,540 (Note 6)(Note 7) | 2,720 (Note 6)(Note 7) | 2,540 (Note 7) | 2,540 (Note 7) | 2,720 (Note 7) | Maximum transfer capability is limited by several 330 kV lines and the most limiting element is Bannaby-Sydney West 330 kV line. | -
SNSW – CNSW (Northern part of "VNI") | 2,700 (Snowy 2.0 generation or pump load <= 660- Note 11) | 2,700 (Snowy 2.0 generation or pump load <= 660 - Note 11) | 2,950 (Snowy 2.0 generation or pump load <= 660 - Note 11) | 2,320 | 2,320 | 2,590 | Thermal capability of Crookwell-Bannaby, Collector-Marula or Yass-Marulan 330 kV lines. Prior to HumeLink service, Snowy 2.0 generation or pump load is limited by a transient stability limit. | Thermal capability of Yass-Canberra, Collector -Yass or Gullen Range-Yass 330 kV line.
VIC – SNSW (Southern part of "VNI") | 870 (with VNI minor) | 1,000 (with VNI minor) | 1,000 (with VNI minor) | 400 (with VNI SIPS) - Note 8 (Snowy 2.0 generation or pump load <= 660 - Note 11) | 400 (Snowy 2.0 generation or pump load <= 660 - Note 11) | 400 (Snowy 2.0 generation or pump load <= 660 - Note 11) | Transient stability for a fault on a Hazelwood-South 500 circuit or volage stability in Southern New South Wales for loss of largest load in Victoria. | Voltage stability in SNSW for loss of the largest generator in Victoria. Prior to HumeLink service, Snowy 2.0 generation or pump load is limited by a transient stability limit.
VIC – SESA (“Heywood”) - (Note 9) | 650 | 650 | 650 | 650 | 650 | 650 | Thermal capacity of Heywood-South East 275 kV line or transient stability limit for loss of the largest generator in South Australia or transient stability limit of loss of South East - Tailem Bend 275 kV line. | Oscillatory stability limit.
SESA-CSA | 650 | 650 | 650 | 650 | 650 | 650 | Transient stability limit for loss of the largest generator in South Australia or transient stability limit of loss of South East - Tailem Bend 275 kV line. | Oscillatory stability limit.
VIC – CSA (Murraylink) | 220 | 220 | 220 | 100 | 200 | 200 | Murraylink thermal capacity. Assumes high renewable generation in North West Victoria during high ambient temperature. | Thermal capability of 132 kV lines between Robertstown and North West Bend
TAS – VIC (Note 12) | 594 | 594 | 594 | 478 | 478 | 478 | Basslink HVDC submarine cable transfer limit. | Basslink HVDC submarine cable transfer limit.
Notes:
1. See table below for reference temperatures for each system condition. The limit is the notional maximum transfer limit at the time of these reference temperatures in the importing region as referred to in the ISP Methodology. The figure quoted is the minimum of the following required limits: transmission asset thermal capacity; voltage stability; transient stability; oscillatory stability; and system strength and inertia.
2. These transfer limits are representation in the Capacity Outlook Model. The actual transfer capability at any point in time is the result of all constraints invoked at the given time. See https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Security-and-reliability/Congestion-information for further details. The actual interconnector limits for historical dispatch intervals and constraints can be found here: https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Data/Market-Management-System-MMS/Dispatch
3. Similar to real time operation, constraint equations are used in PLEXOS time-sequential modelling. These constraint equations are represented with seasonal thermal ratings and location of generation and include both thermal constraints and stability constraints
4. CQ-GG limits are heavily influenced by the amount of generation and northern and central QLD, particularly at Gladstone. The provided transfer limit is a representation with typical generation output from Stanwell and Calvale and reduced generation at Gladstone. This limit will be further reviewed with hourly simulation results.
5. QLD to NSW transfer limit influenced by generation output from Sapphire wind farm. For peak demand, typical summer and winter reference conditions Sapphire wind dispatch assumed to be 33%, 50% and 50% respectively.
6. This limit has been formulated for the DLT model and shouldn't be used for other applications. AEMO has worked closely with EnergyCo and Transgrid to refine this limit to be used for the DLT model. CNSW-SNW transfer limit improvement with Waratah Super Battery (WSB) with a system integrity protection scheme (SIPS) and associated minor network augmentation and, Central West Orana transmission link are provided in a table below titled 'Notional transfer capability uplift between the sub-regions for committed and anticipated projects'.
7. Power is not expected to frequently flow from SNW to CNSW since the major load centre is SNW. For DLT modelling, CNSW-SNW transfer limit can be represented as two limits. One as CNSW-SNW_South and other as CNSW-SNW_North
8. Victoria system integrity protection scheme (SIPS) with 250 MW battery storage in western side of Melbourne raises the thermal capacity of Victoria-New South Wales interconnector. VIC - SNSW transfer limit during peak periods reduces to 250 MW on conclusion of the VNI SIPS agreement 31 March 2032.
9. Heywood interconnector currently operates at 600 MW forward capability and 550 MW reverse capability. AEMO and ElectraNet work towards to release the transfer capability to its designed capability of 650 MW in both directions.
10. Limits were determined with the inclusion of a minor Strathmore to Ross line upgrade.
11. The limit of 660 MW of Snowy 2.0 generation or pumping load represents with Snowy 2.0 connection to the existing network and prior to HumeLink in service. With HumeLink in service, up to 2,200 MW of Snowy 2.0 genertion or pumping load is made avaialble in modelling.
12. The TAS - VIC (Basslink) allowable capability is limited by a daily energy throughput limit, as outlined in the table below. APA has advised AEMO of a new Cable Load Prediction System (CLPS) for Basslink that allows for this dynamic capacity on this existing cable between Tasmania and Victoria, increasing peak transfer capacity to its original design transfer capacity (594 MW towards Victoria and 478 MW towards Tasmania). Source: 2023 ESOO update, https://www.aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/nem_esoo/2023/may-2024-update-to-the-2023-electricity-statement-of-opportunities.pdf?la=en&hash=4425365102C8992B13B4671EC9659E0A
Interconnector Transfer Capability (MW)
This table describes the transfer capability for a regional capacity outlook model for different system conditions. These conditions are the same as the flow path transfer capabilities. This table is included for convenience but not used in the ISP.
Flow paths (Forward power flow direction) | Forward direction capability approximation (MW) - Notes 1,2&3 |  |  | Reverse direction capability approximation (MW) - Notes 1,2&3 |  |  | Dominant constraints
| Peak demand | Summer Typical | Winter Reference | Peak demand | Summer Typical | Winter Reference | Forward direction | Reverse direction
NSW – QLD ("QNI") | 685 (with QNI Minor) | 745 (with QNI Minor) | 745 (with QNI Minor) | 1,205 (with QNI minor) (Note 5) | 1,165 (with QNI minor) (Note 5) | 1,170 (with QNI minor) (Note 5) | Thermal capability of Armidale-Sapphire and Armidale-Dumaresq 330 kV circuits and dispatch of generation at Sapphire. | Thermal capability of Armidale-Sapphire and Armidale-Dumaresq 330 kV circuits and dispatch of generation at Sapphire.
NNSW – SQ (“Terranora”) | 0 | 50 | 50 | 130 | 150 | 200 | Thermal capability of Lismore 132kV lines (9U9). | Thermal capability of Mudgeeraba 275/110 kV transformers
VIC – NSW | 870 (with VNI minor) | 1,000 (with VNI minor) | 1,000 (with VNI minor) | 400 (with VNI SIPS) (Note 4) | 400 | 400 | Transient stability for a fault on a Hazelwood-South 500 circuit or volage stability in Southern New South Wales for loss of largest load in Victoria. | Voltage stability in SNSW for loss of the largest generator in Victoria.
VIC – SESA (“Heywood”) | 650 | 650 | 650 | 650 | 650 | 650 | Thermal capacity of Heywood-South East 275 kV line or transient stability limit for loss of the largest generator in South Australia or transient stability limit of loss of South East - Tailem Bend 275 kV line. | Oscillatory stability limit.
VIC – CSA (Murraylink) | 220 | 220 | 220 | 100 | 200 | 200 | Murraylink thermal capacity. Assumes high renewable generation in North West Victoria during high ambient temperature. | Thermal capability of 132 kV lines between Robertstown and North West Bend
TAS – VIC (Note 6) | 594 | 594 | 594 | 478 | 478 | 478 | Basslink HVDC submarine cable transfer limit. | Basslink HVDC submarine cable transfer limit.
Notes:
1. See table below for reference temperatures for each system condition. The limit is the notional maximum transfer limit at the time of these reference temperatures in the importing region as referred to in the ISP Methodology. The figure quoted is the minimum of the following required limits: transmission asset thermal capacity; voltage stability; transient stability; oscillatory stability; and system strength and inertia.
2. These transfer limits are representation in the Capacity Outlook Model. The actual transfer capability at any point in time is the result of all constraints invoked at the given time. See https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Security-and-reliability/Congestion-information for further details. The actual interconnector limits for historical dispatch intervals and constraints can be found here: https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Data/Market-Management-System-MMS/Dispatch
3. Similar to real time operation, constraint equations are used in PLEXOS time-sequential modelling. These constraint equations are represented with seasonal thermal ratings and location of generation and include both thermal constraints and stability constraints
4. Victoria system integrity protection scheme (SIPS) with 250 MW battery storage in western side of Melbourne raises the thermal capacity of Victoria-New South Wales interconnector. VIC - SNSW transfer limit during peak periods reduces to 250 MW on conclusion of the VNI SIPS agreement 21 March 2032
5. QLD to NSW transfer limit influenced by generation output from Sapphire wind farm. For peak demand, typical summer and winter reference conditions Sapphire wind dispatch assumed to be 33%, 50% and 50% respectively.
6. The TAS - VIC (Basslink) allowable capability is limited by a daily energy throughput limit, as outlined in the table below. APA has advised AEMO of a new Cable Load Prediction System (CLPS) for Basslink that allows for this dynamic capacity on this existing cable between Tasmania and Victoria, increasing peak transfer capacity to its original design transfer capacity (594 MW towards Victoria and 478 MW towards Tasmania). Source: 2023 ESOO update, https://www.aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/nem_esoo/2023/may-2024-update-to-the-2023-electricity-statement-of-opportunities.pdf?la=en&hash=4425365102C8992B13B4671EC9659E0A
Notional transfer capability uplift between the sub-regions for committed and anticipated projects
Flow paths (Forward power flow direction) (Note 1) | Project EnergyConnect |  | WSB + SIPS + Minor network augmentation(Note 3) |  | Minor network augmentation
| Forward direction | Reverse direction | Forward direction | Reverse direction | Forward direction | Reverse direction
SNSW-CSA | 800 | 800
VIC-SESA | 100 | 100
SESA-CSA | 100 | 100
SNSW-CSA and VIC-SESA combined | 650 (Note 4) | 800 (Note 4)
CNSW - SNW |  |  | 910 (Note 6) | - (Note 5) | 250 | - (Note 5)
SNSW-CNSW |  |  | 250 | 0 | 0 | 0
CNSW-NNSW |  |  | 0 | 300 | 0 | 0
Notes:
1. Transfer limits with VNI minor and QNI minor projects are included in previous two tables.
2. Minor network augmentation includes uprating of Bannaby-Sydney West, Yass-Marulan and Yass-Collector-Marulan 330 kV lines. This limit has been formulated for the DLT model and shouldn't be used for other applications.
3. This limit has been formulated for the DLT model and shouldn't be used for other applications.
4. Total maximum transfer capacity of SNSW-CSA and VIC-SESA is limited to 1,300 in forward direction and 1,450 MW in reverse direction.
5. Power is not expected to flow from SNW to CNSW since the major load centre is SNW. For DLT modelling, no additional transfer limit is assumed. This will be reviewed if it becomes material.
6. The increase in capacity between CNSW and SNW is dependent on the output of the generation paired with the SIPS control scheme for a given period in time.
Common reference temperature and summer typical temperature
This table lists the temperature basis for the Flow Path Transfer capabilities described above.
Region | Summer 10% POE Demand Reference Temperature (Peak demand ) | Summer Temperature (Summer Typical) | Winter Reference Temperature (Winter Typical)
Queensland | 37 | 32 | 15
New South Wales | 42 | 32 | 9
Victoria | 41 | 32 | 8
South Australia | 43 | 35 | 11
Tasmania | 7.7 | N/A (note 1) | 1.2
Note 1: Tasmania summer ratings are based on peak demand periods driven by cold weather. AEMO only uses the 10% POE demand reference temperature for Tasmanian summer ratings.
Transfer Capability - Dynamic - Temperature dependent
This table describes the representation of Murraylink's transfer capability in the time sequential (ST) stage of the ISP modelling. These transfer limits are temperature dependent.
VIC – SA (Murraylink) (Note 1)
Ambient temperature °C | Forward (MW) | Reverse (MW)
<33 | 220 | 220
34 | 220 | 220
35 | 220 | 220
36 | 220 | 220
37 | 220 | 220
38 | 220 | 220
39 | 192.5 | 192.5
40 | 165 | 165
41 | 137.5 | 137.5
42 | 110 | 110
43 | 82.5 | 82.5
44 | 55 | 55
45 | 27.5 | 27.5
46 | 0 | 0
47> | 0 | 0
Notes
1. Murray link will be taken as the highest temperature at either Red Cliffs or Berri.
Basslink Static Daily Energy Throughput Limit
This table describes the static daily energy throughput limit (in both forward and reverse direction) for Basslink. This limit is applied in the time sequential (ST) stage of the ISP modelling.
Month of the year | Static Daily Energy limit (MWh)
January | 10728
February | 10632
March | 10584
April | 10536
May | 10512
June | 10512
July | 10512
August | 10584
September | 10872
October | 10992
November | 10920
December | 10824
Committed and anticipated project timing
This table lists the timing as per latest project advice for committed and anticipated transmission projects. Some committed and anticipated transmission projects are not included in this list because they are unlikely to impact AEMO’s modelling.
Project (Note 1) | Service Date (Note 1 + Note 2)
CopperString 2032 (QEJP Stage 4) | 2029-06-30
Project EnergyConnect - Stage 1 | 2024-12-01
Project EnergyConnect - Stage 2 | 2027-07-01
Waratah Super Battery Network Augmentations and SIPS Control | 2025-08-01
Waratah Super Battery Network Augmentation | 2025-08-01
Central-West Orana REZ Transmission Link ( Note 3) | 2028-08-01
Far North Queensland REZ (Note 3) | 2024-04-01
Mortlake Turn-In | 2025-10-01
Koorangie Energy Storage System (KESS) | 2025-06-01
Murray River REZ and Western Victoria REZ minor augmentations | 2025-10-01
Victoria Central North REZ minor augmentations | 2025-10-01
Western Renewables Link | 2027-07-01
South West VIC REZ minor augmentations | Dec-24
Notes
1. For further details on these projects please refer to the Transmission Augmentation Page at https://aemo.com.au/energy-systems/electricity/national-electricity-market-nem/nem-forecasting-and-planning/forecasting-and-planning-data/transmission-augmentation-information.
2. Service date refers to capacity release date in the Transmission Augmentation Information page, or the in-service date in the Transmission Augmentation Information page if no capacity release date is available.
3. The Far North Queensland REZ project is modelled as commissioned by April 2024. However, latest information from Powerlink notes the new date of commissioning is 30 June 2024. Please refer to the Transmission Augmentation Information page for more information, at https://aemo.com.au/en/energy-systems/electricity/national-electricity-market-nem/nem-forecasting-and-planning/forecasting-and-planning-data/transmission-augmentation-information.

## Flow Path Augmentation options
Go to Assumptions Summary | [7 empty] | `
Flow path augmentation options
Flow path augmentation options listed below are for long-term simulations in the Capacity Outlook Model. These include network and non-network options to increase the flow path transfer capacity.
Non-network options also include local generation and/or energy storage within the receiving end of the area. These are separately provided to the Capacity Outlook Model.
The notional transfer level increase presented in this table is in addition to the transfer levels stated in the "Network Capability" work sheet.
Transfer capacities vary with generation dispatch, load and weather conditions. Similar to NEMDE, these variabilities are captured in the network constraint equations for simulations in short-term models using time-sequential half-hourly modelling.
With the Capacity Outlook Modelling results, further studies will be undertaken to identify alternative network (such as network switching reconfiguration, power flow controllers, reactive plants etc.) and non-network options to maximise the utilisation of existing transmission assets.
The transfer capabilities shown in this table are applicable from July 2023. This includes full service of committed and anticipated transmission projects expected by July 2023 (Note 1)
Central Queensland (CQ) to North Queensland (NQ)
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million) - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting capacity provided
[6 empty] | Forward direction | Reverse direction
CQ-NQ | Existing CQ-NQ path | To accommodate more renewable generation in REZ Q1, Q2 and Q3 | CQ-NQ Option 1 | • Construct an additional 275 kV double-circuit line from Ross to Strathmore to Nebo, initially switching one side only. | CQ to NQ | 1100 | 1100 | 1239 | AEMO (TCD) | Class 5b | 350 | Medium | Q3: 1,100
|  |  | CQ-NQ Option 2 | • Establish 500 kV substations at locality of northern part of CQ. • Substation works at Townsville 500kV (established as part of CopperString project) • 2 x 1,500 MVA 500 / 275 kV transformers at northern CQ substation • Establish a 500 kV double-circuit steel tower (DCST) line from CQ to northern CQ substations. • Establish a 500 kV DCST line from northern CQ to NQ substations. • Special protection scheme for transfer limit increase(similar to Virtual transmission line). Cost of this Network Service Agreement (NSA) excluded. Prerequisite: CQ-SQ Option 5 (QEJP) |  | 3000 | 3000 | 4184 | AEMO (TCD) | Class 5b | 750 | Long | Q3: 3,000 Q2: 800 NQ2: 3,000
Central Queensland (CQ) to Gladstone Grid (GG)
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million) - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting capacity provided
[6 empty] | Forward direction | Reverse direction
CQ-GG | Existing CQ-GG path | Increase thermal capability of transmission lines to supply Boyne Island load and load supplied from Calliope River, Gladstone and Larcom Creek substations following retirement of generators in Gladstone and increased generation from North Queensland. | CQ-GG Option 1 | • New 275 kV high-capacity double-circuit line between Calvale and Calliope River. • Rebuild Calliope River to Larcom Creek 275 kV high-capacity double-circuit line. • Rebuild Larcom Creek to Bouldercombe 275 kV high-capacity double-circuit line. • A new (third) 275/132 kV transformer at Calliope River. | CQ to GG | 2600 | 500 | 1300 | Powerlink | Class 5b | 0 | 2030-31 (See note 10) | -
Southern Queensland (SQ) to Central Queensland (CQ)
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million) - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting & generation capacity provided
[6 empty] | Forward direction | Reverse direction
SQ-CQ | West of the existing SQ-CQ path | Increase voltage and transient capability of the SQ-CQ corridor for an outage of Calvale-Halys 275 kV circuit. | SQ-CQ Option 1 | • A new 275 kV double-circuit line between Calvale and Wandoan South. • 275 kV line shunt reactors at both ends of Calvale – Wandoan South 275 kV circuits. | SQ to CQ | 900 | 900 | 820 | AEMO (TCD) | Class 5b | 250 | December 2028 (5 years from project approval) | Q6: 900
| Existing SQ-CQ path |  | SQ-CQ Option 2 | • Mid-point switching substation on the existing Calvale–Halys 275 kV double-circuit line. |  | 0 | 300 | 77 | AEMO (TCD) | Class 5b | 0 | Short | -
|  |  | SQ-CQ Option 3 | • Non-network option – a Virtual Transmission Line option with a 300 MW energy storage system north of Calvale and south of Halys. |  | 300 | 300 | Non-network option costs to be provided by interested parties |  |  |  |  | Q6: 300
| West of the existing SQ-CQ path |  | SQ-CQ Option 4 | • A 1,500 MW HVDC bi-pole overhead transmission line from Calvale to South West Queensland. • A new 1,500 HVDC bipole converter station in locality of Calvale. • A new 1,500 HVDC bipole converter station in South West Queensland. • AC network connection between HVDC converter station and 275 kV substation in Calvale. • AC network connection between HVDC converter station and 275 kV AC network in South West Queensland. |  | 1500 | 1500 | 1853 | AEMO (TCD) | Class 5b | 250 | Long | Q6: 1,500
| East of existing SQ-CQ path |  | SQ-CQ Option 5 | • Establish 500 kV Halys substation (with 3x500/275 kV 1,500 MVA transformers). • Establish 500 kV substations west of Gladstone (CQ 500kV substation) and Woolooga West (each with 2x500/275 kV 1,500 MVA transformers). • Establish CQ 275 kV substation. • Install dynamic reactive support at CQ substation. • Establish a 500 kV double-circuit line between Halys and Woolooga West substations. • Establish a 500 kV double-circuit line between Woolooga West to CQ substations. • Establish a 275 kV double-circuit line from Woolooga West to existing Woolooga Substation. • Cut the Calliope River to Calvale circuits into the CQ 275kV substation. • Cut the Bouldercombe to Larcom Creek circuits into the CQ 275 kV substation. • Install 2x 275 kV power flow control at existing Woolooga substation on existing 275 kV eastern corridor to South Pine • Special protection scheme for transfer limit increase (similar to Virtual transmission line). Cost of this NSA excluded. Prerequisite: CQ-GG Option 1 (GGR) |  | 3150 | 3150 | 3287 | AEMO (TCD) | Class 5b | 492 | Jun-31 (See note 10) | Q1-Q6 path: 3,000 (should there be no transmission constraints further north) Access to Borumba pumped hydro generation and storage of 1,998 MW
Northern NSW (NNSW) to Southern Queensland (SQ)
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million) - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting capacity provided
[6 empty] | Forward direction | Reverse direction
NNSW-SQ | Near Queensland-New South Wales Interconnector (QNI) path | Increase thermal capacity and, voltage and transient stability limits of 330 kV and 275 kV lines between Armidale and Braemar. | NNSW–SQ Option 1 | Option 1: • A new 330 kV single-circuit line from locality of New England Hub 5 to Dumaresq to Bulli Creek to Braemar. • A new 330/275 kV transformer at Braemar. • 330 kV Line shunt reactor at New England Hub 5, Dumaresq, Bulli Creek, and Braemar for the New England Hub 5 – Dumaresq - Bulli Creek - Braemar 330 kV circuits. (Pre-requisite: Cut-in both Tamworth-Armidale 330 kV lines to a new substation in locality of New England Hub 5). | NNSW to SQ | 730 | 900 | 930 (NSW works) 964 (QLD works) | Powerlink & Transgrid preparatory activity | Class 5 | 460.5 | Medium | -
|  |  | NNSW–SQ Option 2 | • A new 330 kV double-circuit line from locality of New England Hub 5 to Dumaresq to Bulli Creek to Braemar. • A new 330/275 kV transformer at Braemar. • 330 kV Line shunt reactors at New England Hub 5, Dumaresq, Bulli Creek, and Braemar, for the 330 kV lines between New England Hub 5 and Braemar (via Dumaresq and Bulli Creek). (Pre-requisite: Cut-in both Tamworth-Armidale 330 kV lines to a new substation in locality of New England Hub 5). |  | 1260 | 1700 | 1,210 (NSW works) 1,309 (QLD works) | Powerlink & Transgrid preparatory activity | Class 5 | 460.5 | Medium | -
|  |  | NNSW–SQ Option 3 | • A Virtual Transmission Line option with a 200 MW energy storage system south of Armidale and north of Braemar. |  | 200 | 200 | Non-network option costs to be provided by interested parties |  |  |  |  | -
| West of Queensland-New South Wales Interconnector (QNI) path |  | NNSW–SQ Option 4 | • A 2,000 MW HVDC bi-pole overhead transmission between a new substation in North West New South Wales (NWNSW) REZ and Halys. • A new 2,000 HVDC bipole converter station in North West New South Wales • A new 2,000 HVDC bipole converter station in locality of Halys. • AC network connection between HVDC converter station and 275 kV substation in Halys. • AC network connection between HVDC converter station and ac network in in NWNSW REZ. • A new 330 kV line between NWNSW REZ and Tamworth. |  | 1800 | 2000 | 4279 | AEMO (TCD) | Class 5b | 765 | Long | -
|  |  | NNSW–SQ Option 5 | • Establish a new substation in NNSW and to New England REZ Hub 5. • A new 500/275 kV transformer at Halys substation • A new 1x500 kV double-circuit line between Halys and new Dumaresq 500kV substation in NNSW. • A new 1x500 kV double-circuit line between Dumaresq and New England REZ Hub 5). • 2x 500/330 kV transformers connecting to 330kV Dumaresq Pre-requisite: CQ-SQ Option 5 (QEJP), CNSW-NNSW Option 1. |  | 3000 | 2250 | 2,600 (NSW works) 2,659 (QLD works) | Powerlink & Transgrid preparatory activity | Class 5 | 616 | Long | SWQLD1 : 700
Central NSW to Northern NSW
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million) - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting capacity provided
[6 empty] | Forward direction | Reverse direction
CNSW-NNSW | Near the existing CNSW-NNSW corridor | Increase thermal capacity and, voltage and transient stability limits of 330 kV lines between Liddell and Armidale. Provide access to Renewable generation in N1 and N2 REZ. | CNSW-NNSW Option 1 (Note 12) | • New Central (Hub 5) 500/330 kV substation with 3 x 500/330/33 kV 1,500 MVA transformers cut into existing line between Tamworth and Armidale. • New 500 kV DCST line between Central (Hub 5) and Bayswater with Quad Orange conductor. • 4 x 500 kV 150 MVAr line shunt reactors (in total) are required for 500kV DCST line between Central Hub 5 and Bayswater. • New 4 x 330 kV 340 MVA phase shifting transformers at Central (Hub 5). | CNSW to NNSW | 3000 | 3000 | 1834 | AEMO (TCD) | Class 5b | 225 | Sep-28 (See note 10) | N2: 2,000
|  |  | CNSW-NNSW Option 2 (Note 12) | • Expand Northern (Hub 10) switching station to 500/330kV substation with 3 x 500/330/33kV 1,500 MVA transformers and cut into the existing 330 kV lines between Armidale to Sapphire/Dumaresq • Expand Central South (Hub 1) switching station to 500/330 kV substation with 3 x 500/330/33 kV 1,500 MVA transformers. • New 500 kV DCST from Central South (Hub 1) to Bayswater with Quad Orange conductor • Operate line between Central Hub 5 and Central South Hub 1 from 330 kV to 500 kV. • Operate line between Central Hub 5 and Northern Hub 10 from 330 kV to 500 kV. • 4 x 500 kV 150 MVAr line shunt reactors (in total) are required for 500 kV double-circuit line between Central South (Hub 1) and Bayswater. |  | 3000 | 3000 | 1493 | AEMO (TCD) | Class 5b | 217 | Long | N2: 3,000
|  |  | CNSW-NNSW Option 3 | • New Central South (Hub 1) 500/330 kV substation in New England with 3 x 500/330/33 kV 1,500 MVA transformers. • New 330 kV Central (Hub5) switching station in New England and cut into the existing lines between Tamworth and Armidale. • New 500 kV built and initially 330 kV operated double-circuit line from Hub 5 to Hub 1 • New 500 kV double-circuit line between Hub 1 and Bayswater with Quad Orange conductor. • 4 x 500 kV 150 MVAr line shunt reactors (in total) are required for 500 kV double-circuit line between Hub 1 and Bayswater. • Rebuild portion of Line 86 from Hub 5 to Tamworth as 330 kV double-circuit line. • Rebuild Line 88 Tamworth - Muswellbrook and Line 83 Liddell - Muswellbrook as 330 kV double-circuit line. • Augment Hub 5, Tamworth, Muswellbrook and Liddell to accommodate additional lines. |  | 3600 | 3600 | 2452 | AEMO (TCD) | Class 5b | 225 | Long | N1+N2: 3,600
|  |  | CNSW-NNSW Option 4 | • 2,000 MW bi-pole HVDC transmission system between locality Bayswater and locality of Hub 5. • A new 330 kV double-circuit line from a new substation in locality of Hub 5 to Armidale. • Reconnect both Tamworth-Armidale 330 kV lines from Armidale to a new substation in locality of Hub 5. |  | 1750 | 2000 | 2544 | AEMO (TCD) | Class 5b | 280 | Long | N2: 2,000
| West of the existing CNSW-NNSW corridor |  | CNSW-NNSW Option 5 | • A 2,000 MW bi-pole HVDC transmission system between locality of Wollar and locality of Boggabri. • A new 330 kV AC line between locality of Boggabri and Tamworth. |  | 1750 | 2000 | 2796 | AEMO (TCD) | Class 5b | 350 | Long | N1: 2,000
Central NSW (CNSW) to Sydney, Newcastle and Wollongong (SNW)
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million) - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting capacity provided
[6 empty] | Forward direction | Reverse direction
CNSW-SNW | Northern side of Sydney | Retirement of coal-powered generation in New South Wales. | CNSW-SNW Option 1 | Sydney Ring Northern 500 kV loop or the Hunter Transmission Project (HTP): • New switching stations near the existing Bayswater and Eraring substations. • A new 500 kV double-circuit line between near Eraring substation and near Bayswater substation. • 500 kV connections between Bayswater and near Bayswater substations, and between Eraring and near Eraring substations. • Two 500/330 kV 1,500 MVA transformers at near Eraring substation. •Line reactors on 500 kV transmission lines between near Eraring and near Bayswater (See Note 11). Note: when Central West Orana REZ exceeds 3 gigawatts (GW), this option should be considered to transfer this additional generation to SNW. | CNSW to SNW | 5,000 (This capacity increase for accommodation of additional new generation from North of Bayswater and 2/3 generation from Central West NSW) | NA | 1099 | AEMO (TCD) (Note 6) | Class 5b | 110 | Dec-28 (See note 10) | N10: 2,000
| Southern side of Sydney |  | CNSW-SNW Option 2 | SNW Southern Loop: • Establish a new substation in the locality of South Creek with 2 x 500/330/33 kV, 1500 MVA transformers. • Connect the new substation in the locality of South Creek into Eraring – Kemps Creek 500 kV lines and Bayswater – Sydney West and Regentville – Sydney West 330 kV lines. • A new 500 kV double-circuit lines from Bannaby to the new substation in the locality of South Creek. • Rebuild the section of existing Bannaby – Sydney West 330 kV line from locality of South Creek to Sydney West to double-circuit line. • Augment the existing Bannaby and Sydney West substations. • Line reactors on 500 kV transmission lines between Bannaby and locality of South Creek. |  | 4,500 (This capacity increase for accommodation of additional new generation from South of Bannaby and 1/3 generation from Central West NSW | NA | 1550 | Transgrid | Class 5b | 114 | Medium | N11: 2,000
|  |  | CNSW-SNW Option 2b | A new 330 kV double-circuit line from Bannaby to near Greendale Rd, adjacent to existing Line 39. • New underground to overhead transition stations at near Greendale Rd and Luddenham Rd. • New 330 kV underground cables connecting Greendale Rd and Luddenham Rd transition stations. • A new 330 kV double-circuit line from near Luddenham Rd to Sydney West substation, adjacent to existing Line 39. • Augment the existing Bannaby and Sydney West substations. |  | 1,200 (This capacity increase is for accommodation of additional new generation from south of Bannaby) | NA | 893 | AEMO (TCD) | Class 5b | 114 | Medium
|  |  | CNSW-SNW Option 2d | Greater Western Sydney switching station and modular power flow controllers in the Greater Western Sydney region. • New 330kV switching station in the Greater Western Sydney region. • Rearrangement of existing 330kV lines 39, 76, and 77 into the new switching station. • New modular power flow controllers at the new switching station. |  | 0 (This option improves power flow sharing between the northern and southern segments of the CNSW-SNW flow paths. This allows more generation to be transferred to Sydney from SNSW.) | NA | 221 | Transgrid | Class 5b | 0 | 2028-09-01
| Northern and Southern sides of Sydney |  | CNSW-SNW Option 3 | Both SNW Northern 500 kV loop and SNW Southern 500 kV loop: • CNSW-SNW Option 1. • CNSW-SNW Option 2. |  | 8,600 (No restriction to generation dispatch from north, south and west of SNW) (This capacity increase of 8,600 MW consists of maximum generation of 5,000 MW from NNSW and 4,500 MW from SSNW) | NA | 2649 | AEMO (TCD) (Note 6) | Class 5b | 219 | Long | N10: 2,000 N11: 2,000
| Northern and Southern sides of Sydney |  | CNSW-SNW Option 3d | Both SNW Northern 500 kV loop and Option 2d: • CNSW-SNW Option 1. • CNSW-SNW Option 2d. |  | 5,000 (This capacity increase is for accommodation of additional new generation from North of Bayswater and 2/3 generation from Central-West NSW and sharing) | NA | 1320 | AEMO (TCD) and Transgrid | Class 5b | 110 | Dec-28 (See note 10) | REZ N10: 2,000
| Northern side of Sydney |  | CNSW-SNW Option 4 | • A new 500 kV substation near Eraring. • A new 500 kV double-circuit line between substation near Eraring and Eraring. • A new 500 kV double-circuit line between Wollar South and new Eraring substation. • Two 500/330 kV 1,500 MVA transformers at Kemps Creek. • 1 x 330 kV single-circuit line between Vales Pt and new Eraring. • 1 x 330 kV single-circuit line between Vales Pt and Munmorah. • Thermal upgrade for Line 24 Vales Pt – Eraring and 92 Newcastle – Vales Point. • 1 x 330 kV single-circuit line between Liddell – Newcastle. • 1 x 330 kV single-circuit line between Eraring – Newcastle. • Line reactors on 500 kV transmission lines. Pre-requisite: CNSW-SNW Option 1, N3 REZ Option 1. |  | 4,400 (This capacity increase is for accommodation of additional new generation from Central West NSW) | NA | 2470 | AEMO (TCD) | Class 5b | 418 | Long | N10: 2,000
| Bayswater to Newcastle | Hydrogen scenario - To provide access to port near Newcastle. | H-Newcastle (This is not an alternative option to supply SNW) | To provide access to port new Newcastle: • Three new 500 kV lines from Bayswater to Newcastle. • Four new 500/330 kV transformers at Newcastle. • Line shunt reactors at each of the new 500 kV lines. |  | 5000 | 5000 | 1663 | AEMO (TCD) | Class 5b | 210 | Long | -
| Bannaby to Dapto | Hydrogen scenario - To provide access to port near Dapto. | H-Dapto (This is not an alternative option to supply SNW) | To provide access to port near Dapto: • Three new 500 kV lines from Bannaby to Dapto. • Four new 500/330 kV transformers at Dapto. • Line shunt reactors at each of the new 500 kV lines. |  | 5000 | 5000 | 1420 | AEMO (TCD) | Class 5b | 194 | Long | -
| Northern side of Sydney | Retirement of coal-powered generation in New South Wales. | CNSW-SNW Option 6a | • A new 500 kV double-circuit line between substation near Eraring and Bayswater substation. • Two 500/330 kV 1,500 MVA transformers either at Eraring substation or new substation near Eraring • Two 500/330 kV 1,500 MVA transformers at Kemps Creek • 1 x 330 kV SCST line between Vales Pt and Eraring • 1 x 330 kV SCST line between Vales Pt and Munmorah • Thermal upgrade for Line 24 Vales Pt – Eraring and 92 Newcastle – Vales Point • 1 x 330 kV SCST line between Liddell – Newcastle • 1 x 330 kV SCST line between Eraring – Newcastle Pre-requisite: CNSW-SNW Option 1. |  | 4,400 (This capacity increase is for accommodation of additional new generation from NNSW and CNSW) | NA | 1833 | AEMO (TCD) | Class 5b | 263 | Long | -
|  |  | CNSW-SNW Option 6b | • A new 500 kV substation near Eraring substation. • A new 500 kV double-circuit line between substation near Eraring and Bayswater substation. • A new 500/330 kV substation in locality of Richmond Vale with two 500/330 kV 1,500 MVA transformers cut in Line 81 and 82. • Two 500/330 kV 1,500 MVA transformers at new substation near Eraring. • 1 x 330 kV single-circuit line between Vales Pt and new Eraring. • 1 x 330 kV single-circuit line between Vales Pt and Munmorah. • Thermal upgrade for Line 24 Vales Pt – Eraring and 92 Newcastle – Vales Point. • 1 x 330 kV single-circuit line between locality of Richmond Vale – Newcastle. • Line reactors on 500 kV transmission lines. Pre-requisite: CNSW-SNW Option 1. |  | 4,400 (This capacity increase is for accommodation of additional new generation from NNSW and CNSW) | NA | 1411 | AEMO (TCD) | Class 5b | 156 | Long | -
Southern NSW to Central NSW
Flow path | Development flow path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million) - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting & generation capacity provided
[6 empty] | Forward direction | Reverse direction
SNSW-CNSW | HumeLink | To provide access to Snowy 2.0 generation to load centres in SNW. | SNSW-CNSW Option 1 (HumeLink) | • New Gugaa 500/330 kV substation and 330 kV double-circuit connection to the existing Wagga Wagga 330 kV substation. • Three new 500 kV transmission circuits between: - Maragle and Bannaby 500 kV substations. - Maragle and Gugaa 500 kV substations. - Gugaaand Bannaby 500 kV substations. • Three 500/330 kV 1,500 MVA transformers at Maragle substation. • Two 500/330 kV 1,500 MVA transformers at new Gugaa substation. • 500 kV Line shunt reactors at the ends of Maragle – Bannaby, Maragle – Gugaa and Gugaa – Bannaby 500 kV lines. • Augmenting the substations at Maragle, Wagga Wagga and Bannaby to accommodate the additional transmission lines and transformers. | SNSW to CNSW | 2200 | 2200 | 4892 (See note 6) | Transgrid | Class 3 | 360 | 2026-27 (See note 10) | N6+N7:2200 N6:1,500 N5:800 Access to Snowy 2.0 generation and storage of 2,200 MW.
| Wagga Wagga to Bannaby | Increased import from Victoria and South Australia with high existing and Snowy 2.0 hydro generation | SNSW-CNSW Option 2 | • A 2000 MW bi-pole overhead transmission line from locality of Bannaby to locality of Wagga Wagga. • A new 2,000 MW bipole converter station in locality of Bannaby. • A new 2,000 MW bipole converter station in locality of Wagga Wagga. • AC network connection between new HVDC converter station in the locality of Bannaby and the existing Bannaby 500 kV substation. • AC network connection between HVDC converter station in the locality of Wagga Wagga and a future Wagga Wagga 500 kV substation. Pre-requisite: HumeLink |  | 2000 | 2000 | 2450 | AEMO (TCD) | Class 5b | 260 | Long | N6: 2,000
|  |  | SNSW-CNSW Option 3 | • An additional new 500 kV double-circuit line from Dinawan to Near Wagga Wagga. • An additional new 500 kV double-circuit line from Near Wagga Wagga to Bannaby. • 4 additional new 500/330/33 kV 1500 MVA transformers at Dinawan. Pre-requisite: HumeLink, VNI West, SNW Southern 500 kV loop |  | 6000 | 6000 | 3014 | AEMO (TCD) | Class 5b | 481 | Long | N5+N6: 6,000
|  |  | SNSW-CNSW Option 4 | • An additional new 500 kV single-circuit line from Dinawan to Near Wagga Wagga. • An additional new 500 kV single-circuit line from Near Wagga Wagga to Bannaby. • 2 additional new 500/330/33 kV 1500 MVA transformers at Dinawan. Pre-requisite: HumeLink, VNI West, SNW Southern 500 kV loop. |  | 3000 | 3000 | 2370 | AEMO (TCD) | Class 5b | 481 | Long | N5+N6: 3,000
Victoria to Southern NSW
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million) - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting capacity provided
[6 empty] | Forward direction | Reverse direction
VIC-SNSW | West of VNI 330 kV path | Increase thermal capacity and, voltage and stability limit of VIC-NSW interconnector. Provide route diversity of existing VNI 330 kV corridor | VIC-SNSW Option 1 - VNI West (Kerang) | • A new 500 kV double-circuit overhead line from Bulgana to near Kerang to Dinawan. • Series compensation on both 500 kV lines between Bulgana to near Kerang. • Upgrade Dinawan – Gugaa double-circuit line from 330 kV to 500 kV operation (lines build at 500 kV as part of Project EnergyConnect). • Establish Dinawan 500 kV switchyard with two 500/330 kV 1,500 MVA transformers. • New terminal station near Kerang with two 500/220 kV 1,000 MVA transformers. • 220 kV connections from the new terminal station near Kerang to the existing 220 kV lines near Kerang. • Modular power flow controllers or other equipment to prevent overloading on 330 kV lines between Upper/Lower Tumut and South Morang and 220 kV lines between Dederang and Thomastown. • 500 kV line shunt reactors at both ends of the three following 500 kV circuits: (i) Bulgana – near Kerang, (ii) near Kerang – Dinawan and (iii) Dinawan – Gugaa. • Two new 500 kV bays and line exits at the Bulgana. • Up to +/- 400 MVAr dynamic reactive compensation at the new 220 kV terminal station near Kerang. | VIC to SNSW | 1935 | 1669 | 3614 (Note 9) | AEMO (Victorian Planning) &Transgrid | Class 4 | 438 | Long | V2: 1,580 V3 (WRL timing): 1,460 V3 (WRL & VNI timing): 200 N5: 900
Tasmania to Victoria
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million) - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting capacity provided
[6 empty] | Forward direction | Reverse direction
TAS-VIC | Proposed Marinus Link path (path between Burnie area and Latrobe Valley area) | Access to high quality wind resources in Tasmania and deep storage capability of Tasmanian hydro generation. | TAS-VIC Option 1 (Project Marinus Stage 1) | •A 750 MW monopole HVDC link between Burnie area in Tasmania and Hazelwood area in Victoria. • A new 750 MW HVDC monopole converter station in Burnie area. • A new 750 MW HVDC monopole converter station in Hazelwood area. • A new 220 kV switching station at Heybridge adjacent to the converter station. • A new double-circuit 220 kV transmission line between Sheffield, Heybridge and Burnie • A new 220 kV double-circuit line from Palmerston to Sheffield with decommissioning of existing the single-circuit line. • A new 500 kV connection from converter station in Hazelwood area. • Decommission existing Sheffield – Burnie 220 kV line. Note: HVDC interconnector components are referred to as Marinus Link 1 | TAS to VIC | 750 Basslink and Marinus Link 1 combined transfer limit 1,344 (Note 4) | 750 Basslink and Marinus Link 1 combined transfer limit 978 | 3,840 (See note 7) | TasNetworks Marinuslink | Class 4 | ~90 (underground cable) 0 (HVAC new easement) | Dec-30 (See note 7)
|  |  | TAS-VIC Option 2 (Project Marinus Stage 2) | • An additional 750 MW monopole HVDC link between Burnie area in Tasmania and Hazelwood area in Victoria. • An additional new 750 MW HVDC monopole converter station in Burnie area. • An additional new 750 MW HVDC monopole converter station in Hazelwood area. • A new 220 kV switching station at Staverton. • A new double-circuit 220 kV transmission line from Staverton to Burnie via Hampshire • Cut-in both Sheffield-Mersey Forth double-circuit 220 kV lines at Staverton. • Capacity increase of the four Sheffield–Staverton 220 kV transmission circuits. • A new 500 kV connection from converter station in Hazelwood area. Pre-requisite: TAS-VIC Option 1 (Project Marinus Stage 1) Note: HVDC interconnector components are referred to as Marinus Link 2 |  | 750 Basslink and Marinus Link1&2 combined transfer limit 2,094 | 750 Basslink and Marinus Link1&2 combined transfer limit 1,728 | 2,735 (See note 7) Note: This part is estimated to cost an additional $235 million if completed more than 2 years after Stage 1 | TasNetworks Marinuslink | Class 4 | 0 (underground cable) ~94 (HVAC new easement) | Dec-32 (See note 7)
Victoria to South East South Australia
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million - Note 2) | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting capacity provided
[6 empty] | Forward direction | Reverse direction
VIC-SESA | Near existing VIC-SESA corridor | Increased generation in SA | VIC-SESA Option 1 | • Build a 275 kV double-circuit line from an offshore collection node in South East SA to Heywood terminal station. • 2x1,000 MVA 500/275 kV transformers at Heywood terminal station. • New offshore collection terminal station. | VIC to SESA | 1,640 (Note 8) | 1,640 (Note 8) | 892 | AEMO (TCD) | Class 5b | 240 | Long | S1: 1,640
|  |  | VIC-SESA Option 2 | • Build a 500 kV double-circuit line from an offshore collection node in South East SA to Heywood terminal station. • New offshore collection terminal station. • 2x 1500 MVA 500/275 kV transformers at offshore collection terminal station. |  | 3,000 (Note 8) | 3,000 (Note 8) | 1363 | AEMO (TCD) | Class 5b | 240 | Long | S1: 3,000
South East South Australia to Central South Australia
Flow path | Development path | Development Driver | Option Name | Augmentation Description | Forward direction power flow | Notional transfer level increase (MW) Note: Same increase applies to all transfer limit conditions (Peak demand, Summer typical and Winter reference) |  | Indicative cost estimate ($2023, $ million - Note 2 | Cost estimate source | Cost estimate class | Easement length in km | Lead time or Earliest in Service Date - Notes 3 & 4 | Additional REZ hosting capacity provided
[6 empty] | Forward direction | Reverse direction
SESA-CSA | East of existing SESA-CSA corridor | Increased power transfer capability with Victoria | SESA-CSA Option 1 | • Build a 500 kV double-circuit line from Bundey terminal station to an offshore collection node in South East SA. • 2x 1,500 MVA 500/275 kV transformers at Bundey terminal station. • New offshore collection terminal station. • 2x 1,500 MVA 500/275 kV transformers at offshore collection terminal station. | SESA to CSA | 3000 | 3000 | 1807 | AEMO (TCD) | Class 5b | 290 | Long | S1: 3,000 S1-TBMO: 3,000
Notes:
1. Committed and anticipated transmission augmentations and transfer capability increase are listed in 'Network Capability' tab.
2. Cost estimates. AEMO estimates sourced from the AEMO Transmission Cost Database Class 5a are with +/-30% accuracy. Class 5b are with +/-50% accuracy. For TNSP cost estimates, refer to the 2023 Transmission Expansion Options Report for accuracy bands and other details.
3. Lead time for expected service is provided from the release of final 2024 ISP. This lead time is categorized as short (3-5 years), medium (6-7 years) and long (beyond 7 years).
4. For modelling runs where MarinusLink is built, certain generator capacities are adjusted upwards in Tasmania: 100 MW across the west coast, 150 MW for Tarraleah and 90 MW capacity for Gordon. This is made available through upgrading assets and adapting hydropower operations to take advantage of the ‘head effect’ (the extra capacity and efficiency of generation when there is a greater altitude difference between the top of the storage and the power station). This also includes 50 MW non scheduled generation Source: Battery of the Nation - Unlocking Tasmania’s energy capacity.
5. A 1% of capital cost is assumed as operation and maintenance cost of each of the interconnector options.
6.Based on updated scope received from EnergyCo in May 2024
7.This cost is presented in real 2023 dollars as advised by Marinus Link Pty Ltd for the HVDC scope and from TasNetworks for the HVAC scope. These cost estimates do not include $267m of design and approval sunk costs as these are covered by grant and shareholder funding from Australian and Tasmanian governments allocated to Project Marinus. Class 4 is indicative of a +/-30% accuracy band. The earliest in service date is as advised by proponents at time of modelling. Updated full capacity release dates have since been advised, as noted in the December 2023 Transmission Augmentation Information page.
8. Transfer limits between Heywood and Sydenham are modelled by a REZ group constraint SWV1
9. This cost estimate applies a cost of $3,614 million for VNI West. This is determined by subtracting the cost of Western Renewables Link from the public cost estimate from AEMO Victorian Planning and Transgrid, and then converting from 2021 dollars to real 2023 dollars.
10.The earliest in service date is as advised by proponents at time of modelling. It is noted that updated project proponent full capacity release dates have since been advised, as noted in the May 2024 Transmission Augmentation Information page.
11. The need for line reactors is a subject of ongoing joint planning with EnergyCo and Transgrid.
12. This table shows the scope, additional network capacity and cost estimate as modelled for the 2024 ISP. In May 2024, EnergyCo released refined scoping and timing for this project, after community consultation and engagement. These changes have not been included in the final 2024 ISP model due to modelling timelines, however it is expected by AEMO and EnergyCo that these updated options would provide the same or similar amount of additional network capacity as modelled in the ISP. The updated EnergyCo advice can be viewed in the May 2024 and June 2024 updates to AEMO’s Transmission Augmentation Information page.

## Flow Path costs forecast
Go to Assumptions Summary | [7 empty] | `
Flow path augmentation cost forecasts (real 2023 dollars)
AEMO has applied escalation factors to flow path augmentation project cost estimates for the ISP, consistent with its transmission cost forecasting approach.
See 2023 Transmission Expansion Options Report for further details.
The worksheet has Progressive and Step Change/Green Energy Export cost forecast. These cost escalations are year on year cost esclations.
Step Change and Green Energy Exports
Central Queensland (CQ) to North Queensland (NQ)
Flow Path | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
CQ-NQ | CQ-NQ Option 1 | 1239107366.22 | 1241358548.8432 | 1259875321.5268 | 1278619518.4222 | 1293512905.8743 | 1302016527.415 | 1311918501.2629 | 1320664833.7496 | 1328492601.0592 | 1333127398.4964 | 1335091179.4665 | 1337090993.1149 | 1339126839.4417 | 1341198718.4468 | 1343297621.9607 | 1345441566.3226 | 1347621543.3628 | 1349837553.0813 | 1352089595.4782 | 1354314613.3664 | 1356548639.4241 | 1358782665.4818 | 1361007683.3699 | 1363241709.4277 | 1365475735.4854 | 1367709761.5431 | 1369943787.6008 | 1372177813.6586 | 1374411839.7163 | 1376645865.774 | 1378879891.8317 | 1381113917.8894 | 1383347943.9472
| CQ-NQ Option 2 | 4184372728.92 | 4201489765.021 | 4257901259.9109 | 4319984498.1611 | 4366305081.8534 | 4393905482.4737 | 4425457728.0795 | 4453743255.4845 | 4479494147.6505 | 4490919735.3323 | 4495826795.0246 | 4500823892.5094 | 4505911027.7868 | 4511088200.8567 | 4516332902.2709 | 4521690150.9258 | 4527137437.3732 | 4532674761.6132 | 4538302123.6457 | 4543861957.3337 | 4549444300.4699 | 4555026643.6061 | 4560586477.2942 | 4566168820.4304 | 4571751163.5666 | 4577333506.7028 | 4582915849.839 | 4588498192.9752 | 4594080536.1114 | 4599662879.2476 | 4605245222.3838 | 4610827565.52 | 4616409908.6562
Central Queensland (CQ) to Gladstone Grid (GG)
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
CQ-GG | CQ-GG Option 1 | 2021-22: Preparatory Activites- See note
Southern Queensland (SQ) to Central Queensland (CQ) | bar: 2021-22; 2032-33 to 2053-54
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
SQ-CQ | SQ-CQ Option 1 | 819110031.49 | 821517020.16 | 833816930.59 | 846920987.02 | 857326971.33 | 862999265.06 | 869542788.87 | 875425592.05 | 880798646.93 | 882285636.64 | 883800134.01 | 885342420.33 | 886912495.59 | 888510359.79 | 890129065.7 | 891782507.79 | 893463738.82 | 895172758.79 | 896909567.71 | 898625534.91 | 900348449.36 | 902071363.8 | 903787331.01 | 905510245.46 | 907233159.9 | 908956074.34 | 910678988.79 | 912401903.23 | 914124817.68 | 915847732.12 | 917570646.56 | 919293561.01 | 921016475.45
| SQ-CQ Option 2 | 77274371.17 | 77448985.4071 | 79266602.937 | 80714734.148 | 81339595.6975 | 81576812.1356 | 81977875.1499 | 82407922.9401 | 82855819.6677 | 82872130.9011 | 82878726.5254 | 82885443.1703 | 82892280.8358 | 82899239.5219 | 82906288.9736 | 82913489.701 | 82920811.449 | 82928254.2177 | 82935818.0069 | 82943291.0308 | 82950794.3097 | 82958297.5887 | 82965770.6125 | 82973273.8915 | 82980777.1705 | 82988280.4495 | 82995783.7284 | 83003287.0074 | 83010790.2864 | 83018293.5653 | 83025796.8443 | 83033300.1233 | 83040803.4023
| SQ-CQ Option 3 | 2021-22: Non-Network Augmentation
| CQ-SQ Option 4 | 1852638866.62 | 1873845311.2944 | 1912297233.7646 | 1946888065.3554 | 1969375333.3089 | 1979785874.0988 | 1990223700.5165 | 2001181986.6978 | 2013009565.5867 | 2017298095.2522 | 2019792290.1995 | 2022332250.1917 | 2024917975.2288 | 2027549465.3108 | 2030215279.1765 | 2032938299.3483 | 2035707084.565 | 2038521634.8266 | 2041381950.1331 | 2044207941.6559 | 2047045374.44 | 2049882807.2241 | 2052708798.7469 | 2055546231.531 | 2058383664.315 | 2061221097.0991 | 2064058529.8831 | 2066895962.6672 | 2069733395.4513 | 2072570828.2353 | 2075408261.0194 | 2078245693.8035 | 2081083126.5875
| CQ-SQ Option 5 | 3286871982.09 | 3300251876.3053 | 3349692819.27 | 3402908138.015 | 3440069815.0958 | 3459850106.6176 | 3483286517.563 | 3505094499.0013 | 3525713286.6638 | 3534393696.7699 | 3538724966.718 | 3543135709.5093 | 3547625925.1436 | 3552195613.621 | 3556824906.7307 | 3561553540.8943 | 3566361647.9009 | 3571249227.7507 | 3576216280.4435 | 3581123728.504 | 3586051044.7753 | 3590978361.0466 | 3595885809.1071 | 3600813125.3784 | 3605740441.6497 | 3610667757.921 | 3615595074.1922 | 3620522390.4635 | 3625449706.7348 | 3630377023.0061 | 3635304339.2774 | 3640231655.5487 | 3645158971.82
Northern NSW (NNSW) to Southern Queensland (SQ) | bar: 2032-33 to 2053-54
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NNSW-SQ | NNSW–SQ Option 1 | 2021-22: Preparatory Activites- See note
NNSW–SQ Option 2
| NNSW–SQ Option 3 | 2021-22: Non-Network Augmentation
| NNSW–SQ Option 4 | 4278938560.29 | 4332575636.9924 | 4418406436.2934 | 4503298550.6955 | 4559966617.3236 | 4587424546.6062 | 4614341908.6381 | 4641754630.0655 | 4670887344.8373 | 4692600124.7925 | 4699052074.8835 | 4705622409.3798 | 4712311128.2815 | 4719118231.5885 | 4726014123.1995 | 4733057995.3172 | 4740220251.8402 | 4747500892.7686 | 4754899918.1023 | 4762210155.132 | 4769549988.2631 | 4776889821.3941 | 4784200058.4238 | 4791539891.5549 | 4798879724.6859 | 4806219557.817 | 4813559390.948 | 4820899224.079 | 4828239057.2101 | 4835578890.3411 | 4842918723.4722 | 4850258556.6032 | 4857598389.7342
| NNSW–SQ Option 5 | 2021-22: Preparatory Activites- See note
Central NSW to Northern NSW | bar: 2032-33 to 2053-54
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
CNSW-NNSW | CNSW-NNSW Option 1 | 1834410577.13 | 1839984585.4914 | 1870490675.9238 | 1901016121.539 | 1920883577.9873 | 1930908055.5878 | 1943401003.8002 | 1955223742.3465 | 1966540533.8133 | 1977435998.7638 | 1979577429.9072 | 1981758153.3652 | 1983978169.1378 | 1986237477.2249 | 1988526254.5479 | 1990864147.2641 | 1993241332.2949 | 1995657809.6402 | 1998113579.3001 | 2000539879.724 | 2002976003.2266 | 2005412126.7292 | 2007838427.1532 | 2010274550.6558 | 2012710674.1584 | 2015146797.661 | 2017582921.1636 | 2020019044.6662 | 2022455168.1688 | 2024891291.6715 | 2027327415.1741 | 2029763538.6767 | 2032199662.1793
| CNSW-NNSW Option 2 | 1492549482.75 | 1498368669.1638 | 1522299684.6068 | 1547240613.4524 | 1564450054.237 | 1573439757.1332 | 1584194116.2321 | 1594242888.5867 | 1603759294.4082 | 1614609348.3586 | 1616684033.8506 | 1618796786.9663 | 1620947607.7058 | 1623136496.0689 | 1625353935.1498 | 1627618958.7604 | 1629922049.9947 | 1632263208.8526 | 1634642435.3343 | 1636993111.0982 | 1639353303.7681 | 1641713496.4379 | 1644064172.2018 | 1646424364.8716 | 1648784557.5415 | 1651144750.2113 | 1653504942.8811 | 1655865135.5509 | 1658225328.2208 | 1660585520.8906 | 1662945713.5604 | 1665305906.2303 | 1667666098.9001
| CNSW-NNSW Option 3 | 2451577025.7 | 2463020830.0123 | 2502997770.0901 | 2545275893.4835 | 2575674869.1369 | 2591488625.8034 | 2609967764.2152 | 2627209212.8181 | 2643522207.6387 | 2666347675.2928 | 2670535825.2448 | 2674800821.9849 | 2679142665.5131 | 2683561355.8295 | 2688037681.2369 | 2692610065.1294 | 2697259295.81 | 2701985373.2788 | 2706788297.5357 | 2711533586.7015 | 2716298087.5643 | 2721062588.4271 | 2725807877.5929 | 2730572378.4557 | 2735336879.3185 | 2740101380.1813 | 2744865881.0441 | 2749630381.9069 | 2754394882.7697 | 2759159383.6326 | 2763923884.4954 | 2768688385.3582 | 2773452886.221
| CNSW-NNSW Option 4 | 2544205834.44 | 2570694957.3285 | 2622183967.2558 | 2666780915.3469 | 2694522775.777 | 2707824210.6601 | 2721435908.9473 | 2735654907.3803 | 2750909197.5317 | 2762078944.5797 | 2764401889.2217 | 2766767456.7011 | 2769175647.018 | 2771626460.1723 | 2774109240.4548 | 2776645299.2841 | 2779223980.9509 | 2781845285.4551 | 2784509212.7968 | 2787141173.0104 | 2789783788.9333 | 2792426404.8563 | 2795058365.0699 | 2797700980.9928 | 2800343596.9158 | 2802986212.8388 | 2805628828.7617 | 2808271444.6847 | 2810914060.6076 | 2813556676.5306 | 2816199292.4536 | 2818841908.3765 | 2821484524.2995
| CNSW-NNSW Option 5 | 2795731374.64 | 2824605711.5108 | 2880109217.9138 | 2929211740.0852 | 2960356667.7182 | 2975470163.7746 | 2990930764.3006 | 3006892333.8964 | 3023860923.2896 | 3038206140.8204 | 3040979041.9005 | 3043802821.8996 | 3046677480.8175 | 3049603018.6544 | 3052566715.6804 | 3055594011.3551 | 3058672185.9486 | 3061801239.4611 | 3064981171.8925 | 3068122945.1347 | 3071277438.1066 | 3074431931.0785 | 3077573704.3207 | 3080728197.2926 | 3083882690.2645 | 3087037183.2364 | 3090191676.2083 | 3093346169.1802 | 3096500662.1521 | 3099655155.1241 | 3102809648.096 | 3105964141.0679 | 3109118634.0398
Central NSW (CNSW) to Sydney, Newcastle and Wollongong (SNW) | bar: 2032-33 to 2053-54
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
CNSW-SNW | CNSW-SNW Option 1 | 925706435.11 | 931364540.8645 | 946768924.2116 | 964526435.3988 | 978038377.6503 | 984436008.773 | 991788027.5855 | 998814424.6394 | 1005617747.3757 | 1012866032.604 | 1015283256.071 | 1017744832.2621 | 1020250761.1775 | 1022801042.8169 | 1025384588.9995 | 1028023576.0874 | 1030706915.8993 | 1033434608.4355 | 1036206653.6958 | 1038945434.413 | 1041695303.3112 | 1044445172.2094 | 1047183952.9266 | 1049933821.8248 | 1052683690.723 | 1055433559.6213 | 1058183428.5195 | 1060933297.4177 | 1063683166.3159 | 1066433035.2141 | 1069182904.1124 | 1071932773.0106 | 1074682641.9088
| CNSW-SNW Option 2 | 2021-22: Preparatory Activites- See note
| CNSW-SNW Option 2b | 552915990.13 | 556927706.0784 | 567020401.1455 | 579412380.434 | 590485651.2496 | 595473724.5624 | 600937923.5443 | 606097290.2313 | 611033885.9796 | 620074971.9348 | 622701354.5053 | 625375927.5816 | 628098691.1639 | 630869645.252 | 633676742.2195 | 636544077.3194 | 639459602.9251 | 642423319.0368 | 645435225.6543 | 648410989.3924 | 651398800.757 | 654386612.1216 | 657362375.8597 | 660350187.2242 | 663337998.5888 | 666325809.9534 | 669313621.318 | 672301432.6825 | 675289244.0471 | 678277055.4117 | 681264866.7763 | 684252678.1409 | 687240489.5054
| CNSW-SNW Option 3 | 2039055401.68 | 2052316307.6177 | 2087946579.4269 | 2128174216.8465 | 2158400720.6009 | 2172546637.8205 | 2188864792.4954 | 2204571191.1475 | 2219843574.1106 | 2236795963.578 | 2242343540.2399 | 2247992907.2993 | 2253744064.7561 | 2259597012.6103 | 2265526303.2627 | 2271582831.9119 | 2277741150.9586 | 2284001260.4027 | 2290363160.2443 | 2296648717.2878 | 2302959721.9307 | 2309270726.5736 | 2315556283.6171 | 2321867288.2599 | 2328178292.9028 | 2334489297.5457 | 2340800302.1885 | 2347111306.8314 | 2353422311.4743 | 2359733316.1171 | 2366044320.76 | 2372355325.4029 | 2378666330.0457
| CNSW-SNW Option 4 | 2470340313.03 | 2488985096.58 | 2532322682.6794 | 2583182159.4332 | 2623553883.4714 | 2642408283.4201 | 2663473008.258 | 2683650412.1815 | 2703237930.3154 | 2729012480.9162 | 2737101240.288 | 2745338417.263 | 2753724011.8411 | 2762258024.0223 | 2770903349.4059 | 2779734196.7935 | 2788713461.7842 | 2797841144.378 | 2807117244.575 | 2816282031.5696 | 2825483922.9651 | 2834685814.3605 | 2843850601.3551 | 2853052492.7506 | 2862254384.146 | 2871456275.5414 | 2880658166.9368 | 2889860058.3323 | 2899061949.7277 | 2908263841.1231 | 2917465732.5186 | 2926667623.914 | 2935869515.3094
| H-Newcastle (This is not an alternative option to supply SNW) | 1663298988.73 | 1672479189.447 | 1700991413.6333 | 1733805466.6957 | 1759029917.3541 | 1770493012.9608 | 1783822438.1464 | 1796628323.8668 | 1809085148.5782 | 1823821583.9245 | 1828687162.982 | 1833642018.7195 | 1838686151.1369 | 1843819560.2342 | 1849019926.8416 | 1854331889.2988 | 1859733128.436 | 1865223644.2532 | 1870803436.7503 | 1876316271.7375 | 1881851425.8947 | 1887386580.0518 | 1892899415.039 | 1898434569.1961 | 1903969723.3533 | 1909504877.5105 | 1915040031.6676 | 1920575185.8248 | 1926110339.9819 | 1931645494.1391 | 1937180648.2962 | 1942715802.4534 | 1948250956.6105
| H-Dapto (This is not an alternative option to supply SNW) | 1419595460.39 | 1423876905.0336 | 1444318279.0159 | 1464859345.2531 | 1477106893.3942 | 1484146952.0608 | 1492892748.9035 | 1501032167.6417 | 1508748636.9055 | 1515734518.842 | 1516095719.3288 | 1516463547.3474 | 1516838002.8979 | 1517219085.9803 | 1517605139.7116 | 1517999477.8577 | 1518400443.5357 | 1518808036.7455 | 1519222257.4872 | 1519631507.58 | 1520042414.5558 | 1520453321.5316 | 1520862571.6244 | 1521273478.6002 | 1521684385.576 | 1522095292.5517 | 1522506199.5275 | 1522917106.5033 | 1523328013.4791 | 1523738920.4548 | 1524149827.4306 | 1524560734.4064 | 1524971641.3822
| CNSW-SNW Option 6a | 1832882856.49 | 1844970117.5375 | 1877018040.5512 | 1914424933.6747 | 1944076914.3214 | 1957619320.1127 | 1972959607.9342 | 1987674133.8199 | 2001990966.6739 | 2020790690.7918 | 2026777644.7177 | 2032874451.0092 | 2039081109.6664 | 2045397620.6891 | 2051796520.9861 | 2058332736.7401 | 2064978804.8597 | 2071734725.3449 | 2078600498.1957 | 2085383881.7724 | 2092194728.4404 | 2099005575.1084 | 2105788958.685 | 2112599805.353 | 2119410652.021 | 2126221498.6891 | 2133032345.3571 | 2139843192.0251 | 2146654038.6931 | 2153464885.3611 | 2160275732.0292 | 2167086578.6972 | 2173897425.3652
| CNSW-SNW Option 6b | 1410776271.14 | 1420984546.1967 | 1446514378.5297 | 1474659658.8976 | 1495226896.2343 | 1504895682.2741 | 1515983605.1787 | 1526731809.8295 | 1537266021.1016 | 1548271515.5895 | 1551846403.3194 | 1555486885.3196 | 1559192961.59 | 1562964632.1307 | 1566785498.3742 | 1570688357.4554 | 1574656810.807 | 1578690858.4288 | 1582790500.3208 | 1586840946.5102 | 1590907791.2672 | 1594974636.0241 | 1599025082.2135 | 1603091926.9704 | 1607158771.7274 | 1611225616.4843 | 1615292461.2413 | 1619359305.9982 | 1623426150.7551 | 1627492995.5121 | 1631559840.269 | 1635626685.026 | 1639693529.7829
Southern NSW to Central NSW | bar: 2032-33 to 2053-54
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
SNSW-CNSW | SNSW-CNSW Option 1 (HumeLink) | 2021-22: Actionable ISP Project - See note below
| SNSW-CNSW Option 2 | 2450117931.33 | 2477575046.4418 | 2527144244.2174 | 2570707259.5764 | 2597701736.7797 | 2610597739.7471 | 2623583232.8268 | 2637273972.8359 | 2652098010.0266 | 2662080621.9756 | 2664345337.2924 | 2666651607.0187 | 2668999431.1545 | 2671388809.6997 | 2673809354.0521 | 2676281841.4163 | 2678795883.19 | 2681351479.3731 | 2683948629.9658 | 2686514614.7513 | 2689090988.1392 | 2691667361.5271 | 2694233346.3127 | 2696809719.7006 | 2699386093.0885 | 2701962466.4764 | 2704538839.8643 | 2707115213.2522 | 2709691586.6402 | 2712267960.0281 | 2714844333.416 | 2717420706.8039 | 2719997080.1918
| SNSW-CNSW Option 3 | 3013855444.3 | 3031187074.9681 | 3076025895.4739 | 3127932407.9652 | 3167568719.3084 | 3188427140.8853 | 3212037650.4618 | 3233959094.9216 | 3254634288.8398 | 3281763297.2156 | 3287864167.1664 | 3294076979.6852 | 3300401734.7719 | 3306838432.4265 | 3313359087.007 | 3320019669.7974 | 3326792195.1557 | 3333676663.0819 | 3340673073.576 | 3347585527.1442 | 3354525966.3543 | 3361466405.5645 | 3368378859.1327 | 3375319298.3428 | 3382259737.553 | 3389200176.7631 | 3396140615.9733 | 3403081055.1834 | 3410021494.3936 | 3416961933.6038 | 3423902372.8139 | 3430842812.0241 | 3437783251.2342
| SNSW-CNSW Option 4 | 2369893492.41 | 2383644371.4131 | 2420652091.3886 | 2463812802.3332 | 2498556401.1515 | 2516141760.966 | 2535860969.1251 | 2554168019.1921 | 2571433728.286 | 2600611810.1156 | 2606859423.4121 | 2613221671.8149 | 2619698555.3241 | 2626290073.9396 | 2632967568.8849 | 2639788357.7132 | 2646723781.6478 | 2653773840.6888 | 2660938534.8361 | 2668017252.6537 | 2675124629.2478 | 2682232005.842 | 2689310723.6596 | 2696418100.2537 | 2703525476.8479 | 2710632853.442 | 2717740230.0362 | 2724847606.6303 | 2731954983.2245 | 2739062359.8186 | 2746169736.4128 | 2753277113.0069 | 2760384489.6011
Victoria to Southern NSW | bar: 2032-33 to 2053-54
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
VIC-SNSW | VIC-SNSW Option 1 - VNI West (Kerang) | 2021-22: Actionable ISP Project - See note below
Tasmania to Victoria | bar: 2032-33 to 2053-54
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
TAS-VIC | TAS-VIC Option 1 (Marinus Link stage 1) | 2021-22: Actionable ISP Project - See note below
TAS-VIC Option 2 (Marinus Link stage 2)
Victoria to South East South Australia | bar: 2032-33 to 2053-54
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
VIC-SESA | VIC-SESA Option 1 | 892159575.75 | 894733267.0364 | 909733866.6606 | 925500161.3645 | 937884944.8111 | 944039376.8543 | 951275839.7923 | 957935143.9975 | 964148755.0813 | 968582019.5867 | 970681645.2005 | 972819796.055 | 974996472.1501 | 977211673.4858 | 979455768.752 | 981748020.569 | 984078797.6266 | 986448099.9248 | 988855927.4636 | 991234861.0719 | 993623425.9905 | 996011990.909 | 998390924.5173 | 1000779489.4359 | 1003168054.3544 | 1005556619.2729 | 1007945184.1914 | 1010333749.1099 | 1012722314.0285 | 1015110878.947 | 1017499443.8655 | 1019888008.784 | 1022276573.7025
| VIC-SESA Option 2 | 1362860559.09 | 1369071037.5159 | 1389832987.0404 | 1412766264.9812 | 1429903851.4189 | 1438957919.4954 | 1449421670.4925 | 1459089726.1023 | 1468161213.3407 | 1473212390.6682 | 1475661210.3667 | 1478154962.5367 | 1480693647.1783 | 1483277264.2913 | 1485894580.7581 | 1488568062.8142 | 1491286477.3419 | 1494049824.3411 | 1496858103.8118 | 1499632683.9289 | 1502418497.1639 | 1505204310.3988 | 1507978890.5159 | 1510764703.7509 | 1513550516.9859 | 1516336330.2208 | 1519122143.4558 | 1521907956.6908 | 1524693769.9258 | 1527479583.1607 | 1530265396.3957 | 1533051209.6307 | 1535837022.8656
South East South Australia to Central South Australia | bar: 2031-32 to 2053-54
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
SESA-CSA | SESA-CSA Option 1 | 1807467832.2 | 1816592456.7582 | 1846020762.1435 | 1880268010.9392 | 1907632793.8116 | 1920694119.99 | 1935675718.6422 | 1949754733.2189 | 1963175580.3898 | 1971438341.6289 | 1976681080.2737 | 1982020015.9579 | 1987455148.6815 | 1992986478.4444 | 1998589955.9868 | 2004313679.8285 | 2010133600.7094 | 2016049718.6298 | 2022062033.5894 | 2028002200.7696 | 2033966417.2096 | 2039930633.6496 | 2045870800.8298 | 2051835017.2698 | 2057799233.7098 | 2063763450.1498 | 2069727666.5898 | 2075691883.0298 | 2081656099.4698 | 2087620315.9098 | 2093584532.3499 | 2099548748.7899 | 2105512965.2299
Note. AEMO received TNSP cost estimates for actionable ISP projects and projects with preparatory activities from most TNSPs during June 2023. Estimates are escalated here consistent with the 2023 Transmission Expansion Options Report. | bar: 2032-33 to 2053-54
Preparatory activities | bar: 2031-32 to 2053-54
Flow path |  | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
500kV QNI Connect (NSW works) |  | 2658844000 | 2668887131.1932 | 2706890589.3579 | 2749766531.5973 | 2781079636.8686 | 2797443191.4624 | 2816684803.1559 | 2834515734.6106 | 2851342532.5933 | 2870734568.8696 | 2874908580.5643 | 2879159179.6295 | 2883486366.0652 | 2887890139.8715 | 2892351354.2057 | 2896908302.753 | 2901541838.6709 | 2906251961.9594 | 2911038672.6184 | 2915767942.7495 | 2920516359.7232 | 2925264776.6969 | 2929994046.828 | 2934742463.8018 | 2939490880.7755 | 2944239297.7492 | 2948987714.7229 | 2953736131.6967 | 2958484548.6704 | 2963232965.6441 | 2967981382.6178 | 2972729799.5916 | 2977478216.5653
330kV QNI single circuit (NSW works) |  | 963705000 | 968980305.2394 | 985160067.7897 | 1004040506.9748 | 1020214441.7978 | 1027996246.3497 | 1036631503.7094 | 1044634763.6567 | 1052185509.9742 | 1069676299.9497 | 1072999736.9272 | 1076384154.3996 | 1079829552.3671 | 1083335930.8296 | 1086888044.6633 | 1090516384.1158 | 1094205704.0632 | 1097956004.5057 | 1101767285.4431 | 1105532831.0094 | 1109313621.6993 | 1113094412.3893 | 1116859957.9555 | 1120640748.6455 | 1124421539.3354 | 1128202330.0254 | 1131983120.7154 | 1135763911.4053 | 1139544702.0953 | 1143325492.7853 | 1147106283.4752 | 1150887074.1652 | 1154667864.8552
330kV QNI double circuit (NSW works) |  | 1308904000 | 1315802850.7246 | 1337170207.1799 | 1361484767.1993 | 1366942815.3519 | 1376691555.039 | 1387655683.0308 | 1397820655.1281 | 1407402454.5425 | 1423851325.7405 | 1427514099.6771 | 1431244080.4749 | 1435041268.134 | 1438905662.6542 | 1442820462.3204 | 1446819270.5631 | 1450885285.6671 | 1455018507.6322 | 1459218936.4586 | 1463368960.139 | 1467535785.5348 | 1471702610.9305 | 1475852634.611 | 1480019460.0068 | 1484186285.4025 | 1488353110.7983 | 1492519936.194 | 1496686761.5898 | 1500853586.9855 | 1505020412.3813 | 1509187237.7771 | 1513354063.1728 | 1517520888.5686
Sydney Southern Ring |  | 1550000000 | 1559715790.4465 | 1587469415.5611 | 1617901903.695 | 1640300802.9138 | 1650861409.0546 | 1663127888.1238 | 1674928379.2746 | 1686391732.5409 | 1698580592.0665 | 1702500160.6869 | 1706491647.9977 | 1710555053.9987 | 1714690378.69 | 1718879642.399 | 1723158804.4709 | 1727509885.2331 | 1731932884.6855 | 1736427802.8283 | 1740868781.9533 | 1745327740.7509 | 1749786699.5485 | 1754227678.6735 | 1758686637.4711 | 1763145596.2687 | 1767604555.0663 | 1772063513.8638 | 1776522472.6614 | 1780981431.459 | 1785440390.2566 | 1789899349.0542 | 1794358307.8518 | 1798817266.6494
500kV QNI Connect (QLD works) |  | 2600000000 | 2616423540.6527 | 2655090312.8631 | 2702373413.2722 | 2740823554.5893 | 2760450415.6403 | 2782250719.8973 | 2802480552.7665 | 2821564787.6321 | 2833089115.7319 | 2840063647.5608 | 2847166152.4508 | 2854396630.4019 | 2861755081.4141 | 2869209512.2221 | 2876823909.3564 | 2884566279.5518 | 2892436622.8083 | 2900434939.1259 | 2908337275.6477 | 2916271605.4347 | 2924205935.2217 | 2932108271.7435 | 2940042601.5305 | 2947976931.3176 | 2955911261.1046 | 2963845590.8916 | 2971779920.6787 | 2979714250.4657 | 2987648580.2528 | 2995582910.0398 | 3003517239.8268 | 3011451569.6139
330kV QNI single circuit (QLD works) |  | 930000000 | 934101741.0348 | 950717237.2284 | 969902118.1873 | 986627189.3598 | 994252779.0329 | 1002889109.0432 | 1010941145.3449 | 1018558694.6621 | 1025680417.6232 | 1029402722.8764 | 1033193327.3087 | 1037052230.9198 | 1040979433.71 | 1044957860.8843 | 1049021662.0324 | 1053153762.3594 | 1057354161.8654 | 1061622860.5503 | 1065840334.851 | 1070074883.9465 | 1074309433.0419 | 1078526907.3426 | 1082761456.4381 | 1086996005.5335 | 1091230554.629 | 1095465103.7244 | 1099699652.8199 | 1103934201.9153 | 1108168751.0108 | 1112403300.1062 | 1116637849.2017 | 1120872398.2971
330kV QNI double circuit (QLD works) |  | 1210000000 | 1214094171.4861 | 1234734221.4502 | 1257823613.2808 | 1264845826.5548 | 1273745869.8798 | 1284068258.7451 | 1293657578.7665 | 1302693444.901 | 1309383135.0057 | 1313247449.7608 | 1317182669.3738 | 1321188793.8446 | 1325265823.1734 | 1329396031.1456 | 1333614870.1901 | 1337904614.0926 | 1342265262.8529 | 1346696816.4711 | 1351075191.4459 | 1355471292.6352 | 1359867393.8244 | 1364245768.7992 | 1368641869.9885 | 1373037971.1778 | 1377434072.367 | 1381830173.5563 | 1386226274.7456 | 1390622375.9348 | 1395018477.1241 | 1399414578.3134 | 1403810679.5026 | 1408206780.6919
CQ-GG |  | 1300000000 | 1304437596.7393 | 1325457018.0761 | 1346619963.7206 | 1362156413.8865 | 1370710386.5611 | 1380692439.767 | 1389764638.5506 | 1398136950.289 | 1402468129.0587 | 1404369992.5143 | 1406306752.5471 | 1408278409.1571 | 1410284962.3442 | 1412317687.9641 | 1414394034.3056 | 1416505277.2242 | 1418651416.7199 | 1420832452.7929 | 1422987316.4329 | 1425150904.2173 | 1427314492.0016 | 1429469355.6417 | 1431632943.4261 | 1433796531.2104 | 1435960118.9948 | 1438123706.7791 | 1440287294.5635 | 1442450882.3478 | 1444614470.1322 | 1446778057.9165 | 1448941645.7009 | 1451105233.4852
Actionable ISP projects | bar: 2031-32 to 2053-54
Flow path |  | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Humelink |  | N/A | N/A | N/A | N/A | N/A | 4892000000 | 4925609941.9223 | 4957023670.2499 | 4987004896.9631 | 4995100133.7877 | 5003342363.6601 | 5011735827.1082 | 5020280524.1319 | 5028976454.7313 | 5037785810.5124 | 5046784208.263 | 5055933839.5893 | 5065234704.4912 | 5074686802.9688 | 5084025476.2646 | 5093401957.9543 | 5102778439.6441 | 5112117112.9399 | 5121493594.6296 | 5130870076.3194 | 5140246558.0091 | 5149623039.6989 | 5158999521.3886 | 5168376003.0783 | 5177752484.7681 | 5187128966.4578 | 5196505448.1476 | 5205881929.8373
VNI West |  | 3614000000 | 3628160087.8308 | 3684619600.6937 | 3742616230.3809 | 3781193300.4727 | 3800977348.9401 | 3824987697.1569 | 3847789418.8726 | 3869710203.024 | 3886019316.6773 | 3890207223.7319 | 3894471973.1177 | 3898813564.8348 | 3903231998.8832 | 3907708064.6801 | 3912280183.391 | 3916929144.4332 | 3921654947.8067 | 3926457593.5115 | 3931202607.4678 | 3935966832.007 | 3940731056.5461 | 3945476070.5024 | 3950240295.0415 | 3955004519.5807 | 3959768744.1198 | 3964532968.6589 | 3969297193.1981 | 3974061417.7372 | 3978825642.2763 | 3983589866.8155 | 3988354091.3546 | 3993118315.8937
Project Marinus Stage 1 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | $ 3840 M | $ 3875 M | $ 3887 M | $ 3899 M | $ 3912 M | $ 3924 M | $ 3937 M | $ 3950 M | $ 3963 M | $ 3977 M | $ 3990 M | $ 4004 M | $ 4017 M | $ 4031 M | $ 4044 M | $ 4058 M | $ 4071 M | $ 4084 M | $ 4098 M | $ 4111 M | $ 4125 M | $ 4138 M | $ 4152 M | $ 4165 M
Project Marinus Stage 2 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | $ 2735 M | $ 2753 M | $ 2758 M | $ 2763 M | $ 2768 M | $ 2773 M | $ 2778 M | $ 2783 M | $ 2789 M | $ 2794 M | $ 2799 M | $ 2804 M | $ 2810 M | $ 2815 M | $ 2820 M | $ 2825 M | $ 2831 M | $ 2836 M | $ 2841 M | $ 2846 M | $ 2847 M | $ 2849 M | $ 2849 M
Progressive Change | bar: 2032-33 to 2052-53
Central Queensland (CQ) to North Queensland (NQ) | bar: 2032-33 to 2052-53
Flow Path | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
CQ-NQ | CQ-NQ Option 1 | 1239107366.22 | 1241358548.8432 | 1259875321.5268 | 1278619518.4222 | 1293512905.8743 | 1296904941.2371 | 1298705742.2225 | 1300554037.0581 | 1302443986.9435 | 1304372099.951 | 1306335880.9211 | 1308335694.5696 | 1310371540.8964 | 1312443419.9015 | 1314542323.4154 | 1316686267.7773 | 1318866244.8175 | 1321082254.536 | 1323334296.9329 | 1325559314.821 | 1327793340.8788 | 1330027366.9365 | 1332252384.8246 | 1334486410.8823 | 1336720436.9401 | 1338954462.9978 | 1341188489.0555 | 1343422515.1132 | 1345656541.171 | 1347890567.2287 | 1350124593.2864 | 1352358619.3441 | 1354592645.4018
| CQ-NQ Option 2 | 4184372728.92 | 4201489765.021 | 4257901259.9109 | 4319984498.1611 | 4366305081.8534 | 4374737788.9829 | 4379237597.167 | 4383856082.262 | 4388578654.2586 | 4393396587.4645 | 4398303647.1568 | 4403300744.6416 | 4408387879.919 | 4413565052.9888 | 4418809754.4031 | 4424167003.058 | 4429614289.5054 | 4435151613.7454 | 4440778975.7778 | 4446338809.4659 | 4451921152.6021 | 4457503495.7383 | 4463063329.4264 | 4468645672.5626 | 4474228015.6988 | 4479810358.835 | 4485392701.9712 | 4490975045.1074 | 4496557388.2436 | 4502139731.3798 | 4507722074.516 | 4513304417.6522 | 4518886760.7884
Central Queensland (CQ) to Gladstone Grid (GG) | bar: 2032-33 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
CQ-GG | CQ-GG Option 1 | 2021-22: Preparatory Activites- See note
Southern Queensland (SQ) to Central Queensland (CQ) | bar: 2021-22; 2032-33 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
SQ-CQ | SQ-CQ Option 1 | 819110031.49 | 821517020.16 | 833816930.59 | 846920987.02 | 857326971.33 | 858672413.8 | 860061218.56 | 861486651.3 | 862944209.03 | 864431198.74 | 865945696.11 | 867487982.43 | 869058057.69 | 870655921.89 | 872274627.8 | 873928069.89 | 875609300.92 | 877318320.89 | 879055129.8 | 880771097.01 | 882494011.46 | 884216925.9 | 885932893.11 | 887655807.55 | 889378722 | 891101636.44 | 892824550.89 | 894547465.33 | 896270379.77 | 897993294.22 | 899716208.66 | 901439123.11 | 903162037.55
| SQ-CQ Option 2 | 77274371.17 | 77448985.4071 | 79266602.937 | 80714734.148 | 81339595.6975 | 81352618.6698 | 81358666.903 | 81364874.6565 | 81371222.3055 | 81377698.1301 | 81384293.7544 | 81391010.3992 | 81397848.0648 | 81404806.7509 | 81411856.2025 | 81419056.9299 | 81426378.678 | 81433821.4466 | 81441385.2359 | 81448858.2597 | 81456361.5387 | 81463864.8177 | 81471337.8415 | 81478841.1205 | 81486344.3994 | 81493847.6784 | 81501350.9574 | 81508854.2364 | 81516357.5153 | 81523860.7943 | 81531364.0733 | 81538867.3523 | 81546370.6312
| SQ-CQ Option 3 | 2021-22: Non-Network Augmentation
| CQ-SQ Option 4 | 1852638866.62 | 1873845311.2944 | 1912297233.7646 | 1946888065.3554 | 1969375333.3089 | 1972930216.9022 | 1975217411.2026 | 1977564927.423 | 1979965349.6611 | 1982414242.7682 | 1984908437.7154 | 1987448397.7076 | 1990034122.7447 | 1992665612.8267 | 1995331426.6924 | 1998054446.8642 | 2000823232.0809 | 2003637782.3425 | 2006498097.649 | 2009324089.1718 | 2012161521.9559 | 2014998954.74 | 2017824946.2628 | 2020662379.0469 | 2023499811.8309 | 2026337244.615 | 2029174677.3991 | 2032012110.1831 | 2034849542.9672 | 2037686975.7512 | 2040524408.5353 | 2043361841.3194 | 2046199274.1034
| CQ-SQ Option 5 | 3286871982.09 | 3300251876.3053 | 3349692819.27 | 3402908138.015 | 3440069815.0958 | 3446757699.0851 | 3450729504.0424 | 3454806060.4951 | 3458974490.3292 | 3463227091.8391 | 3467558361.7873 | 3471969104.5785 | 3476459320.2128 | 3481029008.6902 | 3485658301.8 | 3490386935.9635 | 3495195042.9702 | 3500082622.8199 | 3505049675.5128 | 3509957123.5733 | 3514884439.8446 | 3519811756.1158 | 3524719204.1764 | 3529646520.4476 | 3534573836.7189 | 3539501152.9902 | 3544428469.2615 | 3549355785.5328 | 3554283101.8041 | 3559210418.0753 | 3564137734.3466 | 3569065050.6179 | 3573992366.8892
Northern NSW (NNSW) to Southern Queensland (SQ) | bar: 2032-33 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NNSW-SQ | NNSW–SQ Option 1 | 2021-22: Preparatory Activites- See note below
NNSW–SQ Option 2
| NNSW–SQ Option 3 | 2021-22: Non-Network Augmentation
| NNSW–SQ Option 4 | 4278938560.29 | 4332575636.9924 | 4418406436.2934 | 4503298550.6955 | 4559966617.3236 | 4576724440.3123 | 4582640923.9121 | 4588713447.4457 | 4594922827.5423 | 4601257591.431 | 4607709541.522 | 4614279876.0184 | 4620968594.9201 | 4627775698.2271 | 4634671589.8381 | 4641715461.9558 | 4648877718.4788 | 4656158359.4072 | 4663557384.7409 | 4670867621.7706 | 4678207454.9016 | 4685547288.0327 | 4692857525.0624 | 4700197358.1934 | 4707537191.3245 | 4714877024.4555 | 4722216857.5866 | 4729556690.7176 | 4736896523.8486 | 4744236356.9797 | 4751576190.1107 | 4758916023.2418 | 4766255856.3728
| NNSW–SQ Option 5 | 2021-22: Preparatory Activites- See note
Central NSW to Northern NSW | bar: 2032-33 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
CNSW-NNSW | CNSW-NNSW Option 1 | 1834410577.13 | 1839984585.4914 | 1870490675.9238 | 1901016121.539 | 1920883577.9873 | 1928540541.7841 | 1930504249.2044 | 1932519746.9395 | 1934580668.0351 | 1936683204.5769 | 1938824635.7203 | 1941005359.1783 | 1943225374.9509 | 1945484683.038 | 1947773460.361 | 1950111353.0772 | 1952488538.1079 | 1954905015.4533 | 1957360785.1132 | 1959787085.5371 | 1962223209.0397 | 1964659332.5423 | 1967085632.9663 | 1969521756.4689 | 1971957879.9715 | 1974394003.4741 | 1976830126.9767 | 1979266250.4793 | 1981702373.9819 | 1984138497.4845 | 1986574620.9872 | 1989010744.4898 | 1991446867.9924
| CNSW-NNSW Option 2 | 1492549482.75 | 1498368669.1638 | 1522299684.6068 | 1547240613.4524 | 1564450054.237 | 1571991063.1989 | 1573893564.3584 | 1575846241.6481 | 1577842926.4764 | 1579879929.6413 | 1581954615.1334 | 1584067368.2491 | 1586218188.9885 | 1588407077.3517 | 1590624516.4326 | 1592889540.0432 | 1595192631.2774 | 1597533790.1354 | 1599913016.6171 | 1602263692.381 | 1604623885.0508 | 1606984077.7207 | 1609334753.4846 | 1611694946.1544 | 1614055138.8242 | 1616415331.4941 | 1618775524.1639 | 1621135716.8337 | 1623495909.5035 | 1625856102.1734 | 1628216294.8432 | 1630576487.513 | 1632936680.1829
| CNSW-NNSW Option 3 | 2451577025.7 | 2463020830.0123 | 2502997770.0901 | 2545275893.4835 | 2575674869.1369 | 2591494238.8847 | 2595334801.84 | 2599276654.8232 | 2603307345.5048 | 2607419426.4837 | 2611607576.4357 | 2615872573.1758 | 2620214416.704 | 2624633107.0204 | 2629109432.4278 | 2633681816.3203 | 2638331047.0009 | 2643057124.4697 | 2647860048.7266 | 2652605337.8924 | 2657369838.7552 | 2662134339.618 | 2666879628.7838 | 2671644129.6466 | 2676408630.5094 | 2681173131.3722 | 2685937632.235 | 2690702133.0978 | 2695466633.9606 | 2700231134.8235 | 2704995635.6863 | 2709760136.5491 | 2714524637.4119
| CNSW-NNSW Option 4 | 2544205834.44 | 2570694957.3285 | 2622183967.2558 | 2666780915.3469 | 2694522775.777 | 2703050596.3897 | 2705180753.0017 | 2707367089.7981 | 2709602700.1078 | 2711883453.321 | 2714206397.963 | 2716571965.4424 | 2718980155.7593 | 2721430968.9136 | 2723913749.1961 | 2726449808.0254 | 2729028489.6921 | 2731649794.1964 | 2734313721.5381 | 2736945681.7517 | 2739588297.6746 | 2742230913.5976 | 2744862873.8112 | 2747505489.7341 | 2750148105.6571 | 2752790721.58 | 2755433337.503 | 2758075953.426 | 2760718569.3489 | 2763361185.2719 | 2766003801.1948 | 2768646417.1178 | 2771289033.0408
| CNSW-NNSW Option 5 | 2795731374.64 | 2824605711.5108 | 2880109217.9138 | 2929211740.0852 | 2960356667.7182 | 2971207328.6974 | 2973750098.4803 | 2976359930.683 | 2979028580.6809 | 2981751117.8174 | 2984524018.8975 | 2987347798.8966 | 2990222457.8146 | 2993147995.6514 | 2996111692.6774 | 2999138988.3521 | 3002217162.9457 | 3005346216.4581 | 3008526148.8895 | 3011667922.1317 | 3014822415.1036 | 3017976908.0755 | 3021118681.3177 | 3024273174.2896 | 3027427667.2615 | 3030582160.2334 | 3033736653.2053 | 3036891146.1772 | 3040045639.1492 | 3043200132.1211 | 3046354625.093 | 3049509118.0649 | 3052663611.0368
Central NSW (CNSW) to Sydney, Newcastle and Wollongong (SNW) | bar: 2032-33 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
CNSW-SNW | CNSW-SNW Option 1 | $ 1091 M | $ 1099 M | $ 1118 M | $ 1139 M | $ 1154 M | $ 1160 M | $ 1162 M | $ 1164 M | $ 1166 M | $ 1169 M | $ 1171 M | $ 1174 M | $ 1176 M | $ 1179 M | $ 1181 M | $ 1184 M | $ 1187 M | $ 1189 M | $ 1192 M | $ 1195 M | $ 1198 M | $ 1200 M | $ 1203 M | $ 1206 M | $ 1208 M | $ 1211 M | $ 1214 M | $ 1217 M | $ 1219 M | $ 1222 M | $ 1225 M | $ 1228 M | $ 1230 M
| CNSW-SNW Option 2 | 2021-22: Preparatory Activites- See note
| CNSW-SNW Option 2b | $ 891 M | $ 893 M | $ 893 M | $ 900 M | $ 912 M | $ 915 M | $ 917 M | $ 919 M | $ 921 M | $ 954 M | $ 959 M | $ 964 M | $ 969 M | $ 974 M | $ 979 M | $ 984 M | $ 990 M | $ 995 M | $ 1001 M | $ 1006 M | $ 1012 M | $ 1017 M | $ 1022 M | $ 1028 M | $ 1033 M | $ 1039 M | $ 1044 M | $ 1050 M | $ 1055 M | $ 1060 M | $ 1066 M | $ 1071 M | $ 1077 M
| CNSW-SNW Option 2d | n/a | $ 221 M | $ 226 M | $ 230 M | $ 232 M | $ 232 M | $ 232 M | $ 232 M | $ 232 M | $ 242 M | $ 243 M | $ 244 M | $ 245 M | $ 246 M | $ 247 M | $ 248 M | $ 249 M | $ 250 M | $ 251 M | $ 252 M | $ 253 M | $ 254 M | $ 255 M | $ 256 M | $ 257 M | $ 258 M | $ 259 M | $ 260 M | $ 261 M | $ 262 M | $ 263 M | $ 264 M | $ 265 M
| CNSW-SNW Option 3 | 2038231925.88 | 2051462544.5935 | 2087056111.3183 | 2127222399.7032 | 2157383502.2575 | 2169876774.1494 | 2174941989.7328 | 2180140794.2915 | 2185456764.2837 | 2190880077.8913 | 2196403716.8181 | 2202028706.9179 | 2207755048.1906 | 2213582740.6364 | 2219486446.4618 | 2225516841.2535 | 2231648587.2181 | 2237881684.3557 | 2244216132.6662 | 2250474567.5971 | 2256758340.3212 | 2263042113.0452 | 2269300547.9761 | 2275584320.7002 | 2281868093.4242 | 2288151866.1483 | 2294435638.8724 | 2300719411.5965 | 2307003184.3206 | 2313286957.0446 | 2319570729.7687 | 2325854502.4928 | 2332138275.2169
| CNSW-SNW Option 4 | 2470340313.03 | 2488985096.58 | 2532322682.6794 | 2583182159.4332 | 2623553883.4714 | 2642471129.232 | 2649888578.4375 | 2657501653.6368 | 2665286304.941 | 2673228148.8646 | 2681316908.2364 | 2689554085.2114 | 2697939679.7895 | 2706473691.9707 | 2715119017.3543 | 2723949864.7419 | 2732929129.7326 | 2742056812.3264 | 2751332912.5234 | 2760497699.518 | 2769699590.9135 | 2778901482.3089 | 2788066269.3035 | 2797268160.699 | 2806470052.0944 | 2815671943.4898 | 2824873834.8852 | 2834075726.2807 | 2843277617.6761 | 2852479509.0715 | 2861681400.467 | 2870883291.8624 | 2880085183.2578
| H-Newcastle (This is not an alternative option to supply SNW) | 1419595460.39 | 1423876905.0336 | 1444318279.0159 | 1464859345.2531 | 1477106893.3942 | 1481705493.97 | 1482036717.3215 | 1482376676.3226 | 1482724296.9628 | 1483078937.0126 | 1483440137.4994 | 1483807965.518 | 1484182421.0685 | 1484563504.1509 | 1484949557.8822 | 1485343896.0283 | 1485744861.7063 | 1486152454.9161 | 1486566675.6578 | 1486975925.7506 | 1487386832.7264 | 1487797739.7022 | 1488206989.795 | 1488617896.7708 | 1489028803.7466 | 1489439710.7223 | 1489850617.6981 | 1490261524.6739 | 1490672431.6497 | 1491083338.6254 | 1491494245.6012 | 1491905152.577 | 1492316059.5528
| H-Dapto (This is not an alternative option to supply SNW) | 1663298988.73 | 1672479189.447 | 1700991413.6333 | 1733805466.6957 | 1759029917.3541 | 1769892137.5597 | 1774353907.6959 | 1778933351.5619 | 1783616002.4415 | 1788393208.4125 | 1793258787.47 | 1798213643.2075 | 1803257775.6249 | 1808391184.7222 | 1813591551.3296 | 1818903513.7868 | 1824304752.9241 | 1829795268.7412 | 1835375061.2384 | 1840887896.2255 | 1846423050.3827 | 1851958204.5398 | 1857471039.527 | 1863006193.6842 | 1868541347.8413 | 1874076501.9985 | 1879611656.1556 | 1885146810.3128 | 1890681964.4699 | 1896217118.6271 | 1901752272.7842 | 1907287426.9414 | 1912822581.0986
| CNSW-SNW Option 6a | 1832882856.49 | 1844970117.5375 | 1877018040.5512 | 1914424933.6747 | 1944076914.3214 | 1957891889.6633 | 1963381968.4839 | 1969016841.3391 | 1974778707.4567 | 1980656920.8035 | 1986643874.7294 | 1992740681.021 | 1998947339.6781 | 2005263850.7009 | 2011662750.9978 | 2018198966.7518 | 2024845034.8714 | 2031600955.3566 | 2038466728.2075 | 2045250111.7841 | 2052060958.4521 | 2058871805.1201 | 2065655188.6967 | 2072466035.3648 | 2079276882.0328 | 2086087728.7008 | 2092898575.3688 | 2099709422.0368 | 2106520268.7049 | 2113331115.3729 | 2120141962.0409 | 2126952808.7089 | 2133763655.3769
| CNSW-SNW Option 6b | 1410776271.14 | 1420984546.1967 | 1446514378.5297 | 1474659658.8976 | 1495226896.2343 | 1503407119.3213 | 1506685316.5082 | 1510049972.0736 | 1513490456.998 | 1517000414.3387 | 1520575302.0686 | 1524215784.0688 | 1527921860.3392 | 1531693530.88 | 1535514397.1234 | 1539417256.2046 | 1543385709.5562 | 1547419757.178 | 1551519399.0701 | 1555569845.2594 | 1559636690.0164 | 1563703534.7733 | 1567753980.9627 | 1571820825.7196 | 1575887670.4766 | 1579954515.2335 | 1584021359.9905 | 1588088204.7474 | 1592155049.5044 | 1596221894.2613 | 1600288739.0182 | 1604355583.7752 | 1608422428.5321
Southern NSW to Central NSW | bar: 2032-33 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
SNSW-CNSW | SNSW-CNSW Option 1 (HumeLink) | 2021-22: Actionable ISP Project - See note below
| SNSW-CNSW Option 2 | 2450117931.33 | 2477575046.4418 | 2527144244.2174 | 2570707259.5764 | 2597701736.7797 | 2605383061.3987 | 2607459821.2587 | 2609591353.1108 | 2611770923.3031 | 2613994504.8153 | 2616259220.1321 | 2618565489.8584 | 2620913313.9941 | 2623302692.5394 | 2625723236.8917 | 2628195724.2559 | 2630709766.0296 | 2633265362.2128 | 2635862512.8055 | 2638428497.591 | 2641004870.9789 | 2643581244.3668 | 2646147229.1524 | 2648723602.5403 | 2651299975.9282 | 2653876349.3161 | 2656452722.704 | 2659029096.0919 | 2661605469.4798 | 2664181842.8678 | 2666758216.2557 | 2669334589.6436 | 2671910963.0315
| SNSW-CNSW Option 3 | 3013855444.3 | 3031187074.9681 | 3076025895.4739 | 3127932407.9652 | 3167568719.3084 | 3186483692.9918 | 3192078233.5515 | 3197820323.2579 | 3203691822.5451 | 3209681882.9794 | 3215782752.9303 | 3221995565.449 | 3228320320.5357 | 3234757018.1903 | 3241277672.7708 | 3247938255.5612 | 3254710780.9195 | 3261595248.8457 | 3268591659.3398 | 3275504112.908 | 3282444552.1182 | 3289384991.3283 | 3296297444.8965 | 3303237884.1067 | 3310178323.3168 | 3317118762.527 | 3324059201.7371 | 3330999640.9473 | 3337940080.1575 | 3344880519.3676 | 3351820958.5778 | 3358761397.7879 | 3365701836.9981
| SNSW-CNSW Option 4 | 2369893492.41 | 2383644371.4131 | 2420652091.3886 | 2463812802.3332 | 2498556401.1515 | 2518817838.6187 | 2524546943.8429 | 2530427147.224 | 2536439872.8163 | 2542574011.2853 | 2548821624.5818 | 2555183872.9846 | 2561660756.4938 | 2568252275.1094 | 2574929770.0547 | 2581750558.8829 | 2588685982.8176 | 2595736041.8585 | 2602900736.0059 | 2609979453.8234 | 2617086830.4176 | 2624194207.0117 | 2631272924.8293 | 2638380301.4235 | 2645487678.0176 | 2652595054.6118 | 2659702431.2059 | 2666809807.8001 | 2673917184.3942 | 2681024560.9884 | 2688131937.5825 | 2695239314.1767 | 2702346690.7708
Victoria to Southern NSW | bar: 2032-33 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
VIC-SNSW | VIC-SNSW Option 1 - VNI West (Kerang) | 2021-22: Actionable ISP Project - See note below
Tasmania to Victoria | bar: 2032-33 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
TAS-VIC | TAS-VIC Option 1 (Marinus Link stage 1) | 2021-22: Actionable ISP Project - See note below
TAS-VIC Option 2 (Marinus Link stage 2)
Victoria to South East South Australia | bar: 2032-33 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
VIC-SESA | VIC-SESA Option 1 | 892159575.75 | 894733267.0364 | 909733866.6606 | 925500161.3645 | 937884944.8111 | 941256680.7923 | 943182052.2708 | 945158202.9843 | 947178890.2605 | 949240380.5799 | 951340006.1937 | 953478157.0482 | 955654833.1433 | 957870034.479 | 960114129.7452 | 962406381.5622 | 964737158.6198 | 967106460.918 | 969514288.4568 | 971893222.0652 | 974281786.9837 | 976670351.9022 | 979049285.5106 | 981437850.4291 | 983826415.3476 | 986214980.2661 | 988603545.1846 | 990992110.1031 | 993380675.0217 | 995769239.9402 | 998157804.8587 | 1000546369.7772 | 1002934934.6957
| VIC-SESA Option 2 | 1362860559.09 | 1369071037.5159 | 1389832987.0404 | 1412766264.9812 | 1429903851.4189 | 1433764522.032 | 1436010106.9142 | 1438314916.2879 | 1440671669.2425 | 1443076011.237 | 1445524830.9355 | 1448018583.1055 | 1450557267.7471 | 1453140884.8602 | 1455758201.3269 | 1458431683.383 | 1461150097.9107 | 1463913444.9099 | 1466721724.3806 | 1469496304.4977 | 1472282117.7327 | 1475067930.9677 | 1477842511.0848 | 1480628324.3197 | 1483414137.5547 | 1486199950.7897 | 1488985764.0246 | 1491771577.2596 | 1494557390.4946 | 1497343203.7295 | 1500129016.9645 | 1502914830.1995 | 1505700643.4345
South East South Australia to Central South Australia | bar: 2031-32 to 2052-53
Flow path | Option Name | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
SESA-CSA | SESA-CSA Option 1 | 1807467832.2 | 1816592456.7582 | 1846020762.1435 | 1880268010.9392 | 1907632793.8116 | 1914294315.927 | 1919101944.0859 | 1924036367.5101 | 1929081998.1474 | 1934229513.4123 | 1939472252.0571 | 1944811187.7413 | 1950246320.4649 | 1955777650.2278 | 1961381127.7702 | 1967104851.6118 | 1972924772.4928 | 1978840890.4131 | 1984853205.3728 | 1990793372.553 | 1996757588.993 | 2002721805.433 | 2008661972.6132 | 2014626189.0532 | 2020590405.4932 | 2026554621.9332 | 2032518838.3732 | 2038483054.8132 | 2044447271.2532 | 2050411487.6932 | 2056375704.1332 | 2062339920.5732 | 2068304137.0132
Note. AEMO received TNSP cost estimates for actionable projects and projects with preparatory activities from most TNSPs during June 2023 | bar: 2032-33 to 2052-53
Preparatory activities | bar: 2031-32 to 2052-53
Flow path |  | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
500kV QNI Connect (NSW works) |  | 2658844000 | 2668887131.1932 | 2706890589.3579 | 2749766531.5973 | 2781079636.8686 | 2794499239.3594 | 2798326837.3793 | 2802255383.5959 | 2806272467.5699 | 2810370667.0665 | 2814544678.7612 | 2818795277.8264 | 2823122464.2621 | 2827526238.0684 | 2831987452.4026 | 2836544400.9499 | 2841177936.8678 | 2845888060.1563 | 2850674770.8153 | 2855404040.9464 | 2860152457.9201 | 2864900874.8938 | 2869630145.0249 | 2874378561.9987 | 2879126978.9724 | 2883875395.9461 | 2888623812.9198 | 2893372229.8936 | 2898120646.8673 | 2902869063.841 | 2907617480.8147 | 2912365897.7885 | 2917114314.7622
330kV QNI single circuit (NSW works) |  | 963705000 | 968980305.2394 | 985160067.7897 | 1004040506.9748 | 1020214441.7978 | 1032253652.4228 | 1035301267.497 | 1038429259.6139 | 1041627747.3572 | 1044890821.0352 | 1048214258.0126 | 1051598675.4851 | 1055044073.4526 | 1058550451.9151 | 1062102565.7488 | 1065730905.2012 | 1069420225.1487 | 1073170525.5912 | 1076981806.5286 | 1080747352.0948 | 1084528142.7848 | 1088308933.4748 | 1092074479.041 | 1095855269.731 | 1099636060.4209 | 1103416851.1109 | 1107197641.8008 | 1110978432.4908 | 1114759223.1808 | 1118540013.8707 | 1122320804.5607 | 1126101595.2507 | 1129882385.9406
330kV QNI double circuit (NSW works) |  | 1308904000 | 1315802850.7246 | 1337170207.1799 | 1361484767.1993 | 1366942815.3519 | 1377769960.3686 | 1381128749.8185 | 1384576123.155 | 1388101190.0141 | 1391697437.2964 | 1395360211.233 | 1399090192.0309 | 1402887379.6899 | 1406751774.2102 | 1410666573.8763 | 1414665382.119 | 1418731397.223 | 1422864619.1881 | 1427065048.0145 | 1431215071.6949 | 1435381897.0907 | 1439548722.4864 | 1443698746.1669 | 1447865571.5627 | 1452032396.9584 | 1456199222.3542 | 1460366047.7499 | 1464532873.1457 | 1468699698.5415 | 1472866523.9372 | 1477033349.333 | 1481200174.7287 | 1485367000.1245
Sydney Southern Ring |  | 1550000000 | 1556043175.8181 | 1580895332.725 | 1606796276.1493 | 1624668134.6869 | 1632499408.642 | 1634475139.9871 | 1636502978.8186 | 1638576519.1063 | 1640691929.6452 | 1642846472.9617 | 1645040549.1832 | 1647274158.3095 | 1649547300.3407 | 1651850092.0505 | 1654202299.8915 | 1656594040.6374 | 1659025314.2881 | 1661496120.8438 | 1663937277.7208 | 1666388317.824 | 1668839357.9272 | 1671280514.8041 | 1673731554.9073 | 1676182595.0106 | 1678633635.1138 | 1681084675.217 | 1683535715.3202 | 1685986755.4234 | 1688437795.5266 | 1690888835.6298 | 1693339875.733 | 1695790915.8362
500kV QNI Connect (QLD works) |  | 2600000000 | 2616423540.6527 | 2655090312.8631 | 2702373413.2722 | 2740823554.5893 | 2749991861.5653 | 2756387556.2077 | 2762951929.4414 | 2769664244.1106 | 2776512098.1315 | 2783486629.9605 | 2790589134.8505 | 2797819612.8016 | 2805178063.8137 | 2812632494.6217 | 2820246891.7561 | 2827989261.9515 | 2835859605.208 | 2843857921.5255 | 2851760258.0473 | 2859694587.8343 | 2867628917.6214 | 2875531254.1432 | 2883465583.9302 | 2891399913.7172 | 2899334243.5043 | 2907268573.2913 | 2915202903.0783 | 2923137232.8654 | 2931071562.6524 | 2939005892.4394 | 2946940222.2265 | 2954874552.0135
330kV QNI single circuit (QLD works) |  | 930000000 | 934101741.0348 | 950717237.2284 | 969902118.1873 | 986627189.3598 | 992150918.6586 | 995564298.7557 | 999067702.4837 | 1002650062.5012 | 1006304759.8524 | 1010027065.1056 | 1013817669.5379 | 1017676573.149 | 1021603775.9392 | 1025582203.1135 | 1029646004.2616 | 1033778104.5886 | 1037978504.0946 | 1042247202.7795 | 1046464677.0802 | 1050699226.1757 | 1054933775.2711 | 1059151249.5718 | 1063385798.6673 | 1067620347.7627 | 1071854896.8582 | 1076089445.9536 | 1080323995.0491 | 1084558544.1445 | 1088793093.24 | 1093027642.3354 | 1097262191.4309 | 1101496740.5263
330kV QNI double circuit (QLD works) |  | 1210000000 | 1214094171.4861 | 1234734221.4502 | 1257823613.2808 | 1264845826.5548 | 1269992066.1256 | 1273535669.9346 | 1277172731.8621 | 1280891762.337 | 1284685889.8839 | 1288550204.639 | 1292485424.252 | 1296491548.7229 | 1300568578.0516 | 1304698786.0238 | 1308917625.0683 | 1313207368.9708 | 1317568017.7311 | 1321999571.3493 | 1326377946.3241 | 1330774047.5134 | 1335170148.7026 | 1339548523.6774 | 1343944624.8667 | 1348340726.056 | 1352736827.2452 | 1357132928.4345 | 1361529029.6238 | 1365925130.8131 | 1370321232.0023 | 1374717333.1916 | 1379113434.3809 | 1383509535.5701
CQ-GG |  | 1300000000 | 1304437596.7393 | 1325457018.0761 | 1346619963.7206 | 1362156413.8865 | 1365406502.3708 | 1367150524.5532 | 1368940543.134 | 1370770903.3769 | 1372638223.4583 | 1374540086.9139 | 1376476846.9466 | 1378448503.5566 | 1380455056.7437 | 1382487782.3637 | 1384564128.7051 | 1386675371.6237 | 1388821511.1195 | 1391002547.1924 | 1393157410.8325 | 1395320998.6168 | 1397484586.4012 | 1399639450.0412 | 1401803037.8256 | 1403966625.6099 | 1406130213.3943 | 1408293801.1786 | 1410457388.963 | 1412620976.7474 | 1414784564.5317 | 1416948152.3161 | 1419111740.1004 | 1421275327.8848
Actionable ISP projects | bar: 2031-32 to 2052-53
Flow path |  | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
VNI West |  | 3614000000 | 3628160087.8308 | 3684619600.6937 | 3742616230.3809 | 3781193300.4727 | 3792888786.2887 | 3796729126.4046 | 3800670750.9283 | 3804701207.6858 | 3808813050.3204 | 3813000957.3749 | 3817265706.7608 | 3821607298.4779 | 3826025732.5263 | 3830501798.3231 | 3835073917.0341 | 3839722878.0763 | 3844448681.4498 | 3849251327.1546 | 3853996341.1109 | 3858760565.65 | 3863524790.1891 | 3868269804.1455 | 3873034028.6846 | 3877798253.2237 | 3882562477.7629 | 3887326702.302 | 3892090926.8411 | 3896855151.3803 | 3901619375.9194 | 3906383600.4585 | 3911147824.9977 | 3915912049.5368
Humelink |  | #N/A | #N/A | #N/A | #N/A | #N/A | 4892000000 | 4899558139.4147 | 4907315615.2229 | 4915247921.727 | 4923343158.5516 | 4931585388.424 | 4939978851.8721 | 4948523548.8958 | 4957219479.4952 | 4966028835.2762 | 4975027233.0269 | 4984176864.3532 | 4993477729.2551 | 5002929827.7326 | 5012268501.0285 | 5021644982.7182 | 5031021464.4079 | 5040360137.7038 | 5049736619.3935 | 5059113101.0833 | 5068489582.773 | 5077866064.4627 | 5087242546.1525 | 5096619027.8422 | 5105995509.5319 | 5115371991.2217 | 5124748472.9114 | 5134124954.6012
Project Marinus Stage 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | $ 3840 M | $ 3866 M | $ 3876 M | $ 3885 M | $ 3894 M | $ 3904 M | $ 3913 M | $ 3923 M | $ 3933 M | $ 3943 M | $ 3954 M | $ 3964 M | $ 3974 M | $ 3984 M | $ 3994 M | $ 4004 M | $ 4014 M | $ 4024 M | $ 4034 M | $ 4044 M | $ 4055 M | $ 4065 M | $ 4075 M | $ 4085 M
Project Marinus Stage 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | $ 2735 M | $ 2750 M | $ 2754 M | $ 2758 M | $ 2763 M | $ 2767 M | $ 2771 M | $ 2775 M | $ 2780 M | $ 2784 M | $ 2788 M | $ 2793 M | $ 2797 M | $ 2801 M | $ 2806 M | $ 2810 M | $ 2814 M | $ 2819 M | $ 2823 M | $ 2827 M | $ 2832 M | $ 2836 M | $ 2849 M

## Transmission Reliability
Go to Assumptions Summary
Transmission Reliability
AEMO applies the following rates to probabilistic modelling of single credible contingencies and reclassifications on 4 lines that materially contribute to inter-regional transfer capability.
These rates apply to Reliability Forecast modelling only
Transmission outage rates |  | Unplanned Outage Rate (%) |  | Mean Time to Repair
Line/Flowpath | Implementation | single credible contingency | reclassification events | single credible contingency | reclassification events
Mortlake – Heywood – South East (V-SA) | Static annual FOR | 0.09% | 0.01% | 7.8 | 4.7
Murraylink | Static annual FOR | 0.07% | NA | 12.4 | NA
Basslink | Static annual FOR | 5.39% | NA | 213.9 | NA
Liddell – Muswellbrook – Tamworth – Armidale – Dumaresq – Bulli Creek (QNI) | Static annual FOR | 0.19% | 1.4% | 14.5 | 4.3

## Maximum capacity
Go to Assumptions Summary
Generator nameplate capacity
The maximum capacities of each existing and committed generating unit are based on February 2024 Generation Information. These values describe the nameplate capacity for the purpose of calculating operational costs. The operation/dispatch generation limits for each power station are provided by the seasonal ratings, not the below nameplate capacities.
https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information
Max capacities of each new entrant generation technologies are sourced from Aurecon 2022 Costs and Technical Parameter Review.
Existing generators |  |  | Committed projects 1 |  |  |  | Anticipated projects 2 |  |  |  | Existing, Committed and Anticipated batteries 3 | [5 empty] | Additional projects 5 | [5 empty] | New generation technologies
Generator | Region | Installed capacity (MW) | Generator | Region | Installed capacity (MW) | Commissioning date | Generator | Region | Installed capacity (MW) | Indicative commissioning date | Storage | Region | Installed capacity (MW) | Energy (MWh) | Indicative commissioning date | Project status | Policy | Project | Region | Installed capacity (MW) | Energy (MWh) | Indicative commissioning date | Generator type | Unit size (MW) | Number of units | Total plant size (MW)
Bayswater | NSW | 2715 | Kurri Kurri OCGT | NSW | 750 | 2024-12-01 | SA Hydrogen Turbine | SA | 200 | 2025-12-01 | Adelaide Desalination Plant BESS | SA | 6.27 | 12.6 |  | Existing | LTESA Round 1 | Coppabella Wind Farm | NSW | 289.8 |  | 2025-07-01 | OCGT (small GT) | 49 | 5 | 245
Callide B | QLD | 700 | Tallawarra B* | NSW | 320 | 2024-02-01 | Borumba | QLD | 1998 | 2031-09-01 | Aldoga BESS Stage 1 | QLD | 400 | 400 | 2025-11-01 | Anticipated | VRET2 | Derby Solar Project BESS | VIC | 85 | 100 | 2025-07-01 | OCGT (large GT) | 265 | 1 | 265
Callide C | QLD | 844 | Kidston | QLD | 250 | 2025-02-01 | Aramara Solar Farm | QLD | 101.4 | 2026-06-01 | Ballarat Energy Storage System | VIC | 30 | 30 |  | Existing | VRET2 | Fulham Solar Farm BESS | VIC | 64.8 | 116 | 2025-07-01 | CCGT | 409 | 1 | 409
Eraring | NSW | 2880 | Snowy 2.0 | NSW | 2200 | 2028-12-01 | Banksia Solar Farm | QLD | 60 | 2025-09-01 | Blyth BESS | SA | 200 | 400 | 2024-12-01 | Anticipated | VRET2 | Fulham Solar Farm | VIC | 100.8 |  | 2025-07-01 | CCGT with CCS | 409 | 1 | 409
Gladstone | QLD | 1680 | Girgarre Solar Farm | VIC | 93.48 | 2024-12-01 | Culcairn Solar Farm | NSW | 349.98 | 2025-07-01 | Bolivar Waste Water Treatment BESS | SA | 2.46 | 5.04 |  | Existing | LTESA Round 1 | Goulburn River BESS | NSW | 49 | 392 | 2025-07-01 | Biomass | 30 | 1 | 30
Kogan Creek | QLD | 744 | Glenrowan Solar Farm | VIC | 126.5 | 2024-05-01 | Cultana Solar Farm | SA | 357.45 | 2026-07-01 | Bouldercombe Battery project | QLD | 50 | 100 |  | Existing | VRET2 | Horsham Solar Farm BESS | VIC | 50.01 | 100 | 2025-07-01 | Large scale Solar PV | -
Millmerran | QLD | 852 | Mannum Solar Farm 2* | SA | 29.99 | 2024-02-01 | Derby Solar Farm | VIC | 95.1 | 2025-03-01 | Broken Hill BESS | NSW | 50 | 50 | 2024-01-01 | Committed | VRET2 | Kiamal Solar Farm – Stage 2 | VIC | 150.04 |  | 2026-04-01 | Solar Thermal (15hrs storage) | -
Mt Piper | NSW | 1390 | Metz Solar Farm | NSW | 135 | 2023-04-01 | Frasers Solar Farm | VIC | 77 | 2025-10-01 | Bulgana Green Power Hub BESS | VIC | 20 | 34 |  | Existing | VRET2 | Kiamal Solar Farm – Stage 2 BESS | VIC | 150.04 | 300 | 2026-04-01 | Battery storage (1hr storage) | -
Stanwell | QLD | 1460 | Riverina Solar Farm | NSW | 32.4 | 2025-06-01 | Horsham Solar Farm | VIC | 118.8 | 2025-07-01 | Bungama Solar BESS | SA | 150 | 300 | 2025-10-01 | Anticipated | QEJP | Kogan Gas | QLD | 200 |  | 2026-07-01 | Battery storage (2hrs storage) | -
Tarong | QLD | 1400 | Sebastopol Solar Farm | NSW | 90 | 2023-01-01 | Lockhart Hybrid Facility - Solar | NSW | 10 | 2025-04-01 | Capital Battery | NSW | 100.32 | 200 | 2023-12-01 | Committed | LTESA Round 1 | Limondale BESS | NSW | 50 | 400 | 2025-07-01 | Battery storage (4hrs storage) | -
Tarong North | QLD | 450 | Stubbo Solar Farm | NSW | 400 | 2024-07-01 | Quorn Park Solar Farm | NSW | 96.8 | 2025-12-01 | Chinchilla BESS | QLD | 100 | 200 | 2024-02-01 | Committed | LTESA Round 1 | New England Solar Farm - stage 2 | NSW | 320 |  | 2025-07-01 | Battery Storage (8hrs storage) | -
Vales Point B | NSW | 1320 | Walla Walla Solar Farm | NSW | 303.94 | 2024-05-01 | Tamworth Solar Farm | NSW | 65 | 2026-04-01 | Christies Beach Wastewater Treatment Plant BESS | SA | 2.09 | 4.32 |  | Existing | LTESA Round 1 | Silver City Energy Storage | NSW | 200 | 1600 | 2025-07-01 | Wind | -
Loy Yang A Power Station | VIC | 2210 | Wandoan South Solar Farm - stage 1 | QLD | 160 | 2023-08-01 | Tilbuster Solar Farm | NSW | 248.82 | 2026-03-01 | Dalrymple BESS | SA | 30 | 9 |  | Existing | CIS | Smithfield BESS | NSW | 65 | 130 | 2025-07-01 | Wind - offshore (fixed) | -
Loy Yang B | VIC | 1160 | Wellington North Solar Farm (Lightsource) | NSW | 436.8 | 2024-10-01 | MacIntyre Wind Farm | QLD | 923.4 | 2024-12-01 | Darlington Point Energy Storage System | NSW | 25 | 50 |  | Existing | 5. These projects are not included in the February 2024 Generation Information as an Existing, Committed, or Anticipated project. However they are included in AEMO's modelling under the following policy frameworks: a) 2020 amendment to the National Electricity (Victoria) Act 2005 (NEVA). b) Victorian Renewable Energy Target auction (VRET2) c) New South Wales Long-Term Energy Service Agreements (LTESAs) d) Queensland Energy and Jobs Plan e) South Australia – Hydrogen Jobs Plan f) Kogan Gas is assumed to be hydrogen based gas turbines that can accomodate 100% H2 g) Capacity Investment Scheme (CIS) | [5 empty] | Wind - offshore (floating) | -
Yallourn W | VIC | 1450 | Wollar Solar Farm | NSW | 280 | 2024-06-01 | Uungula Wind Farm | NSW | 414 | 2025-07-01 | Eraring Big Battery | NSW | 460 | 920 | 2025-12-01 | Committed | [6 empty] | Pumped Hydro (8hrs storage) | -
Angaston | SA | 36 | Woolooga Solar Farm | QLD | 222.5 | 2022-09-01 | Woolsthorpe Wind Farm | VIC | 73.2 | 2025-07-01 | Gannawarra Energy Storage System | VIC | 25.33 | 50 |  | Existing | [6 empty] | Pumped Hydro (24hrs storage) | -
Bairnsdale | VIC | 94 | Wunghnu Solar Farm | VIC | 93.5 | 2024-08-01 | 2. Indicative commissioning date of projects are based on Generation Information updates from February 2024. Where information is absent, the commissioning date is assumed to be 1 July 2025. |  |  |  | Gnarwarre BESS | VIC | 290 | 550 | 2026-01-01 | Anticipated | [6 empty] | Pumped Hydro (48hrs storage) | -
Barcaldine Power Station | QLD | 37 | Clarke Creek Wind Farm | QLD | 450 | 2024-08-01 |  |  |  |  | Happy Valley Reservoir BESS | SA | 4.41 | 8.82 |  | Existing | [6 empty] | BOTN - Cethana | 750 | 1 | 750
Barker Inlet Power Station | SA | 210 | Crookwell 3 Wind Farm | NSW | 57.6 | 2024-06-01 |  |  |  |  | Hazelwood BESS | VIC | 200.07 | 162 |  | Existing | [6 empty] | Hydrogen reciprocating engines 6 | 17.6 | 12 | 211.2
Bell Bay Three | TAS | 120 | Flyers Creek Wind Farm | NSW | 145.54 | 2023-12-01 |  |  |  |  | Hornsdale Power Reserve Unit 1 | SA | 150 | 178.3 |  | Existing | [6 empty] | 6. The plant size and number of units reflect Aurecon's gas/diesel reciprocating engines, not hydrogen reciprocating engines. Current view of hydrogen reciprocating engines reflect a unit size of 2.25 MW based on its hypothetical development in 2022, and does not likely reflect unit sizes in the coming decades.
Bolivar Power Station | SA | 123.2 | Golden Plains Wind Farm East | VIC | 756.4 | 2025-08-01 |  |  |  |  | Koorangie Energy Storage System | VIC | 185 | 370 | 2025-04-01 | Anticipated
Braemar | QLD | 564 | Goyder South Wind Farm 1A | SA | 209 | 2024-06-01 |  |  |  |  | Lake Bonney BESS | SA | 25 | 52 |  | Existing
Braemar 2 Power Station | QLD | 519 | Goyder South Wind Farm 1B | SA | 203.5 | 2024-12-01 |  |  |  |  | Liddell BESS | NSW | 500 | 2000 | 2025-07-01 | Anticipated
Colongra | NSW | 724 | Hawkesdale Wind Farm | VIC | 96.6 | 2024-04-01 |  |  |  |  | Lincoln Gap Wind Farm BESS | SA | 10 | 10 | 2024-04-01 | Anticipated
Condamine A | QLD | 144.4 | Ryan Corner Wind Farm | VIC | 218.4 | 2024-03-01 |  |  |  |  | Lockhart Hybrid Facility - Battery | NSW | 10 | 20 | 2025-04-01 | Anticipated
Darling Downs | QLD | 644.5 | Rye Park Wind Farm | NSW | 396 | 2024-07-01 |  |  |  |  | Melbourne Renewable Energy Hub - Side A | VIC | 600 | 1600 | 2025-11-01 | Committed
Dry Creek GT | SA | 156 | Wambo Wind Farm | QLD | 252 | 2025-02-01 |  |  |  |  | Mornington BESS | VIC | 240 | 480 | 2026-01-01 | Anticipated
Hallett GT | SA | 276.86 | 1. Committed * projects are marked with an "*" and are assumed to commence beyond the T-1 year (at the earliest) according to the ESOO and Reliability Forecasting Methodology. | [7 empty] | Mortlake Battery | VIC | 300 | 600 | 2027-03-01 | Anticipated
Jeeralang A | VIC | 212 | [8 empty] | Mt Fox BESS | QLD | 300 | 600 | 2026-11-01 | Anticipated
Jeeralang B | VIC | 228 | [8 empty] | New England Solar Farm BESS | NSW | 200 | 200 | 2026-12-01 | Anticipated
Ladbroke Grove | SA | 80 | [8 empty] | Orana BESS | NSW | 408.48 | 1660 | 2026-12-01 | Anticipated
Laverton North | VIC | 312 | [8 empty] | Philip Island BESS | VIC | 5 | 10 |  | Existing
Lonsdale | SA | 20.7 | [8 empty] | Queanbeyan BESS | NSW | 10 | 20 |  | Existing
Mintaro GT | SA | 90 | [8 empty] | Quorn Park BESS | NSW | 27.6 | 40 | 2025-12-01 | Anticipated
Mortlake | VIC | 584 | [8 empty] | Rangebank BESS | VIC | 200 | 400 | 2024-10-01 | Committed
Mt Stuart | QLD | 423.5 | [8 empty] | Richmond Valley BESS | NSW | 275 | 2200 | 2026-10-01 | Anticipated
Newport | VIC | 500 | [8 empty] | Riverina Energy Storage System 1 | NSW | 60 | 120 |  | Existing
Oakey Power Station | QLD | 346 | [8 empty] | Riverina Energy Storage System 2 | NSW | 65 | 130 |  | Existing
Osborne | SA | 180 | [8 empty] | Sapphire Wind Farm BESS | NSW | 30 | 38 | 2024-12-01 | Anticipated
Pelican Point | SA | 529 | [8 empty] | Stanwell BESS | QLD | 150 | 300 | 2027-03-01 | Anticipated
Port Lincoln GT | SA | 73.5 | [8 empty] | Swanbank BESS | QLD | 250 | 500 | 2026-01-01 | Anticipated
Port Stanvac 1 | SA | 46.8 | [8 empty] | Tailem Bend Battery Project | SA | 41.5 | 84 | 2024-01-01 | Committed
Quarantine | SA | 234 | [8 empty] | Tamworth BESS | NSW | 200 | 400 | 2026-11-01 | Anticipated
Roma | QLD | 80 | [8 empty] | Tarong BESS | QLD | 300 | 300 | 2024-09-01 | Anticipated
Smithfield Energy Facility | NSW | 185 | [8 empty] | Templers BESS | SA | 111 | 291 | 2025-05-01 | Anticipated
Snapper Point Power Station | SA | 154 | [8 empty] | Terang BESS | VIC | 101.5 | 200 | 2025-12-01 | Anticipated
Snuggery | SA | 63 | [8 empty] | Torrens Island BESS | SA | 250.7 | 250 | 2023-08-01 | Committed
Somerton | VIC | 170 | [8 empty] | Ulinda Park BESS | QLD | 154.96 | 298 | 2024-12-01 | Anticipated
Swanbank E GT | QLD | 385 | [8 empty] | Victorian Big Battery | VIC | 300 | 450 |  | Existing
Tallawarra | NSW | 440 | [8 empty] | Wallgrove Grid Battery project | NSW | 50 | 75 |  | Existing
Tamar Valley Combined Cycle | TAS | 208 | [8 empty] | Wandoan South BESS | QLD | 100 | 150 |  | Existing
Tamar Valley Peaking | TAS | 58 | [8 empty] | Waratah Super Battery | NSW | 850.18 | 1679 | 2025-03-01 | Committed
Torrens Island B | SA | 800 | [8 empty] | Western Downs Battery | QLD | 336 | 400 | 2025-01-01 | Anticipated
Townsville Power Station | QLD | 244 | [8 empty] | Wooreen Energy Storage System | VIC | 350 | 1400 | 2026-12-01 | Anticipated
Uranquinty | NSW | 692 | [8 empty] | 2. Indicative commissioning date of projects are based on Generation Information updates from February 2024. Where information is absent, the commissioning date is assumed to be 1 July 2025.
Valley Power | VIC | 300 | [8 empty] | 3. Energy capacity provided here is before accounting for batttery degradation.
Yarwun Cogen | QLD | 180
Barron Gorge | QLD | 70
Bastyan | TAS | 79.9
Blowering | NSW | 80
Bogong / Mackay | VIC | 300.02
Catagunya / Liapootah / Wayatinah | TAS | 176.7
Cethana | TAS | 85
Dartmouth | VIC | 185
Devils Gate | TAS | 60
Eildon | VIC | 135
Fisher | TAS | 43.2
Gordon | TAS | 432
Guthega | NSW | 60
Hume Dam NSW | NSW | 29
Hume Dam VIC | VIC | 29
John Butters | TAS | 144
Kareeya | QLD | 86.4
Lake Echo | TAS | 32.4
Lemonthyme / Wilmot | TAS | 81.6
Mackintosh | TAS | 79.9
Meadowbank | TAS | 40
Murray 1 | VIC | 950
Murray 2 | VIC | 552
Poatina | TAS | 300
Reece | TAS | 231.2
Shoalhaven | NSW | 247
Tarraleah | TAS | 90
Trevallyn | TAS | 93
Tribute | TAS | 82.8
Tumut 3 | NSW | 1500
Tungatinah | TAS | 125
Upper Tumut | NSW | 616
West Kiewa | VIC | 68
Wivenhoe | QLD | 570
Adelaide Desalination Plant Solar Farm | SA | 11
Avonlie Solar Farm | NSW | 254.1
Bannerton Solar Park | VIC | 100
Beryl Solar Farm | NSW | 98.4
Bluegrass Solar Farm | QLD | 148
Bolivar Waste Water Treatment Solar Farm | SA | 11.25
Bomen Solar Farm | NSW | 121
Broken Hill Solar Farm | NSW | 53
Bungala One Solar Farm | SA | 135
Bungala Two Solar Farm | SA | 135
Childers Solar Farm | QLD | 64.38
Clare Solar Farm | QLD | 110.4
Clermont Solar Farm | QLD | 92.5
Cohuna Solar Farm | VIC | 31.16
Coleambally Solar Farm | NSW | 150.3
Collinsville Solar Farm | QLD | 42.5
Columboola Solar Farm | QLD | 217.25
Corowa Solar Farm | NSW | 36.01
Darling Downs Solar Farm | QLD | 121
Darlington Point Solar Farm | NSW | 274.97
Daydream Solar Farm | QLD | 167.75
Edenvale Solar Park | QLD | 180
Emerald Solar Farm | QLD | 72
Finley Solar Farm | NSW | 162.36
Gangarri Solar Farm | QLD | 162
Gannawarra Solar Farm | VIC | 55
Glenrowan West Solar Farm | VIC | 132
Goonumbla Solar Farm | NSW | 69.75
Gullen Range Solar Farm | NSW | 10
Gunnedah Solar Farm | NSW | 110
Hamilton Solar Farm | QLD | 57.5
Happy Valley Reservoir | SA | 8.34
Haughton Solar Farm | QLD | 132.6
Hayman Solar Farm | QLD | 57.75
Hillston Sun Farm | NSW | 110
Hughenden Solar Farm | QLD | 20.97
Jemalong Solar | NSW | 55
Junee Solar Farm | NSW | 36.01
Karadoc Solar Farm | VIC | 104.5
Kennedy Energy Park Solar Farm | QLD | 15
Kiamal Solar Farm stage 1 | VIC | 199.95
Kidston Solar Farm | QLD | 50
Lilyvale Solar Farm | QLD | 118.4
Limondale Solar Farm 1 | NSW | 230
Limondale Solar Farm 2 | NSW | 28.98
Longreach Solar Farm | QLD | 14
Manildra Solar Farm | NSW | 50
Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | SA | 16.8
Mannum Adelaide Pumping Station No 3 - MAPL3 (Tungkillo) | SA | 12.36
Maryrorough Solar Farm | QLD | 34.5
Middlemount Solar Farm | QLD | 26
Molong Solar Farm | NSW | 36.08
Moree Solar Farm | NSW | 56
Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | SA | 6.12
Morgan To Whyalla Pipeline No 2 PS | SA | 5.88
Morgan To Whyalla Pipeline No 3 PS | SA | 7.38
Morgan To Whyalla Pipeline No 4 PS | SA | 5.88
Moura Solar Farm | QLD | 99
Murray Bridge - Onkaparinga Pipeline Pump 2 | SA | 13.74
Nevertire Solar Farm | NSW | 104.64
New England Solar Farm | NSW | 400
Numurkah Solar Farm | VIC | 101.09
Nyngan Solar Plant | NSW | 102.03
Oakey 1 Solar Farm | QLD | 25
Oakey 2 Solar Farm | QLD | 55.64
Parkes Solar Farm | NSW | 55
Port Augusta Renewable Energy Park - Solar | SA | 79.2
Ross River Solar Farm | QLD | 128
Rugby Run Solar Farm | QLD | 65
Sun Metals Corporation Solar Farm | QLD | 143
Sunraysia Solar Farm | NSW | 228.8
Suntop Solar Farm | NSW | 150
Susan River Solar Farm | QLD | 85.26
Tailem Bend Solar Farm | SA | 108
Tailem Bend Solar Farm - stage 2 | SA | 105
Wagga North Solar Farm | NSW | 56
Warwick Solar Farm | QLD | 64.2
Wellington Solar Farm | NSW | 216.08
Wemen Solar Farm | VIC | 97.5
West Wyalong Solar Farm | NSW | 105.27
Western Downs Green Power Hub | QLD | 399.97
White Rock Solar Farm | NSW | 20
Whitsunday Solar Farm | QLD | 57.5
Winton Solar Farm | VIC | 85
Wyalong Solar Farm | NSW | 62.32
Yarranlea Solar Farm | QLD | 102.96
Yatpool Solar Farm | VIC | 94
Ararat Wind Farm | VIC | 240
Bald Hills Wind Farm | VIC | 106.6
Bango 973 Wind Farm | NSW | 159
Bango 999 Wind Farm | NSW | 84.8
Berrybank Wind Farm | VIC | 290
Boco Rock Wind Farm | NSW | 113
Bodangora Wind Farm | NSW | 113.19
Bulgana Green Power Hub - Wind Farm | VIC | 204.4
Canunda Wind Farm | SA | 46
Capital Wind Farm | NSW | 140.7
Cathedral Rocks Wind Farm | SA | 62
Cattle Hill Wind Farm | TAS | 144
Challicum Hills Wind Farm | VIC | 52.5
Cherry Tree Wind Farm | VIC | 57.6
Clements Gap Wind Farm | SA | 56.7
Collector Wind Farm | NSW | 226.8
Coopers Gap Wind Farm | QLD | 452.89
Crookwell 2 Wind Farm | NSW | 96.04
Crowlands Wind Farm | VIC | 79.95
Crudine Ridge Wind Farm | NSW | 141.71
Cullerin Range Wind Farm | NSW | 30
Dulacca Wind Farm | QLD | 172.99
Dundonnell Wind Farm | VIC | 336
Elaine Wind Farm | VIC | 83.6
Granville Harbour Wind Farm | TAS | 111.6
Gullen Range Wind Farm | NSW | 165.5
Gullen Range Wind Farm 2 | NSW | 110.67
Gunning Wind Farm | NSW | 46.5
Hallett 4 North Brown Hill Wind Farm | SA | 132.3
Hallett 5 The Bluff Wind Farm | SA | 52.5
Hallett Stage 1 Brown Hill Wind Farm | SA | 94.5
Hallett Stage 2 Hallett Hill Wind Farm | SA | 71.4
Hornsdale Wind Farm Stage 1 | SA | 102.4
Hornsdale Wind Farm Stage 2 | SA | 102.4
Hornsdale Wind Farm Stage 3 | SA | 112
Kaban Green Power Hub - Wind Farm | QLD | 156.8
Kennedy Energy Park Wind Farm | QLD | 43.2
Kiata Wind Farm | VIC | 31.05
Lake Bonney 1 Wind Farm | SA | 80.5
Lake Bonney 2 Wind Farm | SA | 159
Lake Bonney 3 Wind Farm | SA | 39
Lincoln Gap Wind Farm - Stage 2 | SA | 86.4
Lincoln Gap Wind Farm - stage 1 | SA | 126
Macarthur Wind Farm | VIC | 420
Moorabool Wind Farm | VIC | 312
Mortlake South Wind Farm | VIC | 157.5
Mortons Lane Wind Farm | VIC | 19.5
Mount Emerald Wind Farm | QLD | 180.52
Mount Millar Wind Farm | SA | 72.28
Mt Gellibrand Wind Farm | VIC | 138.6
Mt Mercer Wind Farm | VIC | 131.2
Murra Warra Wind Farm - stage 1 | VIC | 225.7
Murra Warra Wind Farm - stage 2 | VIC | 209
Musselroe Wind Farm | TAS | 168
Oaklands Hill Wind Farm | VIC | 67.2
Port Augusta Renewable Energy Park - Wind | SA | 210
Portland Wind Farm | VIC | 151.7
Salt Creek Wind Farm | VIC | 54
Sapphire Wind Farm | NSW | 270
Silverton Wind Farm | NSW | 198.94
Snowtown S2 Wind Farm | SA | 270
Snowtown Wind Farm | SA | 98.7
Starfish Hill Wind Farm | SA | 33
Stockyard Hill Wind Farm | VIC | 527.56
Taralga Wind Farm | NSW | 106.8
Waterloo Wind Farm | SA | 130.8
Wattle Point Wind Farm | SA | 90.75
Waubra Wind Farm | VIC | 192
White Rock Wind Farm - Stage 1 | NSW | 172.48
Willogoleche Wind Farm | SA | 119.36
Woodlawn Wind Farm | NSW | 48.3
Woolnorth Wind Farm | TAS | 139.75
Yaloak South Wind Farm | VIC | 28.7
Yambuk Wind Farm | VIC | 30
Yendon Wind Farm | VIC | 144.4
Notes:
This table shows the current maximum capacities as of February 2024 Gen Info and does not show the 30 MW upgrade in 2027 for Mt Piper.
For modelling runs where Marinuslink is built, certain generator capacities are adjusted upwards in Tasmania: 100 MW across the west coast, 150 MW for Tarraleah and 90 MW capacity for Gordon. This is made available through upgrading assets and adapting hydropower operations to take advantage of the ‘head effect’ (the extra capacity and efficiency of generation when there is a greater altitude difference between the top of the storage and the power station). This also includes 50 MW non scheduled generation Source: Battery of the Nation - Unlocking Tasmania’s energy capacity.

## Seasonal ratings
Go to Assumptions Summary
Seasonal ratings (available for dispatch in each season)
Seasonal ratings of each existing generating units are based on February 2024 Generation Information seasonal ratings.
https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information
Not all advanced projects have ratings listed in Generation Information. Where information is not available, nameplate capacity is used.
Additional projects are not listed in the Generation Information page; their nameplate capacities are used as ratings.
These ratings represent the Summer Peak (November to March inclusive), Summer Typical (November to March inclusive), and Winter (June to August inclusive) ratings between the Summer 2023-24 and 2032-33. Seasonal ratings are continued beyond this point until retirement.
Summer peak ratings are applied to 'hot days', which are defined as any day which exceeds the POE10 reference temperature in each region (varies by region but usually ~35-40 degrees), or one of the top five hottest days for that year if there aren't five days exceeding the reference temperature.
New generation technologies
Generator type | Summer Peak (% of nameplate) | Summer Typical (% of nameplate) | Winter (% of nameplate)
OCGT (small GT) | 97.7017 | 100 | 100
OCGT (large GT) | 86.3842 | 92.1887 | 98.5177
CCGT | 87.2673 | 92.9095 | 97.5487
CCGT with CCS | 81.1854 | 85.9413 | 90.0714
Biomass | 94.9299 | 100 | 100
Large scale Solar PV | 100 | 100 | 100
Solar Thermal (15hrs storage) | 100 | 100 | 100
Battery storage (1hr storage) | 100 | 100 | 99.9494
Battery storage (2hrs storage) | 100 | 100 | 99.8476
Battery storage (4hrs storage) | 100 | 100 | 99.8975
Battery Storage (8hrs storage) | 100 | 100 | 99.8435
Wind | 100 | 100 | 100
Wind - offshore (fixed) | 100 | 100 | 100
Wind - offshore (floating) | 100 | 100 | 100
Pumped Hydro (8hrs storage) | 100 | 100 | 100
Pumped Hydro (24hrs storage) | 100 | 100 | 100
Pumped Hydro (48hrs storage) | 100 | 100 | 100
BOTN - Cethana | 100 | 100 | 100
Hydrogen reciprocating engines | 100 | 100 | 100
Notes:
1. Sourced from Aurecon 2022 Costs and Technical Parameter Review and GHD 2018 AEMO Cost and Technical Parameter Review for Pumped Hydro.
2. Summer Peak, Summer Typical and Winter rates are based on Aurecon's assumed capacity under ambient conditions for 35oC, 25oC and 15oC respectively.
3. Seasonal rating of renewable energy generators are captured within the renewable energy generation' availability traces.
Existing generators
Generator | DUID | Region | Summer Peak | [9 empty] | Summer Typical | [9 empty] | Winter
|  |  | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Bayswater | BW01 | NSW | 630 | 630 | 630 | 630 | 630 | 630 | 630 | 630 | 630 | 630 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660
Bayswater | BW02 | NSW | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685
Bayswater | BW03 | NSW | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685
Bayswater | BW04 | NSW | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 655 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685 | 685
Callide B | CALL_B_1 | QLD | 325 | 325 | 325 | 325 | 325 | 325 | 0 | 0 | 0 | 0 | 325 | 325 | 325 | 325 | 325 | 325 | 0 | 0 | 0 | 0 | 350 | 350 | 350 | 350 | 350 | 350 | 0 | 0 | 0 | 0
Callide B | CALL_B_2 | QLD | 325 | 325 | 325 | 325 | 325 | 325 | 0 | 0 | 0 | 0 | 325 | 325 | 325 | 325 | 325 | 325 | 0 | 0 | 0 | 0 | 350 | 350 | 350 | 350 | 350 | 350 | 0 | 0 | 0 | 0
Callide C | CPP_3 | QLD | 0 | 434 | 434 | 434 | 434 | 434 | 434 | 434 | 434 | 434 | 0 | 466 | 466 | 466 | 466 | 466 | 466 | 466 | 466 | 466 | 0 | 466 | 466 | 466 | 466 | 466 | 466 | 466 | 466 | 466
Callide C | CPP_4 | QLD | 0 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 0 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 0 | 0 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
Eraring | ER01 | NSW | 680 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 720 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Eraring | ER02 | NSW | 680 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 720 | 720 | 720 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Eraring | ER03 | NSW | 660 | 670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 680 | 690 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Eraring | ER04 | NSW | 660 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 660 | 660 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 680 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gladstone | GSTONE1 | QLD | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
Gladstone | GSTONE2 | QLD | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
Gladstone | GSTONE3 | QLD | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
Gladstone | GSTONE4 | QLD | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
Gladstone | GSTONE5 | QLD | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
Gladstone | GSTONE6 | QLD | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
Kogan Creek | KPP_1 | QLD | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750 | 750
Millmerran | MPP_1 | QLD | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 426 | 426 | 426 | 426 | 426 | 426 | 426 | 426 | 426 | 426
Millmerran | MPP_2 | QLD | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 335 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 426 | 426 | 426 | 426 | 426 | 426 | 426 | 426 | 426 | 426
Mt Piper | MP1 | NSW | 705 | 705 | 705 | 705 | 705 | 705 | 705 | 705 | 705 | 705 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730 | 730
Mt Piper | MP2 | NSW | 675 | 675 | 675 | 675 | 675 | 675 | 675 | 675 | 675 | 675 | 680 | 680 | 680 | 680 | 680 | 680 | 680 | 680 | 680 | 680 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700
Stanwell | STAN-1 | QLD | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365
Stanwell | STAN-2 | QLD | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365
Stanwell | STAN-3 | QLD | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365
Stanwell | STAN-4 | QLD | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365
Tarong | TARONG#1 | QLD | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
Tarong | TARONG#2 | QLD | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
Tarong | TARONG#3 | QLD | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
Tarong | TARONG#4 | QLD | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
Tarong North | TNPS1 | QLD | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443 | 443
Vales Point B | VP5 | NSW | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660
Vales Point B | VP6 | NSW | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660 | 660
Loy Yang A Power Station | LYA1 | VIC | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
Loy Yang A Power Station | LYA2 | VIC | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530
Loy Yang A Power Station | LYA3 | VIC | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
Loy Yang A Power Station | LYA4 | VIC | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 530 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
Loy Yang B | LOYYB1 | VIC | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580
Loy Yang B | LOYYB2 | VIC | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 550 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580 | 580
Yallourn W | YWPS1 | VIC | 335 | 350 | 350 | 350 | 350 | 0 | 0 | 0 | 0 | 0 | 360 | 360 | 360 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 365 | 380 | 380 | 380 | 380 | 380 | 0 | 0 | 0 | 0
Yallourn W | YWPS2 | VIC | 330 | 330 | 330 | 330 | 330 | 0 | 0 | 0 | 0 | 0 | 350 | 350 | 350 | 350 | 350 | 0 | 0 | 0 | 0 | 0 | 360 | 360 | 360 | 360 | 360 | 360 | 0 | 0 | 0 | 0
Yallourn W | YWPS3 | VIC | 360 | 360 | 360 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 370 | 370 | 370 | 370 | 370 | 0 | 0 | 0 | 0 | 0 | 395 | 395 | 395 | 395 | 395 | 395 | 0 | 0 | 0 | 0
Yallourn W | YWPS4 | VIC | 360 | 360 | 360 | 360 | 360 | 0 | 0 | 0 | 0 | 0 | 370 | 370 | 370 | 370 | 370 | 0 | 0 | 0 | 0 | 0 | 395 | 395 | 395 | 395 | 395 | 395 | 0 | 0 | 0 | 0
Angaston | ANGAS1 | SA | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6
Angaston | ANGAS2 | SA | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 14.4
Bairnsdale | BDL01 | VIC | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
Bairnsdale | BDL02 | VIC | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
Barcaldine Power Station | BARCALDN | QLD | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37
Barker Inlet Power Station | BIPS1_01 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_02 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_03 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_04 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_05 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_06 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_07 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_08 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_09 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_10 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_11 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Barker Inlet Power Station | BIPS1_12 | SA | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Bell Bay Three | BBTHREE1 | TAS | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Bell Bay Three | BBTHREE2 | TAS | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Bell Bay Three | BBTHREE3 | TAS | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Bolivar Power Station | BOLIVPS1_1 | SA | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4
Bolivar Power Station | BOLIVPS1_2 | SA | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4
Bolivar Power Station | BOLIVPS1_3 | SA | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4
Bolivar Power Station | BOLIVPS1_4 | SA | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4 | 31.4
Braemar | BRAEMAR1 | QLD | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
Braemar | BRAEMAR2 | QLD | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
Braemar | BRAEMAR3 | QLD | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
Braemar 2 Power Station | BRAEMAR5 | QLD | 155 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 155 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
Braemar 2 Power Station | BRAEMAR6 | QLD | 155 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 155 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
Braemar 2 Power Station | BRAEMAR7 | QLD | 155 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 155 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
Colongra | CG1 | NSW | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
Colongra | CG2 | NSW | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
Colongra | CG3 | NSW | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
Colongra | CG4 | NSW | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
Condamine A | CPSA_GT1 | QLD | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9
Condamine A | CPSA_GT2 | QLD | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.78 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 41.89 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9 | 43.9
Condamine A | CPSA_ST | QLD | 54.97 | 54.97 | 54.97 | 54.97 | 54.97 | 54.97 | 54.97 | 54.97 | 54.97 | 54.97 | 55.32 | 55.32 | 55.32 | 55.32 | 55.32 | 55.32 | 55.32 | 55.32 | 55.32 | 55.32 | 56.43 | 56.43 | 56.43 | 56.43 | 56.43 | 56.43 | 56.43 | 56.43 | 56.43 | 56.43
Darling Downs | DDPS1_ST | QLD | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 273 | 273 | 273 | 273 | 273 | 273 | 273 | 273 | 273 | 273
Darling Downs | DDPS1_GT1 | QLD | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
Darling Downs | DDPS1_GT2 | QLD | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
Darling Downs | DDPS1_GT3 | QLD | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
Dry Creek GT | DRYCGT1 | SA | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 0 | 0 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 0 | 0 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 0 | 0
Dry Creek GT | DRYCGT2 | SA | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 0 | 0 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 0 | 0 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 0 | 0
Dry Creek GT | DRYCGT3 | SA | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 0 | 0 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 0 | 0 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 0 | 0
Hallett GT | AGLHAL01 | SA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 0 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
Hallett GT | AGLHAL02 | SA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 0 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5
Hallett GT | AGLHAL03 | SA | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
Hallett GT | AGLHAL04 | SA | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Hallett GT | AGLHAL05 | SA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Hallett GT | AGLHAL06 | SA | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Hallett GT | AGLHAL07 | SA | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
Hallett GT | AGLHAL08 | SA | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Hallett GT | AGLHAL09 | SA | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 0 | 0 | 0 | 23 | 23 | 23 | 23 | 23 | 23 | 23
Hallett GT | AGLHAL10 | SA | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Hallett GT | AGLHAL11 | SA | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Hallett GT | AGLHAL12 | SA | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Hallett GT | AGLHALRE | SA | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Jeeralang A | JLA01 | VIC | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Jeeralang A | JLA02 | VIC | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Jeeralang A | JLA03 | VIC | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Jeeralang A | JLA04 | VIC | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Jeeralang B | JLB01 | VIC | 0 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 0 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 0 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Jeeralang B | JLB02 | VIC | 68.3 | 68.3 | 68.3 | 68.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 74 | 74 | 74 | 74 | 76 | 76 | 76 | 76 | 76 | 76 | 83 | 83 | 83 | 83 | 85 | 85 | 85 | 85 | 85 | 85
Jeeralang B | JLB03 | VIC | 72.3 | 72.3 | 72.3 | 72.3 | 72.3 | 72.3 | 72.3 | 72.3 | 72.3 | 72.3 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
Ladbroke Grove | LADBROK1 | SA | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
Ladbroke Grove | LADBROK2 | SA | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
Laverton North | LNGS1 | VIC | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172
Laverton North | LNGS2 | VIC | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172
Lonsdale | LONSDALE | SA | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06 | 21.06
Mintaro GT | MINTARO | SA | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 0 | 0 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 0 | 0 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0 | 0
Mortlake | MORTLK11 | VIC | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
Mortlake | MORTLK12 | VIC | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
Mt Stuart | MSTUART1 | QLD | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
Mt Stuart | MSTUART2 | QLD | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 139 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
Mt Stuart | MSTUART3 | QLD | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Newport | NPS | VIC | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510
Oakey Power Station | OAKEY1 | QLD | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
Oakey Power Station | OAKEY2 | QLD | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
Osborne | OsborneGT | SA | 110 | 110 | 110 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 112 | 112 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 121 | 121 | 121 | 0 | 0 | 0 | 0 | 0 | 0
Osborne | OsborneST | SA | 62 | 62 | 62 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 63 | 63 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 65 | 65 | 65 | 0 | 0 | 0 | 0 | 0 | 0
Pelican Point | PPCCGTGT1 | SA | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
Pelican Point | PPCCGTGT2 | SA | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 143 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
Pelican Point | PPCCGTST | SA | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157
Port Lincoln GT | POR01-1 | SA | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0
Port Lincoln GT | POR01-2 | SA | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0
Port Lincoln GT | POR01-3 | SA | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 23.5 | 0 | 0
Port Stanvac 1 | PTSTAN1_1 | SA | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4
Port Stanvac 1 | PTSTAN1_2 | SA | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4 | 23.4
Quarantine | QPS1 | SA | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Quarantine | QPS2 | SA | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
Quarantine | QPS3 | SA | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Quarantine | QPS4 | SA | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
Quarantine | QPS5 | SA | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Roma | ROMA_7 | QLD | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
Roma | ROMA_8 | QLD | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
Smithfield Energy Facility | SITHE01 | NSW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9
Smithfield Energy Facility | SITHE02 | NSW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9
Smithfield Energy Facility | SITHE03 | NSW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9 | 41.9
Smithfield Energy Facility | SITHE04 | NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Snapper Point Power Station | SNAPPER1_1 | SA | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38
Snapper Point Power Station | SNAPPER1_2 | SA | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38
Snapper Point Power Station | SNAPPER1_3 | SA | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38
Snapper Point Power Station | SNAPPER1_4 | SA | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38
Snapper Point Power Station | SNAPPER1_5 | SA | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 27.62 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38 | 31.38
Snuggery | SNUG1 | SA | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 0
Snuggery | SNUG2 | SA | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 0
Snuggery | SNUG3 | SA | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 | 0
Somerton | AGLSOM01 | VIC | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
Somerton | AGLSOM02 | VIC | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
Somerton | AGLSOM03 | VIC | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
Somerton | AGLSOM04 | VIC | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
Swanbank E GT | SWAN_E | QLD | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 355 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365
Tallawarra | TALWA1 | NSW | 385 | 405 | 405 | 405 | 405 | 405 | 405 | 405 | 405 | 405 | 395 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425 | 425
Tamar Valley Combined Cycle | TVCC201_GT | TAS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tamar Valley Combined Cycle | TVCC201_ST | TAS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tamar Valley Peaking | TVPP104 | TAS | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
Torrens Island B | TORRB1 | SA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Torrens Island B | TORRB2 | SA | 195 | 195 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Torrens Island B | TORRB3 | SA | 195 | 195 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Torrens Island B | TORRB4 | SA | 195 | 195 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Townsville Power Station. | YABULU | QLD | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
Townsville Power Station. | YABULU2 | QLD | 78 | 78 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 78 | 78 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 82 | 82 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
Uranquinty | URANQ11 | NSW | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
Uranquinty | URANQ12 | NSW | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
Uranquinty | URANQ13 | NSW | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
Uranquinty | URANQ14 | NSW | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
Valley Power | VPGS1 | VIC | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Valley Power | VPGS2 | VIC | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Valley Power | VPGS3 | VIC | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Valley Power | VPGS4 | VIC | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Valley Power | VPGS5 | VIC | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Valley Power | VPGS6 | VIC | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 47.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Yarwun Cogen | YARWUN_1 | QLD | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
Barron Gorge | BARRON-1 | QLD | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Barron Gorge | BARRON-2 | QLD | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Bastyan | BASTYAN | TAS | 81 | 81 | 81 | 81 | 0 | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 81 | 0 | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 81 | 81 | 0 | 84 | 84 | 84 | 84
Blowering | BLOWERNG | NSW | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Bogong / Mackay | BOGONG1 | VIC | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Bogong / Mackay | BOGONG2 | VIC | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Bogong / Mackay | MCKAY11 | VIC | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67
Bogong / Mackay | MCKAY12 | VIC | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67
Bogong / Mackay | MCKAY13 | VIC | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67
Bogong / Mackay | MCKAY14 | VIC | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67
Bogong / Mackay | MCKAY15 | VIC | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67
Bogong / Mackay | MCKAY16 | VIC | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67 | 26.67
Catagunya / Liapootah / Wayatinah | CA111-1 | TAS | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Catagunya / Liapootah / Wayatinah | CA112-2 | TAS | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0 | 24 | 24
Catagunya / Liapootah / Wayatinah | LI111-1 | TAS | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Catagunya / Liapootah / Wayatinah | LI112-2 | TAS | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Catagunya / Liapootah / Wayatinah | LI113-3 | TAS | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
Catagunya / Liapootah / Wayatinah | WY111-1 | TAS | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
Catagunya / Liapootah / Wayatinah | WY111-2 | TAS | 13 | 13 | 0 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 0 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
Catagunya / Liapootah / Wayatinah | WY111-3 | TAS | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
Cethana | CETHANA | TAS | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Dartmouth | DARTM1 | VIC | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
Devils Gate | DEVILS_G | TAS | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
Eildon | EILDON1 | VIC | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Eildon | EILDON2 | VIC | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Fisher | FISHER | TAS | 46 | 0 | 46 | 46 | 0 | 46 | 46 | 46 | 46 | 46 | 46 | 0 | 46 | 46 | 0 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 0 | 46 | 46 | 46 | 46
Gordon | GO181-1 | TAS | 126 | 126 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126
Gordon | GO182-2 | TAS | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
Gordon | GO183-3 | TAS | 126 | 126 | 126 | 126 | 126 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 0 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 0 | 126 | 126 | 126
Guthega | GUTHEGA1 | NSW | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
Guthega | GUTHEGA2 | NSW | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
Hume Dam NSW | HUMENSW | NSW | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hume Dam VIC | HUMEV | VIC | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
John Butters | JBUTTERS | TAS | 140 | 140 | 140 | 140 | 0 | 144 | 144 | 144 | 144 | 144 | 140 | 140 | 140 | 140 | 0 | 144 | 144 | 144 | 144 | 144 | 140 | 140 | 140 | 140 | 140 | 144 | 144 | 144 | 144 | 144
Kareeya | KAREEYA1 | QLD | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6
Kareeya | KAREEYA2 | QLD | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6
Kareeya | KAREEYA3 | QLD | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6
Kareeya | KAREEYA4 | QLD | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6
Lake Echo | LK_ECHO | TAS | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Lemonthyme / Wilmot | LM111-1 | TAS | 0 | 0 | 55 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 0 | 0 | 55 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 54 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Lemonthyme / Wilmot | WI111-1 | TAS | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
Mackintosh | MACKNTSH | TAS | 81 | 81 | 81 | 0 | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 0 | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 81 | 0 | 84 | 84 | 84 | 84 | 84
Meadowbank | MEADOWBK | TAS | 44 | 44 | 44 | 0 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 0 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
Murray 1 | MURRAY01 | VIC | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Murray 1 | MURRAY02 | VIC | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Murray 1 | MURRAY03 | VIC | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Murray 1 | MURRAY04 | VIC | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95
Murray 1 | MURRAY05 | VIC | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Murray 1 | MURRAY06 | VIC | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95
Murray 1 | MURRAY07 | VIC | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Murray 1 | MURRAY08 | VIC | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Murray 1 | MURRAY09 | VIC | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 0 | 95 | 95 | 95 | 95
Murray 1 | MURRAY10 | VIC | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Murray 2 | MURRAY11 | VIC | 137.5 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 137.5 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 137.5 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Murray 2 | MURRAY12 | VIC | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Murray 2 | MURRAY13 | VIC | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | 150
Murray 2 | MURRAY14 | VIC | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Poatina | PO161-1 | TAS | 57 | 57 | 0 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 57 | 57
Poatina | PO162-2 | TAS | 57 | 57 | 57 | 57 | 57 | 0 | 57 | 0 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 0 | 57 | 0 | 57 | 57 | 57 | 57 | 57 | 0 | 57 | 0 | 57 | 57 | 57 | 57
Poatina | PO163-3 | TAS | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 0 | 0 | 57 | 57 | 57 | 0 | 57 | 57
Poatina | PO164-4 | TAS | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 57 | 57
Poatina | PO165-5 | TAS | 57 | 0 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 0 | 57 | 0 | 57 | 57 | 57 | 57 | 57 | 57
Poatina | PO166-6 | TAS | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 0 | 57 | 57 | 57 | 57 | 0 | 0 | 57 | 57 | 0 | 57 | 57
Reece | REECE1 | TAS | 116 | 116 | 116 | 116 | 116 | 0 | 120 | 120 | 120 | 120 | 116 | 116 | 116 | 116 | 116 | 0 | 120 | 120 | 120 | 120 | 116 | 116 | 116 | 116 | 116 | 116 | 0 | 120 | 120 | 120
Reece | REECE2 | TAS | 116 | 116 | 116 | 116 | 116 | 116 | 0 | 120 | 120 | 120 | 116 | 116 | 116 | 116 | 116 | 116 | 0 | 120 | 120 | 120 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 0 | 120 | 120
Shoalhaven | SHGEN01 | NSW | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
Shoalhaven | SHGEN02 | NSW | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
Shoalhaven | SHGEN03 | NSW | 80 | 80 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 80 | 80 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 80 | 80 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
Shoalhaven | SHGEN04 | NSW | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5
Tarraleah | TA111-1 | TAS | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 0 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12
Tarraleah | TA111-2 | TAS | 12 | 12 | 14 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12
Tarraleah | TA111-3 | TAS | 0 | 12 | 0 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 12 | 0 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 14 | 12 | 12 | 12 | 12 | 12
Tarraleah | TA112-4 | TAS | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12
Tarraleah | TA112-5 | TAS | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12
Tarraleah | TA112-6 | TAS | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 12 | 12 | 14 | 14 | 12 | 12 | 12 | 12 | 12
Trevallyn | TR111-1 | TAS | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Trevallyn | TR111-2 | TAS | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Trevallyn | TR112-3 | TAS | 30 | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Trevallyn | TR112-4 | TAS | 30 | 30 | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 30 | 30 | 30 | 30
Tribute | TRIBUTE | TAS | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 0 | 88
Tumut 3 | TUMUT3_01 | NSW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Tumut 3 | TUMUT3_02 | NSW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Tumut 3 | TUMUT3_03 | NSW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Tumut 3 | TUMUT3_04 | NSW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Tumut 3 | TUMUT3_05 | NSW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Tumut 3 | TUMUT3_06 | NSW | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Tungatinah | TU111-1 | TAS | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Tungatinah | TU112-2 | TAS | 26 | 26 | 26 | 26 | 26 | 26 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Tungatinah | TU113-3 | TAS | 26 | 26 | 26 | 26 | 26 | 26 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Tungatinah | TU114-4 | TAS | 26 | 26 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Tungatinah | TU115-5 | TAS | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Upper Tumut | TUMUT1_01 | NSW | 93 | 93 | 93 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 93 | 93 | 93 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 93 | 93 | 93 | 0 | 103 | 103 | 103 | 103 | 103 | 103
Upper Tumut | TUMUT1_02 | NSW | 93 | 93 | 93 | 93 | 103 | 103 | 103 | 103 | 103 | 103 | 93 | 93 | 93 | 93 | 103 | 103 | 103 | 103 | 103 | 103 | 93 | 93 | 93 | 93 | 0 | 103 | 103 | 103 | 103 | 103
Upper Tumut | TUMUT1_03 | NSW | 93 | 93 | 93 | 93 | 93 | 103 | 103 | 103 | 103 | 103 | 93 | 93 | 93 | 93 | 93 | 103 | 103 | 103 | 103 | 103 | 93 | 93 | 93 | 93 | 93 | 0 | 103 | 103 | 103 | 103
Upper Tumut | TUMUT1_04 | NSW | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 0 | 103 | 103 | 103
Upper Tumut | TUMUT2_01 | NSW | 73 | 73 | 73 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 73 | 73 | 73 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 73 | 73 | 73 | 0 | 78 | 78 | 78 | 78 | 78 | 78
Upper Tumut | TUMUT2_02 | NSW | 73 | 73 | 73 | 73 | 78 | 78 | 78 | 78 | 78 | 78 | 73 | 73 | 73 | 73 | 78 | 78 | 78 | 78 | 78 | 78 | 73 | 73 | 73 | 73 | 0 | 78 | 78 | 78 | 78 | 78
Upper Tumut | TUMUT2_03 | NSW | 73 | 73 | 73 | 73 | 73 | 78 | 78 | 78 | 78 | 78 | 73 | 73 | 73 | 73 | 73 | 78 | 78 | 78 | 78 | 78 | 73 | 73 | 73 | 73 | 73 | 0 | 78 | 78 | 78 | 78
Upper Tumut | TUMUT2_04 | NSW | 73 | 73 | 73 | 73 | 73 | 73 | 78 | 78 | 78 | 78 | 73 | 73 | 73 | 73 | 73 | 73 | 78 | 78 | 78 | 78 | 73 | 73 | 73 | 73 | 73 | 73 | 0 | 78 | 78 | 78
West Kiewa | WKIEWA1_1 | VIC | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
West Kiewa | WKIEWA1_2 | VIC | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
West Kiewa | WKIEWA2_1 | VIC | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
West Kiewa | WKIEWA2_2 | VIC | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
Wivenhoe | W/HOE#1 | QLD | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285
Wivenhoe | W/HOE#2 | QLD | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285 | 285
Adelaide Desalination Plant Solar Farm | ADPPV1 | SA | 10.34 | 10.34 | 10.34 | 10.34 | 10.34 | 10.34 | 10.34 | 10.34 | 10.34 | 10.34 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 10.56 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
Avonlie Solar Farm | AVLSF1 | NSW | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98 | 189.98
Bannerton Solar Park | BANN1 | VIC | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
Beryl Solar Farm | BERYLSF1 | NSW | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 77.4 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 82.8 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
Bluegrass Solar Farm | BLUEGSF1 | QLD | 144.87 | 144.25 | 143.62 | 142.99 | 142.37 | 141.74 | 141.11 | 140.47 | 139.84 | 139.22 | 144.87 | 144.25 | 143.62 | 142.99 | 142.37 | 141.74 | 141.11 | 140.47 | 139.84 | 139.22 | 148 | 147.44 | 146.88 | 146.32 | 145.78 | 145.22 | 144.67 | 144.1 | 143.54 | 142.98
Bolivar Waste Water Treatment Solar Farm | BOWWPV1 | SA | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.57 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 11.25 | 11.25 | 11.25 | 11.25 | 11.25 | 11.25 | 11.25 | 11.25 | 11.25 | 11.25
Bomen Solar Farm | BOMENSF1 | NSW | 97.68 | 97.68 | 97.68 | 97.68 | 97.68 | 97.68 | 97.68 | 97.68 | 97.68 | 97.68 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99.88 | 99.88 | 99.88 | 99.88 | 99.88 | 99.88 | 99.88 | 99.88 | 99.88 | 99.88
Broken Hill Solar Farm | BROKENH1 | NSW | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53
Bungala One Solar Farm | BNGSF1 | SA | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 0 | 0 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62
Bungala Two Solar Farm | BNGSF2 | SA | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 104.76 | 105 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62 | 109.62
Childers Solar Farm | CHILDSF1 | QLD | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87 | 55.87
Clare Solar Farm | CLARESF1 | QLD | 95.22 | 95.22 | 95.22 | 95.22 | 95.22 | 95.22 | 95.22 | 95.22 | 95.22 | 95.22 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 99.98 | 99.98 | 99.98 | 99.98 | 99.98 | 99.98 | 99.98 | 99.98 | 99.98 | 99.98
Clermont Solar Farm | CLERMSF1 | QLD | 71.41 | 71.41 | 71.41 | 71.41 | 71.41 | 71.41 | 71.41 | 71.41 | 71.41 | 71.41 | 72.89 | 72.89 | 72.89 | 72.89 | 72.89 | 72.89 | 72.89 | 72.89 | 72.89 | 72.89 | 74.99 | 74.99 | 74.99 | 74.99 | 74.99 | 74.99 | 74.99 | 74.99 | 74.99 | 74.99
Cohuna Solar Farm | COHUNSF1 | VIC | 24.51 | 24.51 | 24.51 | 24.51 | 24.51 | 24.51 | 24.51 | 24.51 | 24.51 | 24.51 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17 | 27.17
Coleambally Solar Farm | COLEASF1 | NSW | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.93 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.93 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03 | 150.03
Collinsville Solar Farm | CSPVPS1 | QLD | 39.95 | 39.95 | 39.95 | 39.95 | 39.95 | 39.95 | 39.95 | 39.95 | 39.95 | 39.95 | 41.31 | 41.31 | 41.31 | 41.31 | 41.31 | 41.31 | 41.31 | 41.31 | 41.31 | 41.31 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
Columboola Solar Farm | COLUMSF1 | QLD | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95 | 161.95
Corowa Solar Farm | CRWASF1 | NSW | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Darling Downs Solar Farm | DDSF1 | QLD | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
Darlington Point Solar Farm | DARLSF1 | NSW | 263.3 | 263.3 | 263.3 | 263.3 | 263.3 | 263.3 | 263.3 | 263.3 | 263.3 | 263.3 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 266 | 274.96 | 274.96 | 274.96 | 274.96 | 274.96 | 274.96 | 274.96 | 274.96 | 274.96 | 274.96
Daydream Solar Farm | DAYDSF1 | QLD | 145.79 | 145.79 | 145.79 | 145.79 | 145.79 | 145.79 | 145.79 | 145.79 | 145.79 | 145.79 | 147.07 | 147.07 | 147.07 | 147.07 | 147.07 | 147.07 | 147.07 | 147.07 | 147.07 | 147.07 | 149.99 | 149.99 | 149.99 | 149.99 | 149.99 | 149.99 | 149.99 | 149.99 | 149.99 | 149.99
Edenvale Solar Park | EDENVSF1 | QLD | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
Emerald Solar Farm | EMERASF1 | QLD | 67.68 | 67.68 | 67.68 | 67.68 | 67.68 | 67.68 | 67.68 | 67.68 | 67.68 | 67.68 | 69.12 | 69.12 | 69.12 | 69.12 | 69.12 | 69.12 | 69.12 | 69.12 | 69.12 | 69.12 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
Finley Solar Farm | FINLYSF1 | NSW | 116.72 | 116.72 | 116.72 | 116.72 | 116.72 | 116.72 | 116.72 | 116.72 | 116.72 | 116.72 | 129.98 | 129.98 | 129.98 | 129.98 | 129.98 | 129.98 | 129.98 | 129.98 | 129.98 | 129.98 | 132.66 | 132.66 | 132.66 | 132.66 | 132.66 | 132.66 | 132.66 | 132.66 | 132.66 | 132.66
Gangarri Solar Farm | GANGARR1 | QLD | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88 | 119.88
Gannawarra Solar Farm | GANNSF1 | VIC | 47.76 | 47.76 | 47.76 | 47.76 | 47.76 | 47.76 | 47.76 | 47.76 | 47.76 | 47.76 | 49.01 | 49.01 | 49.01 | 49.01 | 49.01 | 49.01 | 49.01 | 49.01 | 49.01 | 49.01 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Glenrowan West Solar Farm | GLRWNSF1 | VIC | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 106.94 | 106.94 | 106.94 | 106.94 | 106.94 | 106.94 | 106.94 | 106.94 | 106.94 | 106.94 | 110.01 | 110.01 | 110.01 | 110.01 | 110.01 | 110.01 | 110.01 | 110.01 | 110.01 | 110.01
Goonumbla Solar Farm | GOONSF1 | NSW | 67.73 | 67.73 | 67.73 | 67.73 | 67.73 | 67.73 | 67.73 | 67.73 | 67.73 | 67.73 | 69.31 | 69.31 | 69.31 | 69.31 | 69.31 | 69.31 | 69.31 | 69.31 | 69.31 | 69.31 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75 | 69.75
Gullen Range Solar Farm | GULLRSF1 | NSW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Gunnedah Solar Farm | GNNDHSF1 | NSW | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
Hamilton Solar Farm | HAMISF1 | QLD | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Happy Valley Reservoir | HVWWPV1 | SA | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.82 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 7.99 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32 | 8.32
Haughton Solar Farm | HAUGHT11 | QLD | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03 | 100.03
Hayman Solar Farm | HAYMSF1 | QLD | 47.83 | 47.83 | 47.83 | 47.83 | 47.83 | 47.83 | 47.83 | 47.83 | 47.83 | 47.83 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Hillston Sun Farm | HILLSTN1 | NSW | 76.52 | 76.52 | 76.52 | 76.52 | 76.52 | 76.52 | 76.52 | 76.52 | 76.52 | 76.52 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Hughenden Solar Farm | HUGSF1 | QLD | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97 | 20.97
Jemalong Solar | JEMALNG1 | NSW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Junee Solar Farm | JUNEESF1 | NSW | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Karadoc Solar Farm | KARSF1 | VIC | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02 | 90.02
Kennedy Energy Park Solar Farm | KEPSF1 | QLD | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.28 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 14.58 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
Kiamal Solar Farm stage 1 | KIAMSF1 | VIC | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 198 | 199.95 | 199.95 | 199.95 | 199.95 | 199.95 | 199.95 | 199.95 | 199.95 | 199.95 | 199.95
Kidston Solar Farm | KSP1 | QLD | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5
Lilyvale Solar Farm | LILYSF1 | QLD | 97.53 | 97.53 | 97.53 | 97.53 | 97.53 | 97.53 | 97.53 | 97.53 | 97.53 | 97.53 | 98.79 | 98.79 | 98.79 | 98.79 | 98.79 | 98.79 | 98.79 | 98.79 | 98.79 | 98.79 | 99.97 | 99.97 | 99.97 | 99.97 | 99.97 | 99.97 | 99.97 | 99.97 | 99.97 | 99.97
Limondale Solar Farm 1 | LIMOSF11 | NSW | 207.1 | 207.1 | 207.1 | 207.1 | 207.1 | 207.1 | 207.1 | 207.1 | 207.1 | 207.1 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Limondale Solar Farm 2 | LIMOSF21 | NSW | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99 | 28.99
Longreach Solar Farm | LRSF1 | QLD | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
Manildra Solar Farm | MANSLR1 | NSW | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7
Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | MAPS2PV1 | SA | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 15.79 | 16.12 | 16.12 | 16.12 | 16.12 | 16.12 | 16.12 | 16.12 | 16.12 | 16.12 | 16.12 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8
Mannum Adelaide Pumping Station No 3 - MAPL3 (Tungkillo) | MAPS3PV1 | SA | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.64 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 11.88 | 12.36 | 12.36 | 12.36 | 12.36 | 12.36 | 12.36 | 12.36 | 12.36 | 12.36 | 12.36
Maryrorough Solar Farm | MARYRSF1 | QLD | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3 | 27.3
Middlemount Solar Farm | MIDDLSF1 | QLD | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
Molong Solar Farm | MOLNGSF1 | NSW | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01 | 36.01
Moree Solar Farm | MOREESF1 | NSW | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | MWPS1PV1 | SA | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.76 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 5.88 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12 | 6.12
Morgan To Whyalla Pipeline No 2 PS | MWPS2PV1 | SA | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86
Morgan To Whyalla Pipeline No 3 PS | MWPS3PV1 | SA | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 6.93 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.07 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37 | 7.37
Morgan To Whyalla Pipeline No 4 PS | MWPS4PV1 | SA | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.62 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86 | 5.86
Moura Solar Farm | MOUSF1 | QLD | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72 | 81.72
Murray Bridge - Onkaparinga Pipeline Pump 2 | MBPS2PV1 | SA | 12.91 | 12.91 | 12.91 | 12.91 | 12.91 | 12.91 | 12.91 | 12.91 | 12.91 | 12.91 | 13.19 | 13.19 | 13.19 | 13.19 | 13.19 | 13.19 | 13.19 | 13.19 | 13.19 | 13.19 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74 | 13.74
Nevertire Solar Farm | NEVERSF1 | NSW | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64 | 104.64
New England Solar Farm | NEWENSF1 | NSW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
Numurkah Solar Farm | NUMURSF1 | VIC | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95 | 99.95
Nyngan Solar Plant | NYNGAN1 | NSW | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02 | 102.02
Oakey 1 Solar Farm | OAKEY1SF | QLD | 23.1 | 23.1 | 23.1 | 23.1 | 23.1 | 23.1 | 23.1 | 23.1 | 23.1 | 23.1 | 24.22 | 24.22 | 24.22 | 24.22 | 24.22 | 24.22 | 24.22 | 24.22 | 24.22 | 24.22 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Oakey 2 Solar Farm | OAKEY2SF | QLD | 52.31 | 52.31 | 52.31 | 52.31 | 52.31 | 52.31 | 52.31 | 52.31 | 52.31 | 52.31 | 53.43 | 53.43 | 53.43 | 53.43 | 53.43 | 53.43 | 53.43 | 53.43 | 53.43 | 53.43 | 54.99 | 54.99 | 54.99 | 54.99 | 54.99 | 54.99 | 54.99 | 54.99 | 54.99 | 54.99
Parkes Solar Farm | PARSF1 | NSW | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5
Port Augusta Renewable Energy Park - Solar | PAREPS1 | SA | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2
Ross River Solar Farm | RRSF1 | QLD | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96 | 115.96
Rugby Run Solar Farm | RUGBYR1 | QLD | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
Sun Metals Corporation Solar Farm | SMCSF1 | QLD | 120.12 | 120.12 | 120.12 | 120.12 | 120.12 | 120.12 | 120.12 | 120.12 | 120.12 | 120.12 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16 | 121.16
Sunraysia Solar Farm | SUNRSF1 | NSW | 191.36 | 191.36 | 191.36 | 191.36 | 191.36 | 191.36 | 191.36 | 191.36 | 191.36 | 191.36 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68 | 199.68
Suntop Solar Farm | SUNTPSF1 | NSW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Susan River Solar Farm | SRSF1 | QLD | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01 | 75.01
Tailem Bend Solar Farm | TBSF1 | SA | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
Tailem Bend Solar Farm - stage 2 | TB2SF1 | SA | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 0 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87
Wagga North Solar Farm | WAGGNSF1 | NSW | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36 | 46.36
Warwick Solar Farm | WARWSF1 | QLD | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1
Warwick Solar Farm | WARWSF2 | QLD | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1 | 32.1
Wellington Solar Farm | WELLSF1 | NSW | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88 | 169.88
Wemen Solar Farm | WEMENSF1 | VIC | 82.36 | 82.36 | 82.36 | 82.36 | 82.36 | 82.36 | 82.36 | 82.36 | 82.36 | 82.36 | 85.52 | 85.52 | 85.52 | 85.52 | 85.52 | 85.52 | 85.52 | 85.52 | 85.52 | 85.52 | 87.98 | 87.98 | 87.98 | 87.98 | 87.98 | 87.98 | 87.98 | 87.98 | 87.98 | 87.98
West Wyalong Solar Farm | WSTWYSF1 | NSW | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01 | 90.01
Western Downs Green Power Hub | WDGPH1 | QLD | 394.95 | 394.95 | 394.95 | 394.95 | 394.95 | 394.95 | 394.95 | 394.95 | 394.95 | 394.95 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 349.86 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96 | 399.96
White Rock Solar Farm | WRSF1 | NSW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Whitsunday Solar Farm | WHITSF1 | QLD | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.11 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 54.9 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
Winton Solar Farm | WINTSF1 | VIC | 84.99 | 84.99 | 84.99 | 84.99 | 84.99 | 84.99 | 84.99 | 84.99 | 84.99 | 84.99 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Wyalong Solar Farm | WYASF1 | NSW | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01 | 53.01
Yarranlea Solar Farm | YARANSF1 | QLD | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96 | 102.96
Yatpool Solar Farm | YATSF1 | VIC | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
Ararat Wind Farm | ARWF1 | VIC | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
Bald Hills Wind Farm | BALDHWF1 | VIC | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6 | 106.6
Bango 973 Wind Farm | BANGOWF1 | NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Bango 999 Wind Farm | BANGOWF2 | NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8 | 84.8
Berrybank Wind Farm | BRYB1WF1 | VIC | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91 | 175.91
Berrybank Wind Farm | BRYB2WF2 | VIC | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19 | 105.19
Boco Rock Wind Farm | BOCORWF1 | NSW | 104.08 | 104.08 | 104.08 | 104.08 | 104.08 | 104.08 | 104.08 | 104.08 | 104.08 | 104.08 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18 | 113.18
Bodangora Wind Farm | BODWF1 | NSW | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19 | 113.19
Bulgana Green Power Hub - Wind Farm | BULGANA1 | VIC | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4
Canunda Wind Farm | CNUNDAWF | SA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
Capital Wind Farm | CAPTL_WF | NSW | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7 | 140.7
Cathedral Rocks Wind Farm | CATHROCK | SA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 0 | 0 | 0 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 0 | 0
Cattle Hill Wind Farm | CTHLWF1 | TAS | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
Challicum Hills Wind Farm | CHALLHWF | VIC | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5
Cherry Tree Wind Farm | CHYTWF1 | VIC | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 53.6 | 53.6 | 53.6 | 53.6 | 53.6 | 53.6 | 53.6 | 53.6 | 53.6 | 53.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6
Clements Gap Wind Farm | CLEMGPWF | SA | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 56.7
Collector Wind Farm | COLWF01 | NSW | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 124.2 | 210.6 | 210.6 | 210.6 | 210.6 | 210.6 | 210.6 | 210.6 | 210.6 | 210.6 | 124.2 | 218.7 | 218.7 | 218.7 | 218.7 | 218.7 | 218.7 | 218.7 | 218.7 | 218.7 | 218.7
Coopers Gap Wind Farm | COOPGWF1 | QLD | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97 | 439.97
Crookwell 2 Wind Farm | CROOKWF2 | NSW | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91
Crowlands Wind Farm | CROWLWF1 | VIC | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95 | 79.95
Crudine Ridge Wind Farm | CRURWF1 | NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01 | 138.01
Cullerin Range Wind Farm | CULLRGWF | NSW | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Dulacca Wind Farm | DULAWF1 | QLD | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 172.98 | 172.98 | 172.98 | 172.98 | 172.98 | 172.98 | 172.98 | 172.98 | 172.98 | 172.98
Dundonnell Wind Farm | DUNDWF1 | VIC | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
Dundonnell Wind Farm | DUNDWF2 | VIC | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 41.8 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2 | 46.2
Dundonnell Wind Farm | DUNDWF3 | VIC | 78.3 | 78.3 | 78.3 | 78.3 | 78.3 | 78.3 | 78.3 | 78.3 | 78.3 | 78.3 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8
Elaine Wind Farm | ELAINWF1 | VIC | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 59.4 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6
Granville Harbour Wind Farm | GRANWF1 | TAS | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6 | 111.6
Gullen Range Wind Farm | GULLRWF1 | NSW | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5
Gullen Range Wind Farm 2 | GULLRWF2 | NSW | 105.4 | 105.4 | 105.4 | 105.4 | 105.4 | 105.4 | 105.4 | 105.4 | 105.4 | 105.4 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67 | 110.67
Gunning Wind Farm | GUNNING1 | NSW | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
Hallett 4 North Brown Hill Wind Farm | NBHWF1 | SA | 88.2 | 88.2 | 88.2 | 88.2 | 88.2 | 88.2 | 88.2 | 88.2 | 88.2 | 88.2 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98 | 131.98
Hallett 5 The Bluff Wind Farm | BLUFF1 | SA | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5 | 52.5
Hallett Stage 1 Brown Hill Wind Farm | HALLWF1 | SA | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5 | 94.5
Hallett Stage 2 Hallett Hill Wind Farm | HALLWF2 | SA | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
Hornsdale Wind Farm Stage 1 | HDWF1 | SA | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Hornsdale Wind Farm Stage 2 | HDWF2 | SA | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Hornsdale Wind Farm Stage 3 | HDWF3 | SA | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99 | 108.99
Kaban Green Power Hub - Wind Farm | KABANWF1 | QLD | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98 | 151.98
Kennedy Energy Park Wind Farm | KEPWF1 | QLD | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2 | 43.2
Kiata Wind Farm | KIATAWF1 | VIC | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 29.7 | 31.05 | 31.05 | 31.05 | 31.05 | 31.05 | 31.05 | 31.05 | 31.05 | 31.05 | 31.05
Lake Bonney 1 Wind Farm | LKBONNY1 | SA | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5 | 80.5
Lake Bonney 2 Wind Farm | LKBONNY2 | SA | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
Lake Bonney 3 Wind Farm | LKBONNY3 | SA | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
Lincoln Gap Wind Farm - Stage 2 | LGAPWF2 | SA | 38.4 | 38.4 | 38.4 | 38.4 | 38.4 | 38.4 | 38.4 | 38.4 | 38.4 | 38.4 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
Lincoln Gap Wind Farm - stage 1 | LGAPWF1 | SA | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5
Macarthur Wind Farm | MACARTH1 | VIC | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
Moorabool Wind Farm | MOORAWF1 | VIC | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312 | 312
Mortlake South Wind Farm | MRTLSWF1 | VIC | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
Mortons Lane Wind Farm | MLWF1 | VIC | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5
Mount Emerald Wind Farm | MEWF1 | QLD | 166.95 | 166.95 | 166.95 | 166.95 | 166.95 | 166.95 | 166.95 | 166.95 | 166.95 | 166.95 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46 | 180.46
Mount Millar Wind Farm | MTMILLAR | SA | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28 | 72.28
Mt Gellibrand Wind Farm | MTGELWF1 | VIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.88 | 99.88 | 114.84 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 99.88 | 99.88 | 114.84 | 132 | 132 | 132 | 132 | 132 | 132 | 132
Mt Mercer Wind Farm | MERCER01 | VIC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2 | 131.2
Murra Warra Wind Farm - stage 1 | MUWAWF1 | VIC | 176.04 | 176.04 | 176.04 | 176.04 | 176.04 | 176.04 | 176.04 | 176.04 | 176.04 | 176.04 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7 | 225.7
Murra Warra Wind Farm - stage 2 | MUWAWF2 | VIC | 189.24 | 189.24 | 189.24 | 189.24 | 189.24 | 189.24 | 189.24 | 189.24 | 189.24 | 189.24 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209 | 209
Musselroe Wind Farm | MUSSELR1 | TAS | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
Oaklands Hill Wind Farm | OAKLAND1 | VIC | 40.99 | 40.99 | 40.99 | 40.99 | 40.99 | 40.99 | 40.99 | 40.99 | 40.99 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
Port Augusta Renewable Energy Park - Wind | PAREPW1 | SA | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
Portland Wind Farm | PORTWF | VIC | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7
Salt Creek Wind Farm | SALTCRK1 | VIC | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 37.5 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
Sapphire Wind Farm | SAPHWF1 | NSW | 155.7 | 155.7 | 155.7 | 155.7 | 155.7 | 155.7 | 155.7 | 155.7 | 155.7 | 155.7 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
Silverton Wind Farm | STWF1 | NSW | 119.48 | 119.48 | 119.48 | 119.48 | 119.48 | 119.48 | 119.48 | 119.48 | 119.48 | 119.48 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01 | 198.01
Snowtown S2 Wind Farm | SNOWNTH1 | SA | 133.2 | 133.2 | 133.2 | 133.2 | 133.2 | 133.2 | 133.2 | 133.2 | 133.2 | 133.2 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
Snowtown S2 Wind Farm | SNOWSTH1 | SA | 116.55 | 116.55 | 116.55 | 116.55 | 116.55 | 116.55 | 116.55 | 116.55 | 116.55 | 116.55 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
Snowtown Wind Farm | SNOWTWN1 | SA | 65.8 | 65.8 | 65.8 | 65.8 | 65.8 | 65.8 | 65.8 | 65.8 | 65.8 | 65.8 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7
Starfish Hill Wind Farm | STARHLWF | SA | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 0 | 0 | 0
Stockyard Hill Wind Farm | STOCKYD1 | VIC | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99 | 510.99
Taralga Wind Farm | TARALGA1 | NSW | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8 | 106.8
Waterloo Wind Farm | WATERLWF | SA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111
Waterloo Wind Farm | WATERLWF | SA | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8
Wattle Point Wind Farm | WPWF | SA | 90.75 | 90.75 | 90.75 | 90.75 | 90.75 | 90.75 | 90.75 | 0 | 0 | 0 | 90.75 | 90.75 | 90.75 | 90.75 | 90.75 | 90.75 | 90.75 | 0 | 0 | 0 | 90.75 | 90.75 | 90.75 | 90.75 | 90.75 | 90.75 | 90.75 | 0 | 0 | 0
Waubra Wind Farm | WAUBRAWF | VIC | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192
White Rock Wind Farm - Stage 1 | WRWF1 | NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48 | 172.48
Willogoleche Wind Farm | WGWF1 | SA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36 | 119.36
Woodlawn Wind Farm | WOODLWN1 | NSW | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
Woolnorth Wind Farm | WOOLNTH1 | TAS | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75 | 139.75
Yaloak South Wind Farm | YSWF1 | VIC | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7
Yambuk Wind Farm | YAMBUKWF | VIC | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Yendon Wind Farm | YENDWF1 | VIC | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 102.6 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 127.3 | 144.4 | 144.4 | 144.4 | 144.4 | 144.4 | 144.4 | 144.4 | 144.4 | 144.4 | 144.4
Committed generators 1
Generator | DUID | Region | Summer Peak 2023-24: Summer Peak; Summer Typical 2023-24: Summer Typical; Winter 2023: Winter
|  |  | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Kurri Kurri OCGT | Kurri Kurri 1 | NSW | 0 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 0 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 0 | 0 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330
Kurri Kurri OCGT | Kurri Kurri 2 | NSW | 0 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 0 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 0 | 0 | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 330
Tallawarra B* | Tallawarra B | NSW | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 318 | 0 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Kidston | Kidston Pumped Storage Hydro 1 | QLD | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 0 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
Snowy 2.0 | SNO2PH01 | NSW | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 244.4 | 366.7 | 366.7 | 366.7 | 366.7
Snowy 2.0 | SNO2PH02 | NSW | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 244.4 | 366.7 | 366.7 | 366.7 | 366.7
Snowy 2.0 | SNO2PH03 | NSW | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 244.4 | 366.7 | 366.7 | 366.7 | 366.7
Snowy 2.0 | SNO2PH04 | NSW | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 244.4 | 366.7 | 366.7 | 366.7 | 366.7
Snowy 2.0 | SNO2PH05 | NSW | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 244.4 | 366.7 | 366.7 | 366.7 | 366.7
Snowy 2.0 | SNO2PH06 | NSW | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 366.7 | 366.7 | 366.7 | 366.7 | 366.7 | 0 | 0 | 0 | 0 | 0 | 244.4 | 366.7 | 366.7 | 366.7 | 366.7
Girgarre Solar Farm | Girgarre Solar Farm | VIC | 0 | 69.54 | 69.54 | 69.54 | 69.54 | 69.54 | 69.54 | 69.54 | 69.54 | 69.54 | 0 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81 | 0 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81 | 75.81
Glenrowan Solar Farm | Glenrowan Solar Farm | VIC | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 0 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98 | 101.98
Mannum Solar Farm 2* | MANSF2 | SA | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98 | 29.98
Metz Solar Farm | METZSF1 | NSW | 107.08 | 107.08 | 107.08 | 107.08 | 107.08 | 107.08 | 107.08 | 107.08 | 107.08 | 107.08 | 111.72 | 111.72 | 111.72 | 111.72 | 111.72 | 111.72 | 111.72 | 111.72 | 111.72 | 111.72 | 115.02 | 115.02 | 115.02 | 115.02 | 115.02 | 115.02 | 115.02 | 115.02 | 115.02 | 115.02
Riverina Solar Farm | Riverina Solar Farm | NSW | 0 | 0 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 0 | 0 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 0 | 0 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4 | 32.4
Sebastopol Solar Farm | SEBSF1 | NSW | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
Stubbo Solar Farm | Stubbo Solar Farm | NSW | 0 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 0 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 0 | 200 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
Walla Walla Solar Farm | WLWLSF1 | NSW | 0 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 0 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 0 | 76.8 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76
Walla Walla Solar Farm | WLWLSF2 | NSW | 0 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 0 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 0 | 76.8 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76 | 149.76
Wandoan South Solar Farm - stage 1 | WANDSF1 | QLD | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 0 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
Wellington North Solar Farm (Lightsource) | WELNSF1 | NSW | 0 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 0 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 0 | 0 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99 | 329.99
Wollar Solar Farm | WOLARSF1 | NSW | 140 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 140 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 0 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
Woolooga Solar Farm | WOOLGSF1 | QLD | 157.53 | 157.53 | 157.53 | 157.53 | 157.53 | 157.53 | 157.53 | 157.53 | 157.53 | 157.53 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95 | 175.95
Wunghnu Solar Farm | WUNUSF1 | VIC | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 0 | 0 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
Clarke Creek Wind Farm | CLRKCWF1 | QLD | 0 | 154 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 0 | 231 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 0 | 77 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03 | 338.03
Clarke Creek Wind Farm | CLRKCWF2 | QLD | 0 | 23 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 0 | 69 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 0 | 23 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97 | 100.97
Crookwell 3 Wind Farm | Crookwell 3 Wind Farm | NSW | 0 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 0 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 0 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6 | 57.6
Flyers Creek Wind Farm | Flyers Creek Wind Farm | NSW | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 0 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54 | 145.54
Golden Plains Wind Farm East | Golden Plains Wind Farm East | VIC | 0 | 0 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 0 | 0 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 0 | 0 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4 | 756.4
Goyder South Wind Farm 1A | GSWF1A | SA | 140.71 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 140.71 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 0 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98 | 200.98
Goyder South Wind Farm 1B | GSWF1B | SA | 0 | 55.5 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 0 | 55.5 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 0 | 0 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69 | 195.69
Hawkesdale Wind Farm | Hawkesdale Wind Farm | VIC | 0 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 0 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 0 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
Ryan Corner Wind Farm | Ryan Corner Wind Farm | VIC | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 0 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4 | 218.4
Rye Park Wind Farm | Rye Park Wind Farm | NSW | 0 | 225.06 | 225.06 | 225.06 | 225.06 | 225.06 | 225.06 | 225.06 | 225.06 | 225.06 | 0 | 335.28 | 335.28 | 335.28 | 335.28 | 335.28 | 335.28 | 335.28 | 335.28 | 335.28 | 0 | 386.1 | 386.1 | 386.1 | 386.1 | 386.1 | 386.1 | 386.1 | 386.1 | 386.1
Wambo Wind Farm | Wambo Wind Farm | QLD | 0 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 0 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 0 | 0 | 252 | 252 | 252 | 252 | 252 | 252 | 252 | 252
Anticipated projects
Generator | DUID | Region | Summer Peak 2023-24: Summer Peak; Summer Typical 2023-24: Summer Typical; Winter 2023: Winter
|  |  | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
SA Hydrogen Turbine | SA Hydrogen Turbine | SA | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Borumba | QEJP - Borumba | QLD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1998 | 1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1998 | 1998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1998 | 1998
Aramara Solar Farm | Aramara Solar Farm | QLD | 0 | 0 | 0 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 0 | 0 | 0 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 0 | 0 | 0 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4
Banksia Solar Farm | Banksia Solar Farm | QLD | 0 | 0 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 58.8 | 0 | 0 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | 0 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Culcairn Solar Farm | Culcairn Solar Farm | NSW | 0 | 0 | 332.44 | 332.44 | 332.44 | 332.44 | 332.44 | 332.44 | 332.44 | 332.44 | 0 | 0 | 349.98 | 349.98 | 349.98 | 349.98 | 349.98 | 349.98 | 349.98 | 349.98 | 0 | 0 | 19.98 | 349.98 | 349.98 | 349.98 | 349.98 | 349.98 | 349.98 | 349.98
Cultana Solar Farm | Cultana Solar Farm | SA | 0 | 0 | 0 | 279.76 | 279.76 | 279.76 | 279.76 | 279.76 | 279.76 | 279.76 | 0 | 0 | 0 | 279.76 | 279.76 | 279.76 | 279.76 | 279.76 | 279.76 | 279.76 | 0 | 0 | 0 | 279.76 | 279.76 | 279.76 | 279.76 | 279.76 | 279.76 | 279.76
Derby Solar Farm | Derby Solar Farm | VIC | 0 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 0 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 0 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1 | 95.1
Frasers Solar Farm | Frasers Solar Farm | VIC | 0 | 0 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 0 | 0 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 0 | 0 | 0 | 77 | 77 | 77 | 77 | 77 | 77 | 77
Horsham Solar Farm | Horsham Solar Farm | VIC | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 0 | 0 | 0 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8
Lockhart Hybrid Facility - Solar | Lockhart Hybrid Facility - Solar | NSW | 0 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
Quorn Park Solar Farm | Quorn Park Solar Farm | NSW | 0 | 0 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 0 | 0 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 0 | 0 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86 | 79.86
Tamworth Solar Farm | Tamworth Solar Farm | NSW | 0 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 0 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65
Tilbuster Solar Farm | Tilbuster Solar Farm | NSW | 0 | 0 | 0 | 200.64 | 200.64 | 200.64 | 200.64 | 200.64 | 200.64 | 200.64 | 0 | 0 | 0 | 200.64 | 200.64 | 200.64 | 200.64 | 200.64 | 200.64 | 200.64 | 0 | 0 | 0 | 200.64 | 200.64 | 200.64 | 200.64 | 200.64 | 200.64 | 200.64
MacIntyre Wind Farm | MacIntyre Wind Farm | QLD | 0 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 0 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 0 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4 | 923.4
Uungula Wind Farm | Uungula Wind Farm | NSW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 0 | 0 | 138 | 414 | 414 | 414 | 414 | 414 | 414 | 414
Woolsthorpe Wind Farm | Woolsthorpe Wind Farm | VIC | 0 | 0 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 0 | 0 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 0 | 0 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2 | 73.2
Existing, Committed and Anticipated batteries
Generator | DUID | Region | Summer Peak 2023-24: Summer Peak; Summer Typical 2023-24: Summer Typical; Winter 2023: Winter
|  |  | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Adelaide Desalination Plant BESS | ADPBA1G | SA | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Aldoga BESS Stage 1 | Aldoga BESS Stage 1 | QLD | 0 | 0 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 0 | 0 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 0 | 0 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
Ballarat Energy Storage System | BALBG1 | VIC | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 19.2 | 19.2 | 19.2 | 19.2 | 29.9 | 29.9 | 29.9 | 29.9 | 29.9 | 29.9 | 19.9 | 19.9 | 19.9 | 19.9 | 29.9 | 29.9 | 29.9 | 29.9 | 29.9 | 29.9 | 19.9 | 19.9 | 19.9 | 19.9
Blyth BESS | Blyth BESS | SA | 0 | 160 | 193.98 | 193.98 | 193.98 | 193.98 | 193.98 | 193.98 | 193.98 | 193.98 | 0 | 160 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Bolivar Waste Water Treatment BESS | BOWWBA1G | SA | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Bouldercombe Battery project | BBATTERY | QLD | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Broken Hill BESS | Broken Hill BESS | NSW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Bulgana Green Power Hub BESS | BULBESG1 | VIC | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Bungama Solar BESS | Bungama Solar BESS | SA | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Capital Battery | CAPBES1G | NSW | 4.95 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 4.95 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99 | 0 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99 | 99.99
Chinchilla BESS | Chinchilla BESS | QLD | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Christies Beach Wastewater Treatment Plant BESS | CBWWBA1G | SA | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Dalrymple BESS | DALNTH01 | SA | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0
Darlington Point Energy Storage System | DPNTBG1 | NSW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Eraring Big Battery | Eraring Big Battery | NSW | 0 | 0 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 0 | 0 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 460 | 0 | 0 | 0 | 460 | 460 | 460 | 460 | 460 | 460 | 460
Gannawarra Energy Storage System | GANNBG1 | VIC | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33 | 25.33
Gnarwarre BESS | Gnarwarre BESS | VIC | 0 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 0 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 0 | 0 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250
Happy Valley Reservoir BESS | HVWWBA1G | SA | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Hazelwood BESS | HBESSG1 | VIC | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Hornsdale Power Reserve Unit 1 | HPRG1 | SA | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Koorangie Energy Storage System | Koorangie Energy Storage System | VIC | 0 | 0 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 0 | 0 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 0 | 0 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185
Lake Bonney BESS | LBBG1 | SA | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
Liddell BESS | Liddell BESS | NSW | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 0 | 0 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
Lincoln Gap Wind Farm BESS | Lincoln Gap Wind Farm BESS | SA | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Lockhart Hybrid Facility - Battery | Lockhart Hybrid Facility - Battery | NSW | 0 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
Melbourne Renewable Energy Hub - Side A | Melbourne Renewable Energy Hub - Side A | VIC | 0 | 0 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 0 | 0 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 0 | 0 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
Mornington BESS | Mornington BESS | VIC | 0 | 0 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 0 | 0 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 0 | 0 | 0 | 240 | 240 | 240 | 240 | 240 | 240 | 240
Mortlake Battery | Mortlake Battery | VIC | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 0 | 0 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300
Mt Fox BESS | Mt Fox BESS | QLD | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 0 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
New England Solar Farm BESS | New England Solar Farm BESS | NSW | 0 | 0 | 50 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 50 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 50 | 100 | 200 | 200 | 200 | 200 | 200 | 200
Orana BESS | Orana BESS | NSW | 0 | 0 | 368.46 | 368.46 | 368.46 | 368.46 | 368.46 | 368.46 | 368.46 | 368.46 | 0 | 0 | 408.48 | 408.48 | 408.48 | 408.48 | 408.48 | 408.48 | 408.48 | 408.48 | 0 | 0 | 408.48 | 408.48 | 408.48 | 408.48 | 408.48 | 408.48 | 408.48 | 408.48
Philip Island BESS | PIBESSG1 | VIC | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Queanbeyan BESS | QBYNBG1 | NSW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Quorn Park BESS | Quorn Park BESS | NSW | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
Rangebank BESS | Rangebank BESS | VIC | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Richmond Valley BESS | Richmond Valley BESS | NSW | 0 | 0 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 0 | 0 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 0 | 0 | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 275
Riverina Energy Storage System 1 | RESS1G | NSW | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Riverina Energy Storage System 2 | RIVNBG2 | NSW | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
Sapphire Wind Farm BESS | Sapphire Wind Farm Battery | NSW | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Stanwell BESS | Stanwell BESS | QLD | 0 | 0 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 0 | 0 | 0 | 150 | 150 | 150 | 150 | 150 | 150
Swanbank BESS | Swanbank BESS | QLD | 0 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 0 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 0 | 0 | 0 | 250 | 250 | 250 | 250 | 250 | 250 | 250
Tailem Bend Battery Project | TB2BG1 | SA | 0 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 0 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 0 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5
Tamworth BESS | Tamworth BESS | NSW | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Tarong BESS | Tarong BESS | QLD | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 0 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Templers BESS | Templers BESS | SA | 0 | 30 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 0 | 30 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 0 | 0 | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 111
Terang BESS | TRGBESS | VIC | 0 | 0 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 0 | 0 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 0 | 0 | 0 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5 | 101.5
Torrens Island BESS | TIBG1 | SA | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7 | 250.7
Ulinda Park BESS | Ulinda Park BESS | QLD | 0 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 0 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 0 | 0 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96 | 154.96
Victorian Big Battery | VBBG1 | VIC | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
Wallgrove Grid Battery project | WALGRVG1 | NSW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Wandoan South BESS | WANDBG1 | QLD | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
Waratah Super Battery | WARATAH | NSW | 0 | 0 | 107.71 | 107.71 | 107.71 | 107.71 | 107.71 | 777.6 | 777.6 | 777.6 | 0 | 0 | 150.04 | 150.04 | 150.04 | 150.04 | 150.04 | 850.17 | 850.17 | 850.17 | 0 | 0 | 150.04 | 150.04 | 150.04 | 150.04 | 150.04 | 850.17 | 850.17 | 850.17
Western Downs Battery | Western Downs Battery | QLD | 0 | 198.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 0 | 198.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 0 | 0 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8 | 254.8
Wooreen Energy Storage System | Wooreen Battery | VIC | 0 | 0 | 0 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 0 | 0 | 0 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 0 | 0 | 0 | 0 | 350 | 350 | 350 | 350 | 350 | 350
Additional projects
Generator | DUID | Region | Summer Peak 2023-24: Summer Peak; Summer Typical 2023-24: Summer Typical; Winter 2023: Winter
|  |  | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
Coppabella Wind Farm | Coppabella Wind Farm | NSW | 0 | 0 | 40.02 | 270.48 | 270.48 | 270.48 | 270.48 | 270.48 | 270.48 | 270.48 | 0 | 0 | 40.02 | 270.48 | 270.48 | 270.48 | 270.48 | 270.48 | 270.48 | 270.48 | 0 | 0 | 0 | 200.1 | 270.48 | 270.48 | 270.48 | 270.48 | 270.48 | 270.48
Derby Solar Project BESS | Derby Solar Project BESS | VIC | 0 | 0 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 0 | 0 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 0 | 0 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Fulham Solar Farm | Fulham Solar Farm | VIC | 0 | 0 | 0 | 83.28 | 83.28 | 83.28 | 83.28 | 83.28 | 83.28 | 83.28 | 0 | 0 | 0 | 83.28 | 83.28 | 83.28 | 83.28 | 83.28 | 83.28 | 83.28 | 0 | 0 | 0 | 83.28 | 83.28 | 83.28 | 83.28 | 83.28 | 83.28 | 83.28
Fulham Solar Farm BESS | Fulham Solar Farm BESS | VIC | 0 | 0 | 0 | 64.8 | 64.8 | 64.8 | 64.8 | 64.8 | 64.8 | 64.8 | 0 | 0 | 0 | 64.8 | 64.8 | 64.8 | 64.8 | 64.8 | 64.8 | 64.8 | 0 | 0 | 0 | 64.8 | 64.8 | 64.8 | 64.8 | 64.8 | 64.8 | 64.8
Goulburn River BESS | Goulburn River BESS | NSW | 0 | 0 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 0 | 0 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 0 | 0 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49
Horsham Solar Farm BESS | Horsham Solar Farm BESS | VIC | 0 | 0 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 0 | 0 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 0 | 0 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01 | 50.01
Kiamal Solar Farm – Stage 2 | Kiamal Solar Farm - Stage 2 | VIC | 0 | 0 | 0 | 0 | 141.9 | 141.9 | 141.9 | 141.9 | 141.9 | 141.9 | 0 | 0 | 0 | 0 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 0 | 0 | 0 | 150.04 | 150.04 | 150.04 | 150.04 | 150.04 | 150.04 | 150.04
Kiamal Solar Farm – Stage 2 BESS | Kiamal Solar Farm Stage 2 BESS | VIC | 0 | 0 | 0 | 0 | 141.9 | 141.9 | 141.9 | 141.9 | 141.9 | 141.9 | 0 | 0 | 0 | 0 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 0 | 0 | 0 | 150.04 | 150.04 | 150.04 | 150.04 | 150.04 | 150.04 | 150.04
Kogan Gas | Kogan Gas | QLD | 0 | 0 | 0 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 0 | 0 | 0 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200
Limondale BESS | Limondale BESS | NSW | 0 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
New England Solar Farm - stage 2 | New England Solar Farm 2 | NSW | 0 | 0 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 0 | 0 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 0 | 0 | 180 | 320 | 320 | 320 | 320 | 320 | 320 | 320
Silver City Energy Storage | Silver City Energy Storage | NSW | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200
Smithfield BESS | Smithfield BESS | NSW | 0 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 0 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65
Note: Seasonal ratings for these Additional projects are assumed to be equal to their nameplate capacity, except for Kogan Gas and SA Hydrogen Turbine which are based on New Entrant hydrogen-based gas turbine.

## Reserves
Go to Assumptions Summary
Initial regional reserve
In the Capacity Outlook models, each region must have a minimum level of firm capacity available. Firm capacity is allowed to be shared across interconnected regions based on interconnector capabilities and available capacity in neighbouring regions.
These reserve requirements are used in capacity outlook models to deliver sufficient capacity to meet reliability requirements, and the resulting capacity is validated through time-sequential modelling.
The initial regional reserve requirements are based on the largest generating unit in the July 2023 Generation Information.
These initial regional reserve requirements for each year in the outlook period are subject to change based on detailed analysis of reliability outcomes from time-sequential modelling to ensure the Reliability Standard is maintained. Details are provided in the ISP Methodology.
Region | Initial regional reserve requirements (MW)
NSW | 705
QLD | 710
SA | 195
TAS | 140
VIC | 550
Note: Regional reserve requirements are based on the 2023-24 peak summer ratings of the largest unit in each region from the July 2023 Generation Information publication.

## Generation limits
Go to Assumptions Summary
Generator operating limits
Coal minimum stable level are based on AEMO internal analysis of historical generation and operational experience
For Minimum Stable Level values applied to AEMO's Time-sequential model, go to the GPG Minimum Stable Level Sheet. |  |  | Link: | GPG Minimum Stable Levels
Coal minimum stable level
Generator Station | Generating unit | Minimum Stable Level (MW)
Bayswater | BW01 | 250
Bayswater | BW02 | 250
Bayswater | BW03 | 250
Bayswater | BW04 | 250
Eraring | ER01 | 210
Eraring | ER02 | 210
Eraring | ER03 | 210
Eraring | ER04 | 210
Mt Piper | MP1 | 270
Mt Piper | MP2 | 270
Vales Point B | VP5 | 250
Vales Point B | VP6 | 250
Callide B | CALL_B_1 | 155
Callide B | CALL_B_2 | 155
Callide C | CPP_3 | 180
Callide C | CPP_4 | 180
Gladstone | GSTONE1 | 110
Gladstone | GSTONE2 | 110
Gladstone | GSTONE3 | 110
Gladstone | GSTONE4 | 110
Gladstone | GSTONE5 | 110
Gladstone | GSTONE6 | 110
Kogan Creek | KPP_1 | 330
Millmerran | MPP_1 | 200
Millmerran | MPP_2 | 200
Stanwell | STAN-1 | 140
Stanwell | STAN-2 | 140
Stanwell | STAN-3 | 140
Stanwell | STAN-4 | 140
Tarong | TARONG#1 | 140
Tarong | TARONG#2 | 140
Tarong | TARONG#3 | 140
Tarong | TARONG#4 | 140
Tarong North | TNPS1 | 180
Loy Yang B | LOYYB1 | 320
Loy Yang B | LOYYB2 | 320
Loy Yang A Power Station | LYA1 | 300
Loy Yang A Power Station | LYA2 | 300
Loy Yang A Power Station | LYA3 | 300
Loy Yang A Power Station | LYA4 | 300
Yallourn W | YWPS1 | 200
Yallourn W | YWPS2 | 200
Yallourn W | YWPS3 | 200
Yallourn W | YWPS4 | 200

## Maintenance
Go to Assumptions Summary
Maintenance rate
The percentage of time per year that a generator is expected to be out of service for maintenance.
Existing generators |  |  | New entrant technologies
Generator type | Proportion of time out (%) | Equivalent average days per year on planned outage | Generator type | Proportion of time out (%) | Equivalent average days per year on planned outage
Black Coal | 5.4795 | 20 | OCGT (small GT) | 0.82192 | 3
Brown Coal | 5.4795 | 20 | OCGT (large GT) | 1.3699 | 5
Hydro | 0.27397 | 1 | CCGT | 3.5068 | 12.8
CCGT | 5.4795 | 20 | CCGT with CCS | 3.5068 | 12.8
OCGT | 1.3699 | 5 | Biomass | 6.2466 | 22.8
Gas-powered steam turbine | 0.68493 | 2.5 | Large scale Solar PV | 0 | 0
Reciprocating Engine | 1.6438 | 6 | Solar Thermal (15hrs storage) | 1.9178 | 7
Large scale Solar PV | 0 | 0 | Battery storage (1hr storage) | 0 | 0
Solar Thermal | 0 | 0 | Battery storage (2hrs storage) | 0 | 0
Battery storage | 0 | 0 | Battery storage (4hrs storage) | 0 | 0
Wind | 0 | 0 | Battery Storage (8hrs storage) | 0 | 0
Hydrogen-based gas turbines | 1.37 | 5 | Wind | 0 | 0
Source: GHD 2018 AEMO costs and technical parameter review. |  |  | Wind - offshore (fixed) | 0 | 0
Note: |  |  | Wind - offshore (floating) | 0 | 0
1. Maintenance for wind and solar technologies has been considered in the renewable generation profiles. |  |  | Pumped Hydro (8hrs storage) | 0.27397 | 1
2. Existing hydro plants are using the maintenace rate of new pumped hydro plants. |  |  | Pumped Hydro (24hrs storage) | 0.27397 | 1
3. Values for Kogan Gas and Sa Hydrogen Turbine are sourced from Aurecon 2022 Costs and Technical Parameter Review. |  |  | Pumped Hydro (48hrs storage) | 0.27397 | 1
|  |  | BOTN - Cethana | 0.27397 | 1
|  |  | Hydrogen reciprocating engines | 0.73973 | 2.7
Notes:
1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
2. Pumped Hydro assumptions are sourced from GHD 2018 AEMO costs and technical parameter review.
3. Maintenance for wind and solar technologies has been considered within the renewable generation profiles.
4. Battery storage maintenance rate is included in Aurecon's Equivalent forced outage rate (EFOR).

## Generator Reliability Settings
Go to Assumptions Summary
Generator Reliability Settings
Existing generator outage rates are based on the most recent four years of outage data that have been calculated for the 2023 ESOO. The below rates represent a four year average for respective technology types.
The forced outage rates published here, and applied in the ISP use technology aggregations to protect confidentiality. The ESOO applies the station-level forced outage rates.
Long Duration outages reflect full outages with duration of more than 5 months.
Forecast full and partial outage rates are also provided below. All other technology rates remain flat.
Further details on the application of the forced outage rates across publications is provided in the IASR Report.
Existing generators - Long Duration Outages
Fuel Type | Full outage (% of time) | Mean time to repair (hrs)
All Coal Average | 0.9002% | 5621.5288
OCGT | 0.7744% | 2561.7305
Hydro | 0.09648% | 2870.056
Other Gas and Liquid | 0.4882% | 6440.6087
Existing generators Outages (Outage rates for year 2023-24) | [6 empty] | New entrant technologies
Fuel type | Forced Outage Rate (%) |  | Mean time to repair (hrs) |  | Partial Outage Derating Factor (%) |  | Fuel type | Forced Outage Rate (%) |  | Mean time to repair (hrs) |  | Partial Outage Derating Factor (%)
| Full outage (% of time) | Partial outage (% of time) | Full outage | Partial outage |  |  |  | Full outage (% of time) | Partial outage (% of time) | Full outage | Partial outage
Brown Coal | 7.75% | 11.56% | 90.05 | 12.2 | 17.91% |  | OCGT (small GT) | 2 |  | 75
Black Coal NSW | 6.31% | 31.46% | 157.62 | 33.97 | 16.6% |  | OCGT (large GT) | 2 |  | 22
Black Coal QLD | 6.75% | 12.86% | 185 | 56.42 | 25.16% |  | CCGT | 3.5 |  | 54
OCGT | 7.21% | 1.12% | 44.08 | 106.48 | 9.99% |  | CCGT with CCS | 3.5 |  | 54
Small peaking plants | 9.58% | 0.32% | 150.2 | 189.52 | 33.7% |  | Biomass | 4 |  | 22
Hydro | 5.11% | 1.71% | 38.1 | 473.44 | 15.18% |  | Large scale Solar PV
CCGT + Steam Turbine | 5.04% | 1.66% | 61.19 | 40.35 | 15.21% |  | Solar Thermal (15hrs Storage) | 3
Batteries | 1.84% | - | 26.05 | - | - |  | Battery storage (1hr storage) | 2.25 |  | 48
Notes: | [6 empty] | Battery storage (2hrs storage) | 2.25 |  | 48
Gas-fired steam turbines: Newport and Torrens Island | [6 empty] | Battery storage (4hrs storage) | 2.25 |  | 48
Forced Outage Rate (%) - The percentage of time per year that a generator is expected to be out of service due to forced outage. | [6 empty] | Battery Storage (8hrs storage) | 2.25 |  | 48
Mean time to repair (hrs) - The average time take to return a generating unit to service | [6 empty] | Wind
Partial Outage Derating Factor - The loss of capacity during a partial outage, relative to generator unit rating. If the outage factor is 20%, the generator will operate at 80% capacity during a partial outage. | [6 empty] | Wind - offshore (fixed)
Small peaking plants have been classified as less than 150MW, but also includes Colongra GT. Liquid-fuelled and reciprocating engines are also included. | [6 empty] | Wind - offshore (floating)
OCGT have been classified as greater than 150MW, but also includes Bell Bay/Tamar OCGT. | [6 empty] | Pumped Hydro (8hrs storage) | 1 |  | 27
Outages for wind and solar technologies has been considered in the renewable generation profile. | [6 empty] | Pumped Hydro (24hrs storage) | 1 |  | 27
[7 empty] | Pumped Hydro (48hrs storage) | 1 |  | 27
[7 empty] | BOTN - Cethana | 1 |  | 27
[7 empty] | Hydrogen-based gas turbines | 2 |  | 22
[7 empty] | Hydrogen reciprocating engines | 2 |  | 22
Notes:
1. Sourced from Aurecon 2022 Costs and Technical Parameter review.
2. Pumped Hydro assumptions are sourced from GHD 2018 AEMO costs and technical parameter review.
3. Mean time to repaired is based on existing generator data where possible.
4. Outages for wind and solar technologies has been considered in the renewable generation profile.
5. Values for hydrogen-based gas turbines in this table are sourced from Aurecon 2022 Costs and Technical Parameter Review, and will only be used for Kogan Gas and SA Hydrogen Turbine.
Outage rate projections
Existing generators Full Outage Rate Forecast (%)
Fuel type | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33
Brown Coal | 7.751% | 7.367% | 7.808% | 7.853% | 8.103% | See "All Coal Average"
Black Coal NSW | 2023-24: 6.314%; 2024-25: 5.892%; 2025-26: 6.112%; 2026-27: 6.678%; 2027-28: 7.281%
Black Coal QLD | 2023-24: 6.749%; 2024-25: 6.939%; 2025-26: 7.03%; 2026-27: 7.048%; 2027-28: 7.194%
All Coal Average | 2028-29: 6.579%; 2029-30: 6.587%; 2030-31: 6.582%; 2031-32: 6.337%; 2032-33: 6.4%
CCGT + Steam Turbine | 5.038% | 4.993% | 5.045% | 5.279% | 5.469% | 5.498% | 5.531% | 5.422% | 5.648% | 5.698%
Existing generators Partial Outage Rate Forecast (%)
Fuel type | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33
Brown Coal | 11.56% | 12.64% | 14.11% | 15.89% | 18.19% | See "All Coal Average"
Black Coal NSW | 2023-24: 31.46%; 2024-25: 28.66%; 2025-26: 28.29%; 2026-27: 18.64%; 2027-28: 19.61%
Black Coal QLD | 2023-24: 12.86%; 2024-25: 14.52%; 2025-26: 14.6%; 2026-27: 14.62%; 2027-28: 14.71%
All Coal Average | 2028-29: 14.57%; 2029-30: 14.18%; 2030-31: 15%; 2031-32: 13.64%; 2032-33: 14.23%
CCGT + Steam Turbine | 1.662% | 1.662% | 1.81% | 1.496% | 1.556% | 1.556% | 1.141% | 1.141% | 0.731% | 1.132%

## Hydro Climate Factor
Go to Assumptions Summary
Hydro Climate Factor
An inflow adjustment to capture climate risks is applied as a scalar to the historical inflow reference years
AEMO's modelling will apply the Median trajectories by default.
Median Projections
North Queensland | RCP | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Progressive Change | 4.5 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Step Change | 2.6 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Green Energy Exports | 1.9 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
South QLD, NSW, VIC | RCP | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Progressive Change | 4.5 | -3.472% | -3.858% | -4.243% | -4.629% | -5.015% | -5.401% | -5.786% | -5.814% | -5.841% | -5.868% | -5.895% | -5.923% | -5.95% | -5.977% | -6.004% | -6.032% | -6.059% | -6.086% | -6.114% | -6.141% | -6.168% | -6.195% | -6.223% | -6.25% | -6.277% | -6.305% | -6.332% | -6.703% | -7.074% | -7.446% | -7.679%
Step Change | 2.6 | -3% | -3.3% | -3.6% | -4% | -4.3% | -4.6% | -5% | -5% | -5% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.9% | -4.8% | -4.8% | -4.8% | -5.3% | -5.7% | -6.104% | -6.393%
Green Energy Exports | 1.9 | -2.796% | -3.107% | -3.418% | -3.729% | -4.039% | -4.35% | -4.661% | -4.642% | -4.623% | -4.604% | -4.585% | -4.566% | -4.547% | -4.528% | -4.509% | -4.49% | -4.471% | -4.452% | -4.433% | -4.414% | -4.395% | -4.376% | -4.357% | -4.338% | -4.319% | -4.3% | -4.281% | -4.724% | -5.167% | -5.61% | -5.868%
Tasmania | RCP | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Progressive Change | 4.5 | -1.21% | -1.345% | -1.479% | -1.614% | -1.748% | -1.882% | -2.017% | -1.989% | -1.961% | -1.933% | -1.905% | -1.877% | -1.849% | -1.821% | -1.793% | -1.765% | -1.737% | -1.709% | -1.681% | -1.654% | -1.626% | -1.598% | -1.57% | -1.542% | -1.514% | -1.486% | -1.458% | -1.464% | -1.469% | -1.475% | -1.468%
Step Change | 2.6 | -1.264% | -1.405% | -1.545% | -1.686% | -1.826% | -1.967% | -2.107% | -2.022% | -1.937% | -1.852% | -1.767% | -1.682% | -1.597% | -1.512% | -1.427% | -1.342% | -1.256% | -1.171% | -1.086% | -1.001% | -0.9161% | -0.831% | -0.7459% | -0.6608% | -0.5757% | -0.4906% | -0.4055% | -0.4241% | -0.4586% | -0.4931% | -0.4719%
Green Energy Exports | 1.9 | -1.284% | -1.427% | -1.57% | -1.713% | -1.855% | -1.998% | -2.141% | -2.035% | -1.929% | -1.822% | -1.716% | -1.61% | -1.504% | -1.398% | -1.292% | -1.185% | -1.079% | -0.9731% | -0.867% | -0.7608% | -0.6547% | -0.5485% | -0.4424% | -0.3362% | -0.2301% | -0.1239% | -0.01776% | 0% | 0% | 0% | 0.05134%

## Hydro Scheme Inflows
Go to Assumptions Summary
Hydroelectric Storage Inflows (GWh)
Queensland and Victoria schemes
Queensland and Victorian schemes will be based on long term historical inflows.
| Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Annual Total
Kuranda Weir | 14.3197 | 12.9075 | 8.8271 | 7.4834 | 5.2035 | 18.9282 | 68.2829 | 78.772 | 110.115 | 43.3021 | 20.1034 | 15.2884 | 403.5332
Koombooloomba Dam | 36.3053 | 73.6406 | 63.5406 | 51.2394 | 36.3801 | 45.0598 | 15.7066 | 21.811 | 22.9161 | 16.9442 | 22.6586 | 40.3669 | 446.5693
Hume | 30.2266 | 33.7233 | 33.7313 | 31.2467 | 21.0069 | 18.0081 | 13.9135 | 15.5105 | 16.0326 | 11.1193 | 15.2299 | 21.8133 | 261.5621
Dartmouth | 55.6328 | 65.4323 | 66.3045 | 56.378 | 32.6493 | 26.3539 | 16.0168 | 15.8832 | 17.694 | 11.5733 | 22.3146 | 34.4065 | 420.6392
Eildon | 42.7076 | 55.5742 | 40.1304 | 27.5012 | 12.1187 | 11.7573 | 3.6585 | 2.8218 | 4.0923 | 4.3094 | 11.1419 | 25.963 | 241.7762
Queensland | Feb: Victoria
Snowy scheme
The Snowy scheme will consider the influence of specific historical reference years. Data used in AEMO's modelling reflects confidential submissions from Snowy Hydro. The data below reflects interpretation of public domain data, and may not match precisely with the confidential data. https://www.snowyhydro.com.au/our-energy/water/inflows/
Blowering, Eucumbene and Guthega
Reference Year (FYE) | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Annual Total
2011 | 865.6913 | 527.6107 | 566.5134 | 663.1503 | 347.269 | 485.6217 | 380.4839 | 375.3992 | 113.0974 | 371.6624 | 498.06 | 861.1939 | 6055.753
2012 | 682.0511 | 421.4805 | 446.6444 | 504.7129 | 244.1462 | 340.1259 | 300.053 | 294.2977 | 88.4854 | 290.8707 | 391.582 | 677.1747 | 4681.6243
2013 | 549.7987 | 331.7523 | 348.0947 | 386.6747 | 181.5982 | 270.4208 | 241.4825 | 239.2594 | 72.1848 | 237.1639 | 316.7908 | 547.7091 | 3722.9299
2014 | 512.9528 | 324.3205 | 357.6385 | 439.9052 | 249.8547 | 317.6532 | 226.0187 | 219.4749 | 65.7618 | 216.2862 | 293.4551 | 507.5974 | 3730.9191
2015 | 475.341 | 282.5933 | 295.9449 | 328.7137 | 155.3044 | 238.8956 | 208.5735 | 207.9291 | 62.8622 | 206.47 | 274.4905 | 474.508 | 3211.6263
2016 | 665.0774 | 393.5352 | 408.6738 | 445.0444 | 201.0191 | 319.1451 | 291.737 | 291.3965 | 88.1532 | 289.5098 | 384.32 | 664.3393 | 4441.9507
2017 | 670.3907 | 413.2341 | 441.0653 | 507.4711 | 255.5108 | 353.3879 | 294.8726 | 289.53 | 87.0841 | 286.2484 | 385.0355 | 665.8372 | 4649.6679
2018 | 640.1975 | 383.8116 | 401.0828 | 441.9137 | 204.1451 | 310.8314 | 281.0664 | 279.2292 | 84.3201 | 276.9965 | 369.232 | 638.3369 | 4311.1631
2019 | 482.1982 | 289.0877 | 302.0964 | 332.8504 | 153.7625 | 234.1189 | 211.6999 | 210.3161 | 63.5101 | 208.6344 | 278.1063 | 480.7968 | 3247.1776
2020 | 555.0751 | 332.7789 | 347.7537 | 383.1557 | 177.0014 | 269.5024 | 243.6951 | 242.1022 | 73.1086 | 240.1663 | 320.1379 | 553.4619 | 3737.9392
2021 | 621.0918 | 372.3573 | 389.1131 | 428.7255 | 198.0527 | 301.5551 | 272.6784 | 270.8961 | 81.8037 | 268.73 | 358.2128 | 619.2867 | 4182.5031
2022 | 818.0328 | 490.4275 | 512.4963 | 564.6694 | 260.8529 | 397.1748 | 359.1416 | 356.7941 | 107.7427 | 353.9412 | 471.798 | 815.6554 | 5508.7265
Dry | 171.4276 | 99.9242 | 103.0243 | 110.6798 | 48.6636 | 81.243 | 75.1234 | 75.4922 | 22.8839 | 75.1319 | 99.2758 | 171.5853 | 1134.455
Snowy
Tasmania
The Tasmanian schemes will consider the influence of specific historical reference years.
Reference Year (FYE) | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Annual Total
2011 | 982.1065 | 1510.9521 | 1501.2597 | 882.6177 | 778.4281 | 829.4745 | 489.7261 | 308.0929 | 608.5587 | 549.7578 | 501.0767 | 1427.6891 | 10369.7396
2012 | 1450.6199 | 1683.9834 | 1036.807 | 657.0437 | 667.7885 | 287.2054 | 128.7897 | 116.9636 | 404.5966 | 573.5908 | 1122.7235 | 1121.3978 | 9251.5098
2013 | 971.4607 | 1433.5766 | 1373.6918 | 676.867 | 292.5323 | 241.8663 | 72.5811 | 24.5847 | 321.4089 | 425.5436 | 777.0809 | 505.2903 | 7116.4843
2014 | 1526.377 | 2534.7929 | 1316.2934 | 1673.4488 | 772.0572 | 460.1078 | 314.5188 | 112.8908 | 241.624 | 519.1388 | 927.4249 | 843.928 | 11242.6025
2015 | 1379.578 | 1103.0548 | 696.0691 | 732.2548 | 447.3389 | 269.2251 | 391.2982 | 61.0887 | 440.5098 | 230.7884 | 1405.987 | 1024.2403 | 8181.433
2016 | 1064.1069 | 1397.3511 | 668.5228 | 171.547 | 203.5751 | 203.9501 | 150.3885 | 141.8676 | 168.0803 | 335.762 | 2049.807 | 2052.6787 | 8607.637
2017 | 2200.9302 | 1443.3691 | 943.4581 | 1975.9386 | 996.381 | 404.0091 | 190.5817 | 199.9556 | 118.5768 | 271.8703 | 712.9215 | 577.7077 | 10035.6998
2018 | 1164.959 | 1395.2287 | 1636.4845 | 799.0718 | 283.3647 | 423.063 | 84.6822 | 206.7749 | 531.5248 | 607.4845 | 965.124 | 1075.2177 | 9172.9797
2019 | 2031.9243 | 1754.9172 | 981.7392 | 315.4639 | 506.8569 | 387.0934 | -11.4768 | 205.9508 | 241.2012 | 616.4933 | 944.1092 | 1106.9226 | 9081.1951
2020 | 2287.6441 | 1316.0493 | 853.3929 | 396.2097 | 854.4045 | 660.0899 | 180.6144 | 176.603 | 462.1835 | 1124.2055 | 1002.6674 | 910.0462 | 10224.1103
2021 | 768.0263 | 946.3277 | 920.8134 | 1160.4513 | 202.8511 | 378.7451 | 148.2794 | 409.7633 | 372.3785 | 685.8274 | 783.8579 | 950.9284 | 7728.2498
2022 | 1582.9637 | 1782.3094 | 1288.8603 | 1346.404 | 690.6256 | 136.5791 | 161.5962 | 24.7728 | 140.0135 | 228.9922 | 893.3144 | 1163.3894 | 9439.8208
Dry | 987.6401 | 832.6914 | 998.7018 | 605.5409 | 237.8379 | 156.9579 | 259.5781 | 27.7256 | 167.7432 | 138.034 | 1356.8306 | 537.6442 | 6306.9259
Tasmania

## Build costs
Go to Assumptions Summary
| Capital cost projections ($/kW, real 2023 dollars) | [6 empty] | GenCost scenario mapping
| Cost to construct new generation, excluding connection costs where these are provided in the Connection cost tab. | [7 empty] | Green Energy Exports | Step Change | Progressive Change
| These capital cost trajectories are developed by CSIRO's GALLM (see GenCost 2022-23 Final report for more details) based on the technology specific capital cost estimates provided by Aurecon (AEMO costs and technical parameter review). | [6 empty] | GenCost scenario | GenCost Global NZE by 2050 | GenCost Global NZE post 2050 | GenCost Current Policies
The capital costs are overnight costs for construction in low cost zones as detailed in the Locaitonal Cost Factors worksheet. To calculate the capital costs of these technologies elsewhere in Australia, use the locational cost factors given in that worksheet.
Extended warranties for battery storage to cover a 20-year battery life are included as part of the fixed operating costs.
The build costs do not include costs associated with expanded transmission access or additional costs incurred when development within a REZ exceeds technology limits. Details on these additional costs are found in the Build limits tab.
The financial years in table are mapped to the preceding calendar year in the GenCost 2022-23 Final report.
Build costs below are in real June 2023 dollars whereas Gencost 2022-2023 reports data in June 2022 dollars. As such, the figures have been adjusted to account for a change in base year.
The hydrogen production technologies have been covered in separate sheets at the end of this workbook.
GenCost 2022-23 Final report used the latest AEMO IASR assumptions for pumped hydro storage as a starting point (Entura (2018)) and applied a different base year and short-term cost pressure adjustments.
Build costs - Current Policies ($/kW)
DO NOT DELETE THIS COLUMN | Technology | Source | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies OCGT (small GT) | OCGT (small GT) | GenCost 2022-23 Final report | 1602.8807 | 1703.3949 | 1646.722 | 1593.257 | 1541.9306 | 1493.8121 | 1463.8717 | 1449.9708 | 1447.8322 | 1444.6243 | 1442.4857 | 1440.3471 | 1438.2085 | 1435.0006 | 1432.862 | 1430.7234 | 1428.5848 | 1426.4462 | 1424.3076 | 1420.0304 | 1415.7532 | 1411.476 | 1407.1988 | 1403.9909 | 1399.7137 | 1395.4365 | 1391.1593 | 1386.8821 | 1384.7435 | 1380.4663 | 1377.2584 | 1370.8426
GenCost Current Policies OCGT (large GT) | OCGT (large GT) | GenCost 2022-23 Final report | 1008.3499 | 1071.4386 | 1029.7359 | 990.1718 | 949.5384 | 905.6971 | 861.8558 | 860.7865 | 858.6479 | 857.5786 | 855.44 | 854.3707 | 853.3014 | 851.1628 | 850.0935 | 849.0242 | 847.9549 | 845.8163 | 844.747 | 842.6084 | 840.4698 | 837.2619 | 835.1233 | 832.9847 | 829.7768 | 827.6382 | 825.4996 | 823.361 | 821.2224 | 821.2224 | 814.8066 | 814.8066
GenCost Current Policies CCGT | CCGT | GenCost 2022-23 Final report | 1888.3838 | 1824.2258 | 1816.7407 | 1811.3942 | 1807.117 | 1786.8003 | 1768.6222 | 1752.5827 | 1749.3748 | 1746.1669 | 1742.959 | 1740.8204 | 1737.6125 | 1734.4046 | 1732.266 | 1729.0581 | 1725.8502 | 1723.7116 | 1721.573 | 1716.2265 | 1710.88 | 1706.6028 | 1701.2563 | 1695.9098 | 1691.6326 | 1686.2861 | 1682.0089 | 1676.6624 | 1673.4545 | 1668.108 | 1663.8308 | 1656.3457
GenCost Current Policies CCGT with CCS | CCGT with CCS | GenCost 2022-23 Final report | 4655.7322 | 4640.762 | 4631.1383 | 4628.9997 | 4627.9304 | 4605.4751 | 4587.297 | 4575.5347 | 4575.5347 | 4575.5347 | 4576.604 | 4576.604 | 4577.6733 | 4444.0108 | 4292.1702 | 4117.8743 | 4056.9242 | 3989.5583 | 3927.5389 | 3870.866 | 3837.7177 | 3814.1931 | 3797.0843 | 3779.9755 | 3769.2825 | 3759.6588 | 3750.0351 | 3737.2035 | 3729.7184 | 3713.6789 | 3704.0552 | 3686.9464
GenCost Current Policies Biomass | Biomass | GenCost 2022-23 Final report | 8367.2725 | 9266.5538 | 9084.7728 | 8917.962 | 8756.4977 | 8445.3314 | 8202.6003 | 8026.1658 | 8040.0667 | 8053.9676 | 8067.8685 | 8081.7694 | 8096.7396 | 8111.7098 | 8127.7493 | 8142.7195 | 8158.759 | 8174.7985 | 8190.838 | 8196.1845 | 8200.4617 | 8205.8082 | 8211.1547 | 8215.4319 | 8220.7784 | 8225.0556 | 8230.4021 | 8235.7486 | 8241.0951 | 8241.0951 | 8241.0951 | 8241.0951
GenCost Current Policies Large scale Solar PV | Large scale Solar PV | GenCost 2022-23 Final report | 1680.9396 | 1621.0588 | 1504.5051 | 1391.1593 | 1279.9521 | 1220.0713 | 1179.4379 | 1166.6063 | 1131.3194 | 1109.9334 | 1092.8246 | 1079.993 | 1068.2307 | 1052.1912 | 1038.2903 | 1012.6271 | 985.8946 | 936.7068 | 897.1427 | 845.8163 | 811.5987 | 774.1732 | 754.9258 | 743.1635 | 738.8863 | 734.6091 | 730.3319 | 726.0547 | 722.8468 | 720.7082 | 718.5696 | 715.3617
GenCost Current Policies Solar Thermal (15hrs Storage) | Solar Thermal (15hrs Storage) | GenCost 2022-23 Final report | 6977.1825 | 6926.9254 | 6778.2927 | 6631.7986 | 6469.265 | 6320.6323 | 6190.1777 | 6061.8617 | 5947.4466 | 5843.7245 | 5748.5568 | 5660.8742 | 5579.6074 | 5503.6871 | 5432.044 | 5363.6088 | 5299.4508 | 5237.4314 | 5160.4418 | 5068.482 | 4963.6906 | 4865.315 | 4773.3552 | 4686.7419 | 4604.4058 | 4526.3469 | 4452.5652 | 4383.0607 | 4331.7343 | 4279.3386 | 4229.0815 | 4178.8244
GenCost Current Policies Battery storage (1hr storage) | Battery storage (1hr storage) | GenCost 2022-23 Final report | 995.5183 | 1000.8648 | 943.1226 | 892.8655 | 847.9549 | 854.3707 | 834.054 | 813.7373 | 793.4206 | 773.1039 | 752.7872 | 732.4705 | 712.1538 | 691.8371 | 671.5204 | 652.273 | 640.5107 | 630.887 | 621.2633 | 611.6396 | 605.2238 | 598.808 | 588.115 | 580.6299 | 573.1448 | 566.729 | 560.3132 | 554.9667 | 549.6202 | 547.4816 | 547.4816 | 545.343
GenCost Current Policies Battery storage (2hrs storage) | Battery storage (2hrs storage) | GenCost 2022-23 Final report | 1439.2778 | 1447.8322 | 1362.2882 | 1287.4372 | 1223.2792 | 1189.0616 | 1156.9826 | 1122.765 | 1090.686 | 1056.4684 | 1024.3894 | 990.1718 | 958.0928 | 923.8752 | 891.7962 | 857.5786 | 840.4698 | 827.6382 | 812.668 | 799.8364 | 791.282 | 782.7276 | 767.7574 | 757.0644 | 746.3714 | 737.817 | 731.4012 | 722.8468 | 716.431 | 714.2924 | 714.2924 | 710.0152
GenCost Current Policies Battery storage (4hrs storage) | Battery storage (4hrs storage) | GenCost 2022-23 Final report | 2335.3512 | 2348.1828 | 2211.3124 | 2087.2736 | 1980.3436 | 1920.4628 | 1881.968 | 1822.0872 | 1757.9292 | 1698.0484 | 1633.8904 | 1574.0096 | 1509.8516 | 1449.9708 | 1385.8128 | 1325.932 | 1295.9916 | 1270.3284 | 1244.6652 | 1227.5564 | 1210.4476 | 1201.8932 | 1176.23 | 1154.844 | 1142.0124 | 1129.1808 | 1116.3492 | 1107.7948 | 1099.2404 | 1094.9632 | 1094.9632 | 1086.4088
GenCost Current Policies Battery storage (8hrs storage) | Battery storage (8hrs storage) | GenCost 2022-23 Final report | 4148.884 | 4174.5472 | 3926.4696 | 3704.0552 | 3515.8584 | 3447.4232 | 3370.4336 | 3250.672 | 3130.9104 | 3011.1488 | 2891.3872 | 2771.6256 | 2651.864 | 2532.1024 | 2412.3408 | 2301.1336 | 2241.2528 | 2198.4808 | 2147.1544 | 2112.9368 | 2087.2736 | 2070.1648 | 2027.3928 | 1993.1752 | 1958.9576 | 1941.8488 | 1924.74 | 1907.6312 | 1890.5224 | 1881.968 | 1881.968 | 1873.4136
GenCost Current Policies Wind | Wind | GenCost 2022-23 Final report | 2825.0906 | 2827.2292 | 2693.5667 | 2564.1814 | 2442.2812 | 2301.1336 | 2198.4808 | 2134.3228 | 2126.8377 | 2120.4219 | 2115.0754 | 2110.7982 | 2108.6596 | 2105.4517 | 2103.3131 | 2100.1052 | 2097.9666 | 2095.828 | 2094.7587 | 2091.5508 | 2088.3429 | 2084.0657 | 2079.7885 | 2074.442 | 2071.2341 | 2066.9569 | 2064.8183 | 2061.6104 | 2060.5411 | 2058.4025 | 2057.3332 | 2055.1946
GenCost Current Policies Wind - offshore (fixed) | Wind - offshore (fixed) | GenCost 2022-23 Final report | 6075.7626 | 5859.764 | 5654.4584 | 5456.6379 | 5265.2332 | 5168.9962 | 5131.5707 | 5151.8874 | 5135.8479 | 5120.8777 | 5104.8382 | 5088.7987 | 5073.8285 | 5057.789 | 5042.8188 | 5027.8486 | 5012.8784 | 4996.8389 | 4981.8687 | 4965.8292 | 4948.7204 | 4932.6809 | 4915.5721 | 4899.5326 | 4882.4238 | 4866.3843 | 4850.3448 | 4834.3053 | 4823.6123 | 4806.5035 | 4795.8105 | 4773.3552
GenCost Current Policies Wind - offshore (floating) | Wind - offshore (floating) | GenCost 2022-23 Final report | 8417.5296 | 8117.0563 | 7649.7722 | 7203.8741 | 6783.6392 | 6424.3544 | 6191.247 | 6078.9705 | 6049.0301 | 6034.0599 | 6031.9213 | 6021.2283 | 5988.08 | 5952.7931 | 5928.1992 | 5927.1299 | 5930.3378 | 5932.4764 | 5934.615 | 5933.5457 | 5932.4764 | 5931.4071 | 5929.2685 | 5927.1299 | 5924.9913 | 5923.922 | 5924.9913 | 5924.9913 | 5924.9913 | 5923.922 | 5923.922 | 5921.7834
GenCost Current Policies Hydrogen reciprocating engines | Hydrogen reciprocating engines | GenCost 2022-23 Final report | 2606.9534 | 2288.302 | 2280.8169 | 2276.5397 | 2273.3318 | 2258.3616 | 2246.5993 | 2235.9063 | 2231.6291 | 2228.4212 | 2224.144 | 2220.9361 | 2216.6589 | 2213.451 | 2209.1738 | 2205.9659 | 2202.758 | 2199.5501 | 2196.3422 | 2189.9264 | 2183.5106 | 2177.0948 | 2170.679 | 2164.2632 | 2157.8474 | 2151.4316 | 2145.0158 | 2139.6693 | 2135.3921 | 2127.907 | 2122.5605 | 2112.9368
Build costs - Global NZE post 2050 ($/kW)
| Technology | Source | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Global NZE post 2050 OCGT (small GT) | OCGT (small GT) | GenCost 2022-23 Final report | 1602.8807 | 1703.3949 | 1646.722 | 1593.257 | 1541.9306 | 1528.0297 | 1521.6139 | 1524.8218 | 1488.4656 | 1460.6638 | 1442.4857 | 1440.3471 | 1438.2085 | 1435.0006 | 1432.862 | 1430.7234 | 1428.5848 | 1426.4462 | 1424.3076 | 1420.0304 | 1415.7532 | 1411.476 | 1407.1988 | 1403.9909 | 1399.7137 | 1395.4365 | 1391.1593 | 1386.8821 | 1384.7435 | 1380.4663 | 1377.2584 | 1370.8426
GenCost Global NZE post 2050 OCGT (large GT) | OCGT (large GT) | GenCost 2022-23 Final report | 1008.3499 | 1071.4386 | 1029.7359 | 990.1718 | 949.5384 | 937.7761 | 924.9445 | 913.1822 | 885.3804 | 857.5786 | 855.44 | 854.3707 | 853.3014 | 851.1628 | 850.0935 | 849.0242 | 847.9549 | 845.8163 | 844.747 | 842.6084 | 840.4698 | 837.2619 | 835.1233 | 832.9847 | 829.7768 | 827.6382 | 825.4996 | 823.361 | 821.2224 | 821.2224 | 814.8066 | 814.8066
GenCost Global NZE post 2050 CCGT | CCGT | GenCost 2022-23 Final report | 1888.3838 | 1824.2258 | 1816.7407 | 1811.3942 | 1807.117 | 1807.117 | 1808.1863 | 1810.3249 | 1787.8696 | 1765.4143 | 1742.959 | 1740.8204 | 1737.6125 | 1734.4046 | 1732.266 | 1729.0581 | 1725.8502 | 1723.7116 | 1721.573 | 1716.2265 | 1710.88 | 1706.6028 | 1701.2563 | 1695.9098 | 1691.6326 | 1686.2861 | 1682.0089 | 1676.6624 | 1673.4545 | 1668.108 | 1663.8308 | 1656.3457
GenCost Global NZE post 2050 CCGT with CCS | CCGT with CCS | GenCost 2022-23 Final report | 4655.7322 | 4640.762 | 4631.1383 | 4628.9997 | 4627.9304 | 4614.0295 | 4600.1286 | 4587.297 | 4579.8119 | 4575.5347 | 4576.604 | 4576.604 | 4577.6733 | 4329.5957 | 4065.4786 | 3793.8764 | 3771.4211 | 3765.0053 | 3761.7974 | 3754.3123 | 3746.8272 | 3739.3421 | 3730.7877 | 3692.2929 | 3637.7586 | 3492.3338 | 3377.9187 | 3264.5729 | 3247.4641 | 3226.0781 | 3220.7316 | 3210.0386
GenCost Global NZE post 2050 Biomass | Biomass | GenCost 2022-23 Final report | 8367.2725 | 9266.5538 | 9084.7728 | 8917.962 | 8756.4977 | 8570.4395 | 8388.6585 | 8211.1547 | 8098.8782 | 8050.7597 | 8058.2448 | 8064.6606 | 8049.6904 | 8035.7895 | 8024.0272 | 8034.7202 | 8050.7597 | 8058.2448 | 8053.9676 | 8038.9974 | 8032.5816 | 8036.8588 | 8042.2053 | 8046.4825 | 8051.829 | 8056.1062 | 8060.3834 | 8065.7299 | 8070.0071 | 8070.0071 | 8070.0071 | 8070.0071
GenCost Global NZE post 2050 Large scale Solar PV | Large scale Solar PV | GenCost 2022-23 Final report | 1680.9396 | 1621.0588 | 1522.6832 | 1441.4164 | 1376.1891 | 1312.0311 | 1250.0117 | 1191.2002 | 1145.2203 | 1105.6562 | 1084.2702 | 1057.5377 | 1035.0824 | 986.9639 | 924.9445 | 850.0935 | 791.282 | 754.9258 | 734.6091 | 722.8468 | 708.9459 | 697.1836 | 683.2827 | 668.3125 | 655.4809 | 645.8572 | 637.3028 | 631.9563 | 626.6098 | 621.2633 | 618.0554 | 610.5703
GenCost Global NZE post 2050 Solar Thermal (15hrs Storage) | Solar Thermal (15hrs Storage) | GenCost 2022-23 Final report | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5731.448 | 5619.1715 | 5479.0932 | 5312.2824 | 5132.64 | 4975.4529 | 4842.8597 | 4735.9297 | 4654.6629 | 4579.8119 | 4515.6539 | 4446.1494 | 4389.4765 | 4323.1799 | 4254.7447 | 4182.0323 | 4115.7357 | 4056.9242 | 3986.3504 | 3906.1529 | 3812.0545 | 3721.164 | 3655.9367 | 3592.848 | 3529.7593 | 3467.7399
GenCost Global NZE post 2050 Battery storage (1hr storage) | Battery storage (1hr storage) | GenCost 2022-23 Final report | 995.5183 | 1000.8648 | 943.1226 | 892.8655 | 847.9549 | 794.4899 | 747.4407 | 704.6687 | 666.1739 | 633.0256 | 621.2633 | 610.5703 | 599.8773 | 589.1843 | 578.4913 | 569.9369 | 560.3132 | 550.6895 | 542.1351 | 533.5807 | 527.1649 | 519.6798 | 512.1947 | 505.7789 | 498.2938 | 491.878 | 485.4622 | 479.0464 | 473.6999 | 467.2841 | 461.9376 | 456.5911
GenCost Global NZE post 2050 Battery storage (2hrs storage) | Battery storage (2hrs storage) | GenCost 2022-23 Final report | 1439.2778 | 1447.8322 | 1330.2092 | 1229.695 | 1137.7352 | 1056.4684 | 981.6174 | 915.3208 | 857.5786 | 806.2522 | 791.282 | 776.3118 | 761.3416 | 748.51 | 735.6784 | 722.8468 | 710.0152 | 699.3222 | 688.6292 | 677.9362 | 669.3818 | 662.966 | 652.273 | 643.7186 | 635.1642 | 628.7484 | 620.194 | 613.7782 | 607.3624 | 600.9466 | 594.5308 | 588.115
GenCost Global NZE post 2050 Battery storage (4hrs storage) | Battery storage (4hrs storage) | GenCost 2022-23 Final report | 2335.3512 | 2348.1828 | 2130.0456 | 1933.2944 | 1762.2064 | 1608.2272 | 1484.1884 | 1360.1496 | 1253.2196 | 1159.1212 | 1133.458 | 1116.3492 | 1094.9632 | 1073.5772 | 1052.1912 | 1035.0824 | 1017.9736 | 1000.8648 | 983.756 | 970.9244 | 962.37 | 953.8156 | 940.984 | 928.1524 | 919.598 | 911.0436 | 902.4892 | 893.9348 | 885.3804 | 876.826 | 872.5488 | 863.9944
GenCost Global NZE post 2050 Battery storage (8hrs storage) | Battery storage (8hrs storage) | GenCost 2022-23 Final report | 4148.884 | 4174.5472 | 3746.8272 | 3370.4336 | 3036.812 | 2737.408 | 2540.6568 | 2301.1336 | 2087.2736 | 1907.6312 | 1864.8592 | 1830.6416 | 1796.424 | 1762.2064 | 1727.9888 | 1702.3256 | 1668.108 | 1642.4448 | 1616.7816 | 1599.6728 | 1582.564 | 1574.0096 | 1548.3464 | 1539.792 | 1522.6832 | 1505.5744 | 1497.02 | 1488.4656 | 1471.3568 | 1462.8024 | 1454.248 | 1445.6936
GenCost Global NZE post 2050 Wind | Wind | GenCost 2022-23 Final report | 2825.0906 | 2827.2292 | 2693.5667 | 2564.1814 | 2442.2812 | 2323.5889 | 2210.2431 | 2103.3131 | 2031.67 | 1993.1752 | 1987.8287 | 1980.3436 | 1973.9278 | 1968.5813 | 1964.3041 | 1960.0269 | 1954.6804 | 1948.2646 | 1942.9181 | 1937.5716 | 1931.1558 | 1926.8786 | 1923.6707 | 1920.4628 | 1919.3935 | 1917.2549 | 1916.1856 | 1912.9777 | 1910.8391 | 1908.7005 | 1907.6312 | 1906.5619
GenCost Global NZE post 2050 Wind - offshore (fixed) | Wind - offshore (fixed) | GenCost 2022-23 Final report | 6075.7626 | 5859.764 | 5654.4584 | 5456.6379 | 5265.2332 | 5085.5908 | 4918.78 | 4765.8701 | 4653.5936 | 4580.8812 | 4537.0399 | 4484.6442 | 4437.595 | 4400.1695 | 4383.0607 | 4353.1203 | 4331.7343 | 4295.3781 | 4264.3684 | 4223.735 | 4193.7946 | 4164.9235 | 4140.3296 | 4113.5971 | 4089.0032 | 4064.4093 | 4043.0233 | 4022.7066 | 4010.9443 | 3986.3504 | 3968.1723 | 3933.9547
GenCost Global NZE post 2050 Wind - offshore (floating) | Wind - offshore (floating) | GenCost 2022-23 Final report | 8417.5296 | 8117.0563 | 7649.7722 | 7203.8741 | 6783.6392 | 6393.3447 | 6034.0599 | 5705.7848 | 5483.3704 | 5364.6781 | 5331.5298 | 5293.035 | 5206.4217 | 5127.2935 | 5065.2741 | 5043.8881 | 5029.9872 | 5004.324 | 4982.938 | 4951.9283 | 4930.5423 | 4910.2256 | 4894.1861 | 4873.8694 | 4856.7606 | 4840.7211 | 4825.7509 | 4812.9193 | 4804.3649 | 4787.2561 | 4774.4245 | 4749.8306
GenCost Global NZE post 2050 Hydrogen reciprocating engines | Hydrogen reciprocating engines | GenCost 2022-23 Final report | 2606.9534 | 2288.302 | 2280.8169 | 2276.5397 | 2273.3318 | 2262.6388 | 2253.0151 | 2242.3221 | 2233.7677 | 2228.4212 | 2224.144 | 2220.9361 | 2216.6589 | 2213.451 | 2209.1738 | 2205.9659 | 2202.758 | 2199.5501 | 2196.3422 | 2189.9264 | 2183.5106 | 2177.0948 | 2170.679 | 2164.2632 | 2157.8474 | 2151.4316 | 2145.0158 | 2139.6693 | 2135.3921 | 2127.907 | 2122.5605 | 2112.9368
Build costs - Global NZE by 2050 ($/kW)
| Technology | Source | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Global NZE by 2050 OCGT (small GT) | OCGT (small GT) | GenCost 2022-23 Final report | 1602.8807 | 1703.3949 | 1672.3852 | 1644.5834 | 1617.8509 | 1585.7719 | 1554.7622 | 1524.8218 | 1488.4656 | 1460.6638 | 1442.4857 | 1440.3471 | 1438.2085 | 1435.0006 | 1432.862 | 1430.7234 | 1428.5848 | 1426.4462 | 1424.3076 | 1420.0304 | 1415.7532 | 1411.476 | 1407.1988 | 1403.9909 | 1399.7137 | 1395.4365 | 1391.1593 | 1386.8821 | 1384.7435 | 1380.4663 | 1377.2584 | 1370.8426
GenCost Global NZE by 2050 OCGT (large GT) | OCGT (large GT) | GenCost 2022-23 Final report | 1008.3499 | 1071.4386 | 1045.7754 | 1021.1815 | 996.5876 | 968.7858 | 940.984 | 913.1822 | 885.3804 | 857.5786 | 855.44 | 854.3707 | 853.3014 | 851.1628 | 850.0935 | 849.0242 | 847.9549 | 845.8163 | 844.747 | 842.6084 | 840.4698 | 837.2619 | 835.1233 | 832.9847 | 829.7768 | 827.6382 | 825.4996 | 823.361 | 821.2224 | 821.2224 | 814.8066 | 814.8066
GenCost Global NZE by 2050 CCGT | CCGT | GenCost 2022-23 Final report | 1888.3838 | 1824.2258 | 1822.0872 | 1823.1565 | 1824.2258 | 1819.9486 | 1814.6021 | 1810.3249 | 1787.8696 | 1765.4143 | 1742.959 | 1740.8204 | 1737.6125 | 1734.4046 | 1732.266 | 1729.0581 | 1725.8502 | 1723.7116 | 1721.573 | 1716.2265 | 1710.88 | 1706.6028 | 1701.2563 | 1695.9098 | 1691.6326 | 1686.2861 | 1682.0089 | 1676.6624 | 1673.4545 | 1668.108 | 1663.8308 | 1656.3457
GenCost Global NZE by 2050 CCGT with CCS | CCGT with CCS | GenCost 2022-23 Final report | 4655.7322 | 4628.9997 | 4622.5839 | 4623.6532 | 4624.7225 | 4612.9602 | 4600.1286 | 4587.297 | 4579.8119 | 4575.5347 | 4576.604 | 4576.604 | 4577.6733 | 4303.9325 | 4026.9838 | 3748.9658 | 3745.7579 | 3744.6886 | 3744.6886 | 3738.2728 | 3583.2243 | 3426.0372 | 3266.7115 | 3254.9492 | 3244.2562 | 3236.7711 | 3230.3553 | 3223.9395 | 3220.7316 | 3212.1772 | 3207.9 | 3197.207
GenCost Global NZE by 2050 Biomass | Biomass | GenCost 2022-23 Final report | 8367.2725 | 9266.5538 | 9084.7728 | 8917.962 | 8756.4977 | 8570.4395 | 8388.6585 | 8212.224 | 8095.6703 | 8043.2746 | 8011.1956 | 7958.7999 | 7861.4936 | 7778.0882 | 7719.2767 | 7705.3758 | 7720.346 | 7735.3162 | 7750.2864 | 7755.6329 | 7759.9101 | 7764.1873 | 7769.5338 | 7773.811 | 7778.0882 | 7783.4347 | 7787.7119 | 7793.0584 | 7797.3356 | 7797.3356 | 7797.3356 | 7797.3356
GenCost Global NZE by 2050 Large scale Solar PV | Large scale Solar PV | GenCost 2022-23 Final report | 1680.9396 | 1621.0588 | 1522.6832 | 1441.4164 | 1376.1891 | 1312.0311 | 1250.0117 | 1191.2002 | 1145.2203 | 1105.6562 | 1084.2702 | 1057.5377 | 1035.0824 | 986.9639 | 924.9445 | 850.0935 | 787.0048 | 737.817 | 698.2529 | 666.1739 | 639.4414 | 618.0554 | 599.8773 | 587.0457 | 576.3527 | 566.729 | 557.1053 | 550.6895 | 548.5509 | 546.4123 | 545.343 | 542.1351
GenCost Global NZE by 2050 Solar Thermal (15hrs Storage) | Solar Thermal (15hrs Storage) | GenCost 2022-23 Final report | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
GenCost Global NZE by 2050 Battery storage (1hr storage) | Battery storage (1hr storage) | GenCost 2022-23 Final report | 995.5183 | 1000.8648 | 943.1226 | 892.8655 | 847.9549 | 776.3118 | 715.3617 | 664.0353 | 620.194 | 562.4518 | 554.9667 | 547.4816 | 539.9965 | 532.5114 | 525.0263 | 517.5412 | 511.1254 | 503.6403 | 497.2245 | 490.8087 | 484.3929 | 479.0464 | 472.6306 | 466.2148 | 459.799 | 454.4525 | 449.106 | 443.7595 | 438.413 | 433.0665 | 427.72 | 422.3735
GenCost Global NZE by 2050 Battery storage (2hrs storage) | Battery storage (2hrs storage) | GenCost 2022-23 Final report | 1439.2778 | 1447.8322 | 1287.4372 | 1152.7054 | 1041.4982 | 945.2612 | 863.9944 | 793.4206 | 735.6784 | 658.6888 | 647.9958 | 639.4414 | 630.887 | 622.3326 | 613.7782 | 605.2238 | 596.6694 | 590.2536 | 581.6992 | 573.1448 | 566.729 | 560.3132 | 553.8974 | 545.343 | 538.9272 | 532.5114 | 526.0956 | 519.6798 | 515.4026 | 508.9868 | 502.571 | 496.1552
GenCost Global NZE by 2050 Battery storage (4hrs storage) | Battery storage (4hrs storage) | GenCost 2022-23 Final report | 2335.3512 | 2348.1828 | 2040.2244 | 1783.5924 | 1569.7324 | 1385.8128 | 1244.6652 | 1116.3492 | 1005.142 | 859.7172 | 846.8856 | 838.3312 | 825.4996 | 816.9452 | 804.1136 | 795.5592 | 782.7276 | 774.1732 | 765.6188 | 757.0644 | 748.51 | 739.9556 | 735.6784 | 727.124 | 718.5696 | 710.0152 | 705.738 | 697.1836 | 692.9064 | 684.352 | 680.0748 | 671.5204
GenCost Global NZE by 2050 Battery storage (8hrs storage) | Battery storage (8hrs storage) | GenCost 2022-23 Final report | 4148.884 | 4174.5472 | 3575.7392 | 3071.0296 | 2651.864 | 2301.1336 | 2061.6104 | 1804.9784 | 1591.1184 | 1308.8232 | 1291.7144 | 1274.6056 | 1257.4968 | 1240.388 | 1231.8336 | 1214.7248 | 1197.616 | 1189.0616 | 1171.9528 | 1163.3984 | 1154.844 | 1146.2896 | 1129.1808 | 1120.6264 | 1112.072 | 1103.5176 | 1094.9632 | 1086.4088 | 1077.8544 | 1069.3 | 1060.7456 | 1060.7456
GenCost Global NZE by 2050 Wind | Wind | GenCost 2022-23 Final report | 2825.0906 | 2827.2292 | 2695.7053 | 2569.5279 | 2448.697 | 2332.1433 | 2220.9361 | 2115.0754 | 2045.5709 | 2010.284 | 2009.2147 | 1995.3138 | 1967.512 | 1932.2251 | 1902.2847 | 1880.8987 | 1864.8592 | 1850.9583 | 1839.196 | 1827.4337 | 1817.81 | 1810.3249 | 1803.9091 | 1796.424 | 1787.8696 | 1779.3152 | 1770.7608 | 1762.2064 | 1755.7906 | 1751.5134 | 1750.4441 | 1748.3055
GenCost Global NZE by 2050 Wind - offshore (fixed) | Wind - offshore (fixed) | GenCost 2022-23 Final report | 6075.7626 | 5226.7384 | 4809.7114 | 4417.2783 | 4055.8549 | 3722.2333 | 3415.3442 | 3134.1183 | 2945.9215 | 2846.4766 | 2829.3678 | 2818.6748 | 2809.0511 | 2800.4967 | 2791.9423 | 2784.4572 | 2778.0414 | 2772.6949 | 2768.4177 | 2763.0712 | 2757.7247 | 2752.3782 | 2747.0317 | 2741.6852 | 2737.408 | 2732.0615 | 2725.6457 | 2719.2299 | 2714.9527 | 2708.5369 | 2705.329 | 2698.9132
GenCost Global NZE by 2050 Wind - offshore (floating) | Wind - offshore (floating) | GenCost 2022-23 Final report | 8417.5296 | 7240.2303 | 6530.2151 | 5868.3184 | 5274.8569 | 4736.999 | 4254.7447 | 3821.6782 | 3542.5909 | 3405.7205 | 3396.0968 | 3391.8196 | 3296.6519 | 3200.4149 | 3105.2472 | 3104.1779 | 3103.1086 | 3102.0393 | 3103.1086 | 3102.0393 | 3100.97 | 3100.97 | 3099.9007 | 3099.9007 | 3098.8314 | 2943.7829 | 2737.408 | 2510.7164 | 2438.004 | 2405.925 | 2395.232 | 2377.0539
GenCost Global NZE by 2050 Hydrogen reciprocating engines | Hydrogen reciprocating engines | GenCost 2022-23 Final report | 2606.9534 | 2288.302 | 2280.8169 | 2276.5397 | 2273.3318 | 2262.6388 | 2253.0151 | 2242.3221 | 2233.7677 | 2228.4212 | 2224.144 | 2220.9361 | 2216.6589 | 2213.451 | 2209.1738 | 2205.9659 | 2202.758 | 2199.5501 | 2196.3422 | 2189.9264 | 2183.5106 | 2177.0948 | 2170.679 | 2164.2632 | 2157.8474 | 2151.4316 | 2145.0158 | 2139.6693 | 2135.3921 | 2127.907 | 2122.5605 | 2112.9368
Build costs - Pumped hydro energy storage ($/kW) | Build costs - Pumped hydro energy storage ($/kW)
| Technology | Source | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost 2022-23 Final report Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | GenCost 2022-23 Final report | 3355.4634 | 3290.2361 | 3227.1474 | 3164.0587 | 3100.97 | 3035.7427 | 2970.5154 | 2904.2188 | 2838.9915 | 2835.7836 | 2831.5064 | 2828.2985 | 2825.0906 | 2821.8827 | 2818.6748 | 2815.4669 | 2812.259 | 2809.0511 | 2805.8432 | 2801.566 | 2797.2888 | 2793.0116 | 2788.7344 | 2784.4572 | 2780.18 | 2775.9028 | 2771.6256 | 2768.4177 | 2764.1405 | 2758.794 | 2754.5168 | 2749.1703
GenCost 2022-23 Final report Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | GenCost 2022-23 Final report | 4709.1972 | 4618.3067 | 4528.4855 | 4439.7336 | 4352.051 | 4260.0912 | 4168.1314 | 4076.1716 | 3984.2118 | 3978.8653 | 3974.5881 | 3969.2416 | 3964.9644 | 3960.6872 | 3955.3407 | 3951.0635 | 3946.7863 | 3942.5091 | 3938.2319 | 3931.8161 | 3926.4696 | 3920.0538 | 3913.638 | 3908.2915 | 3901.8757 | 3896.5292 | 3890.1134 | 3884.7669 | 3878.3511 | 3871.9353 | 3865.5195 | 3859.1037
GenCost 2022-23 Final report Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | GenCost 2022-23 Final report | 7074.4888 | 6937.6184 | 6801.8173 | 6670.2934 | 6537.7002 | 6399.7605 | 6261.8208 | 6122.8118 | 5984.8721 | 5977.387 | 5969.9019 | 5963.4861 | 5956.001 | 5949.5852 | 5942.1001 | 5935.6843 | 5929.2685 | 5922.8527 | 5915.3676 | 5906.8132 | 5898.2588 | 5888.6351 | 5880.0807 | 5870.457 | 5861.9026 | 5853.3482 | 5843.7245 | 5835.1701 | 5826.6157 | 5816.992 | 5806.299 | 5796.6753
Hydro Tasmania BOTN - Cethana1 | BOTN - Cethana1 | Hydro Tasmania | 2400.7511 | 2358.5711 | 2316.789 | 2274.7354 | 2233.7663 | 2190.4524 | 2146.9843 | 2102.736 | 2058.9689 | 2059.8854 | 2061.3597 | 2061.6667 | 2063.1491 | 2064.6369 | 2064.9504 | 2066.4463 | 2067.9477 | 2068.8289 | 2070.3396 | 2070.7295 | 2071.0554 | 2071.4479 | 2071.8419 | 2072.1712 | 2072.5678 | 2072.8994 | 2073.2987 | 2073.6325 | 2074.0345 | 2074.4371 | 2074.8402 | 2075.244
1. To reflect short-term cost pressures, BOTN (Cethana) has been adjusted using the same factor applied to Pumped Hydro (24hrs storage) in GenCost 2022-23 Final report.
Build cost by technology ($/kW)
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies OCGT (small GT) | OCGT (small GT) | GenCost Current Policies | 1602.8807 | 1703.3949 | 1646.722 | 1593.257 | 1541.9306 | 1493.8121 | 1463.8717 | 1449.9708 | 1447.8322 | 1444.6243 | 1442.4857 | 1440.3471 | 1438.2085 | 1435.0006 | 1432.862 | 1430.7234 | 1428.5848 | 1426.4462 | 1424.3076 | 1420.0304 | 1415.7532 | 1411.476 | 1407.1988 | 1403.9909 | 1399.7137 | 1395.4365 | 1391.1593 | 1386.8821 | 1384.7435 | 1380.4663 | 1377.2584 | 1370.8426
GenCost Global NZE post 2050 OCGT (small GT) | OCGT (small GT) | GenCost Global NZE post 2050 | 1602.8807 | 1703.3949 | 1646.722 | 1593.257 | 1541.9306 | 1528.0297 | 1521.6139 | 1524.8218 | 1488.4656 | 1460.6638 | 1442.4857 | 1440.3471 | 1438.2085 | 1435.0006 | 1432.862 | 1430.7234 | 1428.5848 | 1426.4462 | 1424.3076 | 1420.0304 | 1415.7532 | 1411.476 | 1407.1988 | 1403.9909 | 1399.7137 | 1395.4365 | 1391.1593 | 1386.8821 | 1384.7435 | 1380.4663 | 1377.2584 | 1370.8426
GenCost Global NZE by 2050 OCGT (small GT) | OCGT (small GT) | GenCost Global NZE by 2050 | 1602.8807 | 1703.3949 | 1672.3852 | 1644.5834 | 1617.8509 | 1585.7719 | 1554.7622 | 1524.8218 | 1488.4656 | 1460.6638 | 1442.4857 | 1440.3471 | 1438.2085 | 1435.0006 | 1432.862 | 1430.7234 | 1428.5848 | 1426.4462 | 1424.3076 | 1420.0304 | 1415.7532 | 1411.476 | 1407.1988 | 1403.9909 | 1399.7137 | 1395.4365 | 1391.1593 | 1386.8821 | 1384.7435 | 1380.4663 | 1377.2584 | 1370.8426
Green Energy Exports OCGT (small GT) | OCGT (small GT) | Green Energy Exports | 1602.8807 | 1703.3949 | 1672.3852 | 1644.5834 | 1617.8509 | 1585.7719 | 1554.7622 | 1524.8218 | 1488.4656 | 1460.6638 | 1442.4857 | 1440.3471 | 1438.2085 | 1435.0006 | 1432.862 | 1430.7234 | 1428.5848 | 1426.4462 | 1424.3076 | 1420.0304 | 1415.7532 | 1411.476 | 1407.1988 | 1403.9909 | 1399.7137 | 1395.4365 | 1391.1593 | 1386.8821 | 1384.7435 | 1380.4663 | 1377.2584 | 1370.8426
Step Change OCGT (small GT) | OCGT (small GT) | Step Change | 1602.8807 | 1703.3949 | 1646.722 | 1593.257 | 1541.9306 | 1528.0297 | 1521.6139 | 1524.8218 | 1488.4656 | 1460.6638 | 1442.4857 | 1440.3471 | 1438.2085 | 1435.0006 | 1432.862 | 1430.7234 | 1428.5848 | 1426.4462 | 1424.3076 | 1420.0304 | 1415.7532 | 1411.476 | 1407.1988 | 1403.9909 | 1399.7137 | 1395.4365 | 1391.1593 | 1386.8821 | 1384.7435 | 1380.4663 | 1377.2584 | 1370.8426
Progressive Change OCGT (small GT) | OCGT (small GT) | Progressive Change | 1602.8807 | 1703.3949 | 1646.722 | 1593.257 | 1541.9306 | 1493.8121 | 1463.8717 | 1449.9708 | 1447.8322 | 1444.6243 | 1442.4857 | 1440.3471 | 1438.2085 | 1435.0006 | 1432.862 | 1430.7234 | 1428.5848 | 1426.4462 | 1424.3076 | 1420.0304 | 1415.7532 | 1411.476 | 1407.1988 | 1403.9909 | 1399.7137 | 1395.4365 | 1391.1593 | 1386.8821 | 1384.7435 | 1380.4663 | 1377.2584 | 1370.8426
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies OCGT (large GT) | OCGT (large GT) | GenCost Current Policies | 1008.3499 | 1071.4386 | 1029.7359 | 990.1718 | 949.5384 | 905.6971 | 861.8558 | 860.7865 | 858.6479 | 857.5786 | 855.44 | 854.3707 | 853.3014 | 851.1628 | 850.0935 | 849.0242 | 847.9549 | 845.8163 | 844.747 | 842.6084 | 840.4698 | 837.2619 | 835.1233 | 832.9847 | 829.7768 | 827.6382 | 825.4996 | 823.361 | 821.2224 | 821.2224 | 814.8066 | 814.8066
GenCost Global NZE post 2050 OCGT (large GT) | OCGT (large GT) | GenCost Global NZE post 2050 | 1008.3499 | 1071.4386 | 1029.7359 | 990.1718 | 949.5384 | 937.7761 | 924.9445 | 913.1822 | 885.3804 | 857.5786 | 855.44 | 854.3707 | 853.3014 | 851.1628 | 850.0935 | 849.0242 | 847.9549 | 845.8163 | 844.747 | 842.6084 | 840.4698 | 837.2619 | 835.1233 | 832.9847 | 829.7768 | 827.6382 | 825.4996 | 823.361 | 821.2224 | 821.2224 | 814.8066 | 814.8066
GenCost Global NZE by 2050 OCGT (large GT) | OCGT (large GT) | GenCost Global NZE by 2050 | 1008.3499 | 1071.4386 | 1045.7754 | 1021.1815 | 996.5876 | 968.7858 | 940.984 | 913.1822 | 885.3804 | 857.5786 | 855.44 | 854.3707 | 853.3014 | 851.1628 | 850.0935 | 849.0242 | 847.9549 | 845.8163 | 844.747 | 842.6084 | 840.4698 | 837.2619 | 835.1233 | 832.9847 | 829.7768 | 827.6382 | 825.4996 | 823.361 | 821.2224 | 821.2224 | 814.8066 | 814.8066
Green Energy Exports OCGT (large GT) | OCGT (large GT) | Green Energy Exports | 1008.3499 | 1071.4386 | 1045.7754 | 1021.1815 | 996.5876 | 968.7858 | 940.984 | 913.1822 | 885.3804 | 857.5786 | 855.44 | 854.3707 | 853.3014 | 851.1628 | 850.0935 | 849.0242 | 847.9549 | 845.8163 | 844.747 | 842.6084 | 840.4698 | 837.2619 | 835.1233 | 832.9847 | 829.7768 | 827.6382 | 825.4996 | 823.361 | 821.2224 | 821.2224 | 814.8066 | 814.8066
Step Change OCGT (large GT) | OCGT (large GT) | Step Change | 1008.3499 | 1071.4386 | 1029.7359 | 990.1718 | 949.5384 | 937.7761 | 924.9445 | 913.1822 | 885.3804 | 857.5786 | 855.44 | 854.3707 | 853.3014 | 851.1628 | 850.0935 | 849.0242 | 847.9549 | 845.8163 | 844.747 | 842.6084 | 840.4698 | 837.2619 | 835.1233 | 832.9847 | 829.7768 | 827.6382 | 825.4996 | 823.361 | 821.2224 | 821.2224 | 814.8066 | 814.8066
Progressive Change OCGT (large GT) | OCGT (large GT) | Progressive Change | 1008.3499 | 1071.4386 | 1029.7359 | 990.1718 | 949.5384 | 905.6971 | 861.8558 | 860.7865 | 858.6479 | 857.5786 | 855.44 | 854.3707 | 853.3014 | 851.1628 | 850.0935 | 849.0242 | 847.9549 | 845.8163 | 844.747 | 842.6084 | 840.4698 | 837.2619 | 835.1233 | 832.9847 | 829.7768 | 827.6382 | 825.4996 | 823.361 | 821.2224 | 821.2224 | 814.8066 | 814.8066
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies CCGT | CCGT | GenCost Current Policies | 1888.3838 | 1824.2258 | 1816.7407 | 1811.3942 | 1807.117 | 1786.8003 | 1768.6222 | 1752.5827 | 1749.3748 | 1746.1669 | 1742.959 | 1740.8204 | 1737.6125 | 1734.4046 | 1732.266 | 1729.0581 | 1725.8502 | 1723.7116 | 1721.573 | 1716.2265 | 1710.88 | 1706.6028 | 1701.2563 | 1695.9098 | 1691.6326 | 1686.2861 | 1682.0089 | 1676.6624 | 1673.4545 | 1668.108 | 1663.8308 | 1656.3457
GenCost Global NZE post 2050 CCGT | CCGT | GenCost Global NZE post 2050 | 1888.3838 | 1824.2258 | 1816.7407 | 1811.3942 | 1807.117 | 1807.117 | 1808.1863 | 1810.3249 | 1787.8696 | 1765.4143 | 1742.959 | 1740.8204 | 1737.6125 | 1734.4046 | 1732.266 | 1729.0581 | 1725.8502 | 1723.7116 | 1721.573 | 1716.2265 | 1710.88 | 1706.6028 | 1701.2563 | 1695.9098 | 1691.6326 | 1686.2861 | 1682.0089 | 1676.6624 | 1673.4545 | 1668.108 | 1663.8308 | 1656.3457
GenCost Global NZE by 2050 CCGT | CCGT | GenCost Global NZE by 2050 | 1888.3838 | 1824.2258 | 1822.0872 | 1823.1565 | 1824.2258 | 1819.9486 | 1814.6021 | 1810.3249 | 1787.8696 | 1765.4143 | 1742.959 | 1740.8204 | 1737.6125 | 1734.4046 | 1732.266 | 1729.0581 | 1725.8502 | 1723.7116 | 1721.573 | 1716.2265 | 1710.88 | 1706.6028 | 1701.2563 | 1695.9098 | 1691.6326 | 1686.2861 | 1682.0089 | 1676.6624 | 1673.4545 | 1668.108 | 1663.8308 | 1656.3457
Green Energy Exports CCGT | CCGT | Green Energy Exports | 1888.3838 | 1824.2258 | 1822.0872 | 1823.1565 | 1824.2258 | 1819.9486 | 1814.6021 | 1810.3249 | 1787.8696 | 1765.4143 | 1742.959 | 1740.8204 | 1737.6125 | 1734.4046 | 1732.266 | 1729.0581 | 1725.8502 | 1723.7116 | 1721.573 | 1716.2265 | 1710.88 | 1706.6028 | 1701.2563 | 1695.9098 | 1691.6326 | 1686.2861 | 1682.0089 | 1676.6624 | 1673.4545 | 1668.108 | 1663.8308 | 1656.3457
Step Change CCGT | CCGT | Step Change | 1888.3838 | 1824.2258 | 1816.7407 | 1811.3942 | 1807.117 | 1807.117 | 1808.1863 | 1810.3249 | 1787.8696 | 1765.4143 | 1742.959 | 1740.8204 | 1737.6125 | 1734.4046 | 1732.266 | 1729.0581 | 1725.8502 | 1723.7116 | 1721.573 | 1716.2265 | 1710.88 | 1706.6028 | 1701.2563 | 1695.9098 | 1691.6326 | 1686.2861 | 1682.0089 | 1676.6624 | 1673.4545 | 1668.108 | 1663.8308 | 1656.3457
Progressive Change CCGT | CCGT | Progressive Change | 1888.3838 | 1824.2258 | 1816.7407 | 1811.3942 | 1807.117 | 1786.8003 | 1768.6222 | 1752.5827 | 1749.3748 | 1746.1669 | 1742.959 | 1740.8204 | 1737.6125 | 1734.4046 | 1732.266 | 1729.0581 | 1725.8502 | 1723.7116 | 1721.573 | 1716.2265 | 1710.88 | 1706.6028 | 1701.2563 | 1695.9098 | 1691.6326 | 1686.2861 | 1682.0089 | 1676.6624 | 1673.4545 | 1668.108 | 1663.8308 | 1656.3457
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies CCGT with CCS | CCGT with CCS | GenCost Current Policies | 4655.7322 | 4640.762 | 4631.1383 | 4628.9997 | 4627.9304 | 4605.4751 | 4587.297 | 4575.5347 | 4575.5347 | 4575.5347 | 4576.604 | 4576.604 | 4577.6733 | 4444.0108 | 4292.1702 | 4117.8743 | 4056.9242 | 3989.5583 | 3927.5389 | 3870.866 | 3837.7177 | 3814.1931 | 3797.0843 | 3779.9755 | 3769.2825 | 3759.6588 | 3750.0351 | 3737.2035 | 3729.7184 | 3713.6789 | 3704.0552 | 3686.9464
GenCost Global NZE post 2050 CCGT with CCS | CCGT with CCS | GenCost Global NZE post 2050 | 4655.7322 | 4640.762 | 4631.1383 | 4628.9997 | 4627.9304 | 4614.0295 | 4600.1286 | 4587.297 | 4579.8119 | 4575.5347 | 4576.604 | 4576.604 | 4577.6733 | 4329.5957 | 4065.4786 | 3793.8764 | 3771.4211 | 3765.0053 | 3761.7974 | 3754.3123 | 3746.8272 | 3739.3421 | 3730.7877 | 3692.2929 | 3637.7586 | 3492.3338 | 3377.9187 | 3264.5729 | 3247.4641 | 3226.0781 | 3220.7316 | 3210.0386
GenCost Global NZE by 2050 CCGT with CCS | CCGT with CCS | GenCost Global NZE by 2050 | 4655.7322 | 4628.9997 | 4622.5839 | 4623.6532 | 4624.7225 | 4612.9602 | 4600.1286 | 4587.297 | 4579.8119 | 4575.5347 | 4576.604 | 4576.604 | 4577.6733 | 4303.9325 | 4026.9838 | 3748.9658 | 3745.7579 | 3744.6886 | 3744.6886 | 3738.2728 | 3583.2243 | 3426.0372 | 3266.7115 | 3254.9492 | 3244.2562 | 3236.7711 | 3230.3553 | 3223.9395 | 3220.7316 | 3212.1772 | 3207.9 | 3197.207
Green Energy Exports CCGT with CCS | CCGT with CCS | Green Energy Exports | 4655.7322 | 4628.9997 | 4622.5839 | 4623.6532 | 4624.7225 | 4612.9602 | 4600.1286 | 4587.297 | 4579.8119 | 4575.5347 | 4576.604 | 4576.604 | 4577.6733 | 4303.9325 | 4026.9838 | 3748.9658 | 3745.7579 | 3744.6886 | 3744.6886 | 3738.2728 | 3583.2243 | 3426.0372 | 3266.7115 | 3254.9492 | 3244.2562 | 3236.7711 | 3230.3553 | 3223.9395 | 3220.7316 | 3212.1772 | 3207.9 | 3197.207
Step Change CCGT with CCS | CCGT with CCS | Step Change | 4655.7322 | 4640.762 | 4631.1383 | 4628.9997 | 4627.9304 | 4614.0295 | 4600.1286 | 4587.297 | 4579.8119 | 4575.5347 | 4576.604 | 4576.604 | 4577.6733 | 4329.5957 | 4065.4786 | 3793.8764 | 3771.4211 | 3765.0053 | 3761.7974 | 3754.3123 | 3746.8272 | 3739.3421 | 3730.7877 | 3692.2929 | 3637.7586 | 3492.3338 | 3377.9187 | 3264.5729 | 3247.4641 | 3226.0781 | 3220.7316 | 3210.0386
Progressive Change CCGT with CCS | CCGT with CCS | Progressive Change | 4655.7322 | 4640.762 | 4631.1383 | 4628.9997 | 4627.9304 | 4605.4751 | 4587.297 | 4575.5347 | 4575.5347 | 4575.5347 | 4576.604 | 4576.604 | 4577.6733 | 4444.0108 | 4292.1702 | 4117.8743 | 4056.9242 | 3989.5583 | 3927.5389 | 3870.866 | 3837.7177 | 3814.1931 | 3797.0843 | 3779.9755 | 3769.2825 | 3759.6588 | 3750.0351 | 3737.2035 | 3729.7184 | 3713.6789 | 3704.0552 | 3686.9464
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Hydrogen reciprocating engines | Hydrogen reciprocating engines | GenCost Current Policies | 2606.9534 | 2288.302 | 2280.8169 | 2276.5397 | 2273.3318 | 2258.3616 | 2246.5993 | 2235.9063 | 2231.6291 | 2228.4212 | 2224.144 | 2220.9361 | 2216.6589 | 2213.451 | 2209.1738 | 2205.9659 | 2202.758 | 2199.5501 | 2196.3422 | 2189.9264 | 2183.5106 | 2177.0948 | 2170.679 | 2164.2632 | 2157.8474 | 2151.4316 | 2145.0158 | 2139.6693 | 2135.3921 | 2127.907 | 2122.5605 | 2112.9368
GenCost Global NZE post 2050 Hydrogen reciprocating engines | Hydrogen reciprocating engines | GenCost Global NZE post 2050 | 2606.9534 | 2288.302 | 2280.8169 | 2276.5397 | 2273.3318 | 2262.6388 | 2253.0151 | 2242.3221 | 2233.7677 | 2228.4212 | 2224.144 | 2220.9361 | 2216.6589 | 2213.451 | 2209.1738 | 2205.9659 | 2202.758 | 2199.5501 | 2196.3422 | 2189.9264 | 2183.5106 | 2177.0948 | 2170.679 | 2164.2632 | 2157.8474 | 2151.4316 | 2145.0158 | 2139.6693 | 2135.3921 | 2127.907 | 2122.5605 | 2112.9368
GenCost Global NZE by 2050 Hydrogen reciprocating engines | Hydrogen reciprocating engines | GenCost Global NZE by 2050 | 2606.9534 | 2288.302 | 2280.8169 | 2276.5397 | 2273.3318 | 2262.6388 | 2253.0151 | 2242.3221 | 2233.7677 | 2228.4212 | 2224.144 | 2220.9361 | 2216.6589 | 2213.451 | 2209.1738 | 2205.9659 | 2202.758 | 2199.5501 | 2196.3422 | 2189.9264 | 2183.5106 | 2177.0948 | 2170.679 | 2164.2632 | 2157.8474 | 2151.4316 | 2145.0158 | 2139.6693 | 2135.3921 | 2127.907 | 2122.5605 | 2112.9368
Green Energy Exports Hydrogen reciprocating engines | Hydrogen reciprocating engines | Green Energy Exports | 2606.9534 | 2288.302 | 2280.8169 | 2276.5397 | 2273.3318 | 2262.6388 | 2253.0151 | 2242.3221 | 2233.7677 | 2228.4212 | 2224.144 | 2220.9361 | 2216.6589 | 2213.451 | 2209.1738 | 2205.9659 | 2202.758 | 2199.5501 | 2196.3422 | 2189.9264 | 2183.5106 | 2177.0948 | 2170.679 | 2164.2632 | 2157.8474 | 2151.4316 | 2145.0158 | 2139.6693 | 2135.3921 | 2127.907 | 2122.5605 | 2112.9368
Step Change Hydrogen reciprocating engines | Hydrogen reciprocating engines | Step Change | 2606.9534 | 2288.302 | 2280.8169 | 2276.5397 | 2273.3318 | 2262.6388 | 2253.0151 | 2242.3221 | 2233.7677 | 2228.4212 | 2224.144 | 2220.9361 | 2216.6589 | 2213.451 | 2209.1738 | 2205.9659 | 2202.758 | 2199.5501 | 2196.3422 | 2189.9264 | 2183.5106 | 2177.0948 | 2170.679 | 2164.2632 | 2157.8474 | 2151.4316 | 2145.0158 | 2139.6693 | 2135.3921 | 2127.907 | 2122.5605 | 2112.9368
Progressive Change Hydrogen reciprocating engines | Hydrogen reciprocating engines | Progressive Change | 2606.9534 | 2288.302 | 2280.8169 | 2276.5397 | 2273.3318 | 2258.3616 | 2246.5993 | 2235.9063 | 2231.6291 | 2228.4212 | 2224.144 | 2220.9361 | 2216.6589 | 2213.451 | 2209.1738 | 2205.9659 | 2202.758 | 2199.5501 | 2196.3422 | 2189.9264 | 2183.5106 | 2177.0948 | 2170.679 | 2164.2632 | 2157.8474 | 2151.4316 | 2145.0158 | 2139.6693 | 2135.3921 | 2127.907 | 2122.5605 | 2112.9368
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Biomass | Biomass | GenCost Current Policies | 8367.2725 | 9266.5538 | 9084.7728 | 8917.962 | 8756.4977 | 8445.3314 | 8202.6003 | 8026.1658 | 8040.0667 | 8053.9676 | 8067.8685 | 8081.7694 | 8096.7396 | 8111.7098 | 8127.7493 | 8142.7195 | 8158.759 | 8174.7985 | 8190.838 | 8196.1845 | 8200.4617 | 8205.8082 | 8211.1547 | 8215.4319 | 8220.7784 | 8225.0556 | 8230.4021 | 8235.7486 | 8241.0951 | 8241.0951 | 8241.0951 | 8241.0951
GenCost Global NZE post 2050 Biomass | Biomass | GenCost Global NZE post 2050 | 8367.2725 | 9266.5538 | 9084.7728 | 8917.962 | 8756.4977 | 8570.4395 | 8388.6585 | 8211.1547 | 8098.8782 | 8050.7597 | 8058.2448 | 8064.6606 | 8049.6904 | 8035.7895 | 8024.0272 | 8034.7202 | 8050.7597 | 8058.2448 | 8053.9676 | 8038.9974 | 8032.5816 | 8036.8588 | 8042.2053 | 8046.4825 | 8051.829 | 8056.1062 | 8060.3834 | 8065.7299 | 8070.0071 | 8070.0071 | 8070.0071 | 8070.0071
GenCost Global NZE by 2050 Biomass | Biomass | GenCost Global NZE by 2050 | 8367.2725 | 9266.5538 | 9084.7728 | 8917.962 | 8756.4977 | 8570.4395 | 8388.6585 | 8212.224 | 8095.6703 | 8043.2746 | 8011.1956 | 7958.7999 | 7861.4936 | 7778.0882 | 7719.2767 | 7705.3758 | 7720.346 | 7735.3162 | 7750.2864 | 7755.6329 | 7759.9101 | 7764.1873 | 7769.5338 | 7773.811 | 7778.0882 | 7783.4347 | 7787.7119 | 7793.0584 | 7797.3356 | 7797.3356 | 7797.3356 | 7797.3356
Green Energy Exports Biomass | Biomass | Green Energy Exports | 8367.2725 | 9266.5538 | 9084.7728 | 8917.962 | 8756.4977 | 8570.4395 | 8388.6585 | 8212.224 | 8095.6703 | 8043.2746 | 8011.1956 | 7958.7999 | 7861.4936 | 7778.0882 | 7719.2767 | 7705.3758 | 7720.346 | 7735.3162 | 7750.2864 | 7755.6329 | 7759.9101 | 7764.1873 | 7769.5338 | 7773.811 | 7778.0882 | 7783.4347 | 7787.7119 | 7793.0584 | 7797.3356 | 7797.3356 | 7797.3356 | 7797.3356
Step Change Biomass | Biomass | Step Change | 8367.2725 | 9266.5538 | 9084.7728 | 8917.962 | 8756.4977 | 8570.4395 | 8388.6585 | 8211.1547 | 8098.8782 | 8050.7597 | 8058.2448 | 8064.6606 | 8049.6904 | 8035.7895 | 8024.0272 | 8034.7202 | 8050.7597 | 8058.2448 | 8053.9676 | 8038.9974 | 8032.5816 | 8036.8588 | 8042.2053 | 8046.4825 | 8051.829 | 8056.1062 | 8060.3834 | 8065.7299 | 8070.0071 | 8070.0071 | 8070.0071 | 8070.0071
Progressive Change Biomass | Biomass | Progressive Change | 8367.2725 | 9266.5538 | 9084.7728 | 8917.962 | 8756.4977 | 8445.3314 | 8202.6003 | 8026.1658 | 8040.0667 | 8053.9676 | 8067.8685 | 8081.7694 | 8096.7396 | 8111.7098 | 8127.7493 | 8142.7195 | 8158.759 | 8174.7985 | 8190.838 | 8196.1845 | 8200.4617 | 8205.8082 | 8211.1547 | 8215.4319 | 8220.7784 | 8225.0556 | 8230.4021 | 8235.7486 | 8241.0951 | 8241.0951 | 8241.0951 | 8241.0951
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Large scale Solar PV | Large scale Solar PV | GenCost Current Policies | 1680.9396 | 1621.0588 | 1504.5051 | 1391.1593 | 1279.9521 | 1220.0713 | 1179.4379 | 1166.6063 | 1131.3194 | 1109.9334 | 1092.8246 | 1079.993 | 1068.2307 | 1052.1912 | 1038.2903 | 1012.6271 | 985.8946 | 936.7068 | 897.1427 | 845.8163 | 811.5987 | 774.1732 | 754.9258 | 743.1635 | 738.8863 | 734.6091 | 730.3319 | 726.0547 | 722.8468 | 720.7082 | 718.5696 | 715.3617
GenCost Global NZE post 2050 Large scale Solar PV | Large scale Solar PV | GenCost Global NZE post 2050 | 1680.9396 | 1621.0588 | 1522.6832 | 1441.4164 | 1376.1891 | 1312.0311 | 1250.0117 | 1191.2002 | 1145.2203 | 1105.6562 | 1084.2702 | 1057.5377 | 1035.0824 | 986.9639 | 924.9445 | 850.0935 | 791.282 | 754.9258 | 734.6091 | 722.8468 | 708.9459 | 697.1836 | 683.2827 | 668.3125 | 655.4809 | 645.8572 | 637.3028 | 631.9563 | 626.6098 | 621.2633 | 618.0554 | 610.5703
GenCost Global NZE by 2050 Large scale Solar PV | Large scale Solar PV | GenCost Global NZE by 2050 | 1680.9396 | 1621.0588 | 1522.6832 | 1441.4164 | 1376.1891 | 1312.0311 | 1250.0117 | 1191.2002 | 1145.2203 | 1105.6562 | 1084.2702 | 1057.5377 | 1035.0824 | 986.9639 | 924.9445 | 850.0935 | 787.0048 | 737.817 | 698.2529 | 666.1739 | 639.4414 | 618.0554 | 599.8773 | 587.0457 | 576.3527 | 566.729 | 557.1053 | 550.6895 | 548.5509 | 546.4123 | 545.343 | 542.1351
Green Energy Exports Large scale Solar PV | Large scale Solar PV | Green Energy Exports | 1680.9396 | 1621.0588 | 1522.6832 | 1441.4164 | 1376.1891 | 1312.0311 | 1250.0117 | 1191.2002 | 1145.2203 | 1105.6562 | 1084.2702 | 1057.5377 | 1035.0824 | 986.9639 | 924.9445 | 850.0935 | 787.0048 | 737.817 | 698.2529 | 666.1739 | 639.4414 | 618.0554 | 599.8773 | 587.0457 | 576.3527 | 566.729 | 557.1053 | 550.6895 | 548.5509 | 546.4123 | 545.343 | 542.1351
Step Change Large scale Solar PV | Large scale Solar PV | Step Change | 1680.9396 | 1621.0588 | 1522.6832 | 1441.4164 | 1376.1891 | 1312.0311 | 1250.0117 | 1191.2002 | 1145.2203 | 1105.6562 | 1084.2702 | 1057.5377 | 1035.0824 | 986.9639 | 924.9445 | 850.0935 | 791.282 | 754.9258 | 734.6091 | 722.8468 | 708.9459 | 697.1836 | 683.2827 | 668.3125 | 655.4809 | 645.8572 | 637.3028 | 631.9563 | 626.6098 | 621.2633 | 618.0554 | 610.5703
Progressive Change Large scale Solar PV | Large scale Solar PV | Progressive Change | 1680.9396 | 1621.0588 | 1504.5051 | 1391.1593 | 1279.9521 | 1220.0713 | 1179.4379 | 1166.6063 | 1131.3194 | 1109.9334 | 1092.8246 | 1079.993 | 1068.2307 | 1052.1912 | 1038.2903 | 1012.6271 | 985.8946 | 936.7068 | 897.1427 | 845.8163 | 811.5987 | 774.1732 | 754.9258 | 743.1635 | 738.8863 | 734.6091 | 730.3319 | 726.0547 | 722.8468 | 720.7082 | 718.5696 | 715.3617
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Solar Thermal (15hrs Storage) | Solar Thermal (15hrs Storage) | GenCost Current Policies | 6977.1825 | 6926.9254 | 6778.2927 | 6631.7986 | 6469.265 | 6320.6323 | 6190.1777 | 6061.8617 | 5947.4466 | 5843.7245 | 5748.5568 | 5660.8742 | 5579.6074 | 5503.6871 | 5432.044 | 5363.6088 | 5299.4508 | 5237.4314 | 5160.4418 | 5068.482 | 4963.6906 | 4865.315 | 4773.3552 | 4686.7419 | 4604.4058 | 4526.3469 | 4452.5652 | 4383.0607 | 4331.7343 | 4279.3386 | 4229.0815 | 4178.8244
GenCost Global NZE post 2050 Solar Thermal (15hrs Storage) | Solar Thermal (15hrs Storage) | GenCost Global NZE post 2050 | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5731.448 | 5619.1715 | 5479.0932 | 5312.2824 | 5132.64 | 4975.4529 | 4842.8597 | 4735.9297 | 4654.6629 | 4579.8119 | 4515.6539 | 4446.1494 | 4389.4765 | 4323.1799 | 4254.7447 | 4182.0323 | 4115.7357 | 4056.9242 | 3986.3504 | 3906.1529 | 3812.0545 | 3721.164 | 3655.9367 | 3592.848 | 3529.7593 | 3467.7399
GenCost Global NZE by 2050 Solar Thermal (15hrs Storage) | Solar Thermal (15hrs Storage) | GenCost Global NZE by 2050 | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Green Energy Exports Solar Thermal (15hrs Storage) | Solar Thermal (15hrs Storage) | Green Energy Exports | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5682.2602 | 5470.5388 | 5257.7481 | 5074.8978 | 4940.166 | 4812.9193 | 4705.9893 | 4595.8514 | 4502.8223 | 4408.7239 | 4321.0413 | 4210.9034 | 4100.7655 | 3977.796 | 3873.0046 | 3763.936 | 3677.3227 | 3594.9866 | 3528.69 | 3465.6013 | 3406.7898 | 3349.0476 | 3300.9291 | 3253.8799 | 3206.8307 | 3160.8508
Step Change Solar Thermal (15hrs Storage) | Solar Thermal (15hrs Storage) | Step Change | 6977.1825 | 6809.3024 | 6582.6108 | 6309.9393 | 6059.7231 | 5867.2491 | 5731.448 | 5619.1715 | 5479.0932 | 5312.2824 | 5132.64 | 4975.4529 | 4842.8597 | 4735.9297 | 4654.6629 | 4579.8119 | 4515.6539 | 4446.1494 | 4389.4765 | 4323.1799 | 4254.7447 | 4182.0323 | 4115.7357 | 4056.9242 | 3986.3504 | 3906.1529 | 3812.0545 | 3721.164 | 3655.9367 | 3592.848 | 3529.7593 | 3467.7399
Progressive Change Solar Thermal (15hrs Storage) | Solar Thermal (15hrs Storage) | Progressive Change | 6977.1825 | 6926.9254 | 6778.2927 | 6631.7986 | 6469.265 | 6320.6323 | 6190.1777 | 6061.8617 | 5947.4466 | 5843.7245 | 5748.5568 | 5660.8742 | 5579.6074 | 5503.6871 | 5432.044 | 5363.6088 | 5299.4508 | 5237.4314 | 5160.4418 | 5068.482 | 4963.6906 | 4865.315 | 4773.3552 | 4686.7419 | 4604.4058 | 4526.3469 | 4452.5652 | 4383.0607 | 4331.7343 | 4279.3386 | 4229.0815 | 4178.8244
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Battery storage (1hr storage) | Battery storage (1hr storage) | GenCost Current Policies | 995.5183 | 1000.8648 | 943.1226 | 892.8655 | 847.9549 | 854.3707 | 834.054 | 813.7373 | 793.4206 | 773.1039 | 752.7872 | 732.4705 | 712.1538 | 691.8371 | 671.5204 | 652.273 | 640.5107 | 630.887 | 621.2633 | 611.6396 | 605.2238 | 598.808 | 588.115 | 580.6299 | 573.1448 | 566.729 | 560.3132 | 554.9667 | 549.6202 | 547.4816 | 547.4816 | 545.343
GenCost Global NZE post 2050 Battery storage (1hr storage) | Battery storage (1hr storage) | GenCost Global NZE post 2050 | 995.5183 | 1000.8648 | 943.1226 | 892.8655 | 847.9549 | 794.4899 | 747.4407 | 704.6687 | 666.1739 | 633.0256 | 621.2633 | 610.5703 | 599.8773 | 589.1843 | 578.4913 | 569.9369 | 560.3132 | 550.6895 | 542.1351 | 533.5807 | 527.1649 | 519.6798 | 512.1947 | 505.7789 | 498.2938 | 491.878 | 485.4622 | 479.0464 | 473.6999 | 467.2841 | 461.9376 | 456.5911
GenCost Global NZE by 2050 Battery storage (1hr storage) | Battery storage (1hr storage) | GenCost Global NZE by 2050 | 995.5183 | 1000.8648 | 943.1226 | 892.8655 | 847.9549 | 776.3118 | 715.3617 | 664.0353 | 620.194 | 562.4518 | 554.9667 | 547.4816 | 539.9965 | 532.5114 | 525.0263 | 517.5412 | 511.1254 | 503.6403 | 497.2245 | 490.8087 | 484.3929 | 479.0464 | 472.6306 | 466.2148 | 459.799 | 454.4525 | 449.106 | 443.7595 | 438.413 | 433.0665 | 427.72 | 422.3735
Green Energy Exports Battery storage (1hr storage) | Battery storage (1hr storage) | Green Energy Exports | 995.5183 | 1000.8648 | 943.1226 | 892.8655 | 847.9549 | 776.3118 | 715.3617 | 664.0353 | 620.194 | 562.4518 | 554.9667 | 547.4816 | 539.9965 | 532.5114 | 525.0263 | 517.5412 | 511.1254 | 503.6403 | 497.2245 | 490.8087 | 484.3929 | 479.0464 | 472.6306 | 466.2148 | 459.799 | 454.4525 | 449.106 | 443.7595 | 438.413 | 433.0665 | 427.72 | 422.3735
Step Change Battery storage (1hr storage) | Battery storage (1hr storage) | Step Change | 995.5183 | 1000.8648 | 943.1226 | 892.8655 | 847.9549 | 794.4899 | 747.4407 | 704.6687 | 666.1739 | 633.0256 | 621.2633 | 610.5703 | 599.8773 | 589.1843 | 578.4913 | 569.9369 | 560.3132 | 550.6895 | 542.1351 | 533.5807 | 527.1649 | 519.6798 | 512.1947 | 505.7789 | 498.2938 | 491.878 | 485.4622 | 479.0464 | 473.6999 | 467.2841 | 461.9376 | 456.5911
Progressive Change Battery storage (1hr storage) | Battery storage (1hr storage) | Progressive Change | 995.5183 | 1000.8648 | 943.1226 | 892.8655 | 847.9549 | 854.3707 | 834.054 | 813.7373 | 793.4206 | 773.1039 | 752.7872 | 732.4705 | 712.1538 | 691.8371 | 671.5204 | 652.273 | 640.5107 | 630.887 | 621.2633 | 611.6396 | 605.2238 | 598.808 | 588.115 | 580.6299 | 573.1448 | 566.729 | 560.3132 | 554.9667 | 549.6202 | 547.4816 | 547.4816 | 545.343
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Battery storage (2hrs storage) | Battery storage (2hrs storage) | GenCost Current Policies | 1439.2778 | 1447.8322 | 1362.2882 | 1287.4372 | 1223.2792 | 1189.0616 | 1156.9826 | 1122.765 | 1090.686 | 1056.4684 | 1024.3894 | 990.1718 | 958.0928 | 923.8752 | 891.7962 | 857.5786 | 840.4698 | 827.6382 | 812.668 | 799.8364 | 791.282 | 782.7276 | 767.7574 | 757.0644 | 746.3714 | 737.817 | 731.4012 | 722.8468 | 716.431 | 714.2924 | 714.2924 | 710.0152
GenCost Global NZE post 2050 Battery storage (2hrs storage) | Battery storage (2hrs storage) | GenCost Global NZE post 2050 | 1439.2778 | 1447.8322 | 1330.2092 | 1229.695 | 1137.7352 | 1056.4684 | 981.6174 | 915.3208 | 857.5786 | 806.2522 | 791.282 | 776.3118 | 761.3416 | 748.51 | 735.6784 | 722.8468 | 710.0152 | 699.3222 | 688.6292 | 677.9362 | 669.3818 | 662.966 | 652.273 | 643.7186 | 635.1642 | 628.7484 | 620.194 | 613.7782 | 607.3624 | 600.9466 | 594.5308 | 588.115
GenCost Global NZE by 2050 Battery storage (2hrs storage) | Battery storage (2hrs storage) | GenCost Global NZE by 2050 | 1439.2778 | 1447.8322 | 1287.4372 | 1152.7054 | 1041.4982 | 945.2612 | 863.9944 | 793.4206 | 735.6784 | 658.6888 | 647.9958 | 639.4414 | 630.887 | 622.3326 | 613.7782 | 605.2238 | 596.6694 | 590.2536 | 581.6992 | 573.1448 | 566.729 | 560.3132 | 553.8974 | 545.343 | 538.9272 | 532.5114 | 526.0956 | 519.6798 | 515.4026 | 508.9868 | 502.571 | 496.1552
Green Energy Exports Battery storage (2hrs storage) | Battery storage (2hrs storage) | Green Energy Exports | 1439.2778 | 1447.8322 | 1287.4372 | 1152.7054 | 1041.4982 | 945.2612 | 863.9944 | 793.4206 | 735.6784 | 658.6888 | 647.9958 | 639.4414 | 630.887 | 622.3326 | 613.7782 | 605.2238 | 596.6694 | 590.2536 | 581.6992 | 573.1448 | 566.729 | 560.3132 | 553.8974 | 545.343 | 538.9272 | 532.5114 | 526.0956 | 519.6798 | 515.4026 | 508.9868 | 502.571 | 496.1552
Step Change Battery storage (2hrs storage) | Battery storage (2hrs storage) | Step Change | 1439.2778 | 1447.8322 | 1330.2092 | 1229.695 | 1137.7352 | 1056.4684 | 981.6174 | 915.3208 | 857.5786 | 806.2522 | 791.282 | 776.3118 | 761.3416 | 748.51 | 735.6784 | 722.8468 | 710.0152 | 699.3222 | 688.6292 | 677.9362 | 669.3818 | 662.966 | 652.273 | 643.7186 | 635.1642 | 628.7484 | 620.194 | 613.7782 | 607.3624 | 600.9466 | 594.5308 | 588.115
Progressive Change Battery storage (2hrs storage) | Battery storage (2hrs storage) | Progressive Change | 1439.2778 | 1447.8322 | 1362.2882 | 1287.4372 | 1223.2792 | 1189.0616 | 1156.9826 | 1122.765 | 1090.686 | 1056.4684 | 1024.3894 | 990.1718 | 958.0928 | 923.8752 | 891.7962 | 857.5786 | 840.4698 | 827.6382 | 812.668 | 799.8364 | 791.282 | 782.7276 | 767.7574 | 757.0644 | 746.3714 | 737.817 | 731.4012 | 722.8468 | 716.431 | 714.2924 | 714.2924 | 710.0152
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Battery storage (4hrs storage) | Battery storage (4hrs storage) | GenCost Current Policies | 2335.3512 | 2348.1828 | 2211.3124 | 2087.2736 | 1980.3436 | 1920.4628 | 1881.968 | 1822.0872 | 1757.9292 | 1698.0484 | 1633.8904 | 1574.0096 | 1509.8516 | 1449.9708 | 1385.8128 | 1325.932 | 1295.9916 | 1270.3284 | 1244.6652 | 1227.5564 | 1210.4476 | 1201.8932 | 1176.23 | 1154.844 | 1142.0124 | 1129.1808 | 1116.3492 | 1107.7948 | 1099.2404 | 1094.9632 | 1094.9632 | 1086.4088
GenCost Global NZE post 2050 Battery storage (4hrs storage) | Battery storage (4hrs storage) | GenCost Global NZE post 2050 | 2335.3512 | 2348.1828 | 2130.0456 | 1933.2944 | 1762.2064 | 1608.2272 | 1484.1884 | 1360.1496 | 1253.2196 | 1159.1212 | 1133.458 | 1116.3492 | 1094.9632 | 1073.5772 | 1052.1912 | 1035.0824 | 1017.9736 | 1000.8648 | 983.756 | 970.9244 | 962.37 | 953.8156 | 940.984 | 928.1524 | 919.598 | 911.0436 | 902.4892 | 893.9348 | 885.3804 | 876.826 | 872.5488 | 863.9944
GenCost Global NZE by 2050 Battery storage (4hrs storage) | Battery storage (4hrs storage) | GenCost Global NZE by 2050 | 2335.3512 | 2348.1828 | 2040.2244 | 1783.5924 | 1569.7324 | 1385.8128 | 1244.6652 | 1116.3492 | 1005.142 | 859.7172 | 846.8856 | 838.3312 | 825.4996 | 816.9452 | 804.1136 | 795.5592 | 782.7276 | 774.1732 | 765.6188 | 757.0644 | 748.51 | 739.9556 | 735.6784 | 727.124 | 718.5696 | 710.0152 | 705.738 | 697.1836 | 692.9064 | 684.352 | 680.0748 | 671.5204
Green Energy Exports Battery storage (4hrs storage) | Battery storage (4hrs storage) | Green Energy Exports | 2335.3512 | 2348.1828 | 2040.2244 | 1783.5924 | 1569.7324 | 1385.8128 | 1244.6652 | 1116.3492 | 1005.142 | 859.7172 | 846.8856 | 838.3312 | 825.4996 | 816.9452 | 804.1136 | 795.5592 | 782.7276 | 774.1732 | 765.6188 | 757.0644 | 748.51 | 739.9556 | 735.6784 | 727.124 | 718.5696 | 710.0152 | 705.738 | 697.1836 | 692.9064 | 684.352 | 680.0748 | 671.5204
Step Change Battery storage (4hrs storage) | Battery storage (4hrs storage) | Step Change | 2335.3512 | 2348.1828 | 2130.0456 | 1933.2944 | 1762.2064 | 1608.2272 | 1484.1884 | 1360.1496 | 1253.2196 | 1159.1212 | 1133.458 | 1116.3492 | 1094.9632 | 1073.5772 | 1052.1912 | 1035.0824 | 1017.9736 | 1000.8648 | 983.756 | 970.9244 | 962.37 | 953.8156 | 940.984 | 928.1524 | 919.598 | 911.0436 | 902.4892 | 893.9348 | 885.3804 | 876.826 | 872.5488 | 863.9944
Progressive Change Battery storage (4hrs storage) | Battery storage (4hrs storage) | Progressive Change | 2335.3512 | 2348.1828 | 2211.3124 | 2087.2736 | 1980.3436 | 1920.4628 | 1881.968 | 1822.0872 | 1757.9292 | 1698.0484 | 1633.8904 | 1574.0096 | 1509.8516 | 1449.9708 | 1385.8128 | 1325.932 | 1295.9916 | 1270.3284 | 1244.6652 | 1227.5564 | 1210.4476 | 1201.8932 | 1176.23 | 1154.844 | 1142.0124 | 1129.1808 | 1116.3492 | 1107.7948 | 1099.2404 | 1094.9632 | 1094.9632 | 1086.4088
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Battery storage (8hrs storage) | Battery storage (8hrs storage) | GenCost Current Policies | 4148.884 | 4174.5472 | 3926.4696 | 3704.0552 | 3515.8584 | 3447.4232 | 3370.4336 | 3250.672 | 3130.9104 | 3011.1488 | 2891.3872 | 2771.6256 | 2651.864 | 2532.1024 | 2412.3408 | 2301.1336 | 2241.2528 | 2198.4808 | 2147.1544 | 2112.9368 | 2087.2736 | 2070.1648 | 2027.3928 | 1993.1752 | 1958.9576 | 1941.8488 | 1924.74 | 1907.6312 | 1890.5224 | 1881.968 | 1881.968 | 1873.4136
GenCost Global NZE post 2050 Battery storage (8hrs storage) | Battery storage (8hrs storage) | GenCost Global NZE post 2050 | 4148.884 | 4174.5472 | 3746.8272 | 3370.4336 | 3036.812 | 2737.408 | 2540.6568 | 2301.1336 | 2087.2736 | 1907.6312 | 1864.8592 | 1830.6416 | 1796.424 | 1762.2064 | 1727.9888 | 1702.3256 | 1668.108 | 1642.4448 | 1616.7816 | 1599.6728 | 1582.564 | 1574.0096 | 1548.3464 | 1539.792 | 1522.6832 | 1505.5744 | 1497.02 | 1488.4656 | 1471.3568 | 1462.8024 | 1454.248 | 1445.6936
GenCost Global NZE by 2050 Battery storage (8hrs storage) | Battery storage (8hrs storage) | GenCost Global NZE by 2050 | 4148.884 | 4174.5472 | 3575.7392 | 3071.0296 | 2651.864 | 2301.1336 | 2061.6104 | 1804.9784 | 1591.1184 | 1308.8232 | 1291.7144 | 1274.6056 | 1257.4968 | 1240.388 | 1231.8336 | 1214.7248 | 1197.616 | 1189.0616 | 1171.9528 | 1163.3984 | 1154.844 | 1146.2896 | 1129.1808 | 1120.6264 | 1112.072 | 1103.5176 | 1094.9632 | 1086.4088 | 1077.8544 | 1069.3 | 1060.7456 | 1060.7456
Green Energy Exports Battery storage (8hrs storage) | Battery storage (8hrs storage) | Green Energy Exports | 4148.884 | 4174.5472 | 3575.7392 | 3071.0296 | 2651.864 | 2301.1336 | 2061.6104 | 1804.9784 | 1591.1184 | 1308.8232 | 1291.7144 | 1274.6056 | 1257.4968 | 1240.388 | 1231.8336 | 1214.7248 | 1197.616 | 1189.0616 | 1171.9528 | 1163.3984 | 1154.844 | 1146.2896 | 1129.1808 | 1120.6264 | 1112.072 | 1103.5176 | 1094.9632 | 1086.4088 | 1077.8544 | 1069.3 | 1060.7456 | 1060.7456
Step Change Battery storage (8hrs storage) | Battery storage (8hrs storage) | Step Change | 4148.884 | 4174.5472 | 3746.8272 | 3370.4336 | 3036.812 | 2737.408 | 2540.6568 | 2301.1336 | 2087.2736 | 1907.6312 | 1864.8592 | 1830.6416 | 1796.424 | 1762.2064 | 1727.9888 | 1702.3256 | 1668.108 | 1642.4448 | 1616.7816 | 1599.6728 | 1582.564 | 1574.0096 | 1548.3464 | 1539.792 | 1522.6832 | 1505.5744 | 1497.02 | 1488.4656 | 1471.3568 | 1462.8024 | 1454.248 | 1445.6936
Progressive Change Battery storage (8hrs storage) | Battery storage (8hrs storage) | Progressive Change | 4148.884 | 4174.5472 | 3926.4696 | 3704.0552 | 3515.8584 | 3447.4232 | 3370.4336 | 3250.672 | 3130.9104 | 3011.1488 | 2891.3872 | 2771.6256 | 2651.864 | 2532.1024 | 2412.3408 | 2301.1336 | 2241.2528 | 2198.4808 | 2147.1544 | 2112.9368 | 2087.2736 | 2070.1648 | 2027.3928 | 1993.1752 | 1958.9576 | 1941.8488 | 1924.74 | 1907.6312 | 1890.5224 | 1881.968 | 1881.968 | 1873.4136
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Wind | Wind | GenCost Current Policies | 2825.0906 | 2827.2292 | 2693.5667 | 2564.1814 | 2442.2812 | 2301.1336 | 2198.4808 | 2134.3228 | 2126.8377 | 2120.4219 | 2115.0754 | 2110.7982 | 2108.6596 | 2105.4517 | 2103.3131 | 2100.1052 | 2097.9666 | 2095.828 | 2094.7587 | 2091.5508 | 2088.3429 | 2084.0657 | 2079.7885 | 2074.442 | 2071.2341 | 2066.9569 | 2064.8183 | 2061.6104 | 2060.5411 | 2058.4025 | 2057.3332 | 2055.1946
GenCost Global NZE post 2050 Wind | Wind | GenCost Global NZE post 2050 | 2825.0906 | 2827.2292 | 2693.5667 | 2564.1814 | 2442.2812 | 2323.5889 | 2210.2431 | 2103.3131 | 2031.67 | 1993.1752 | 1987.8287 | 1980.3436 | 1973.9278 | 1968.5813 | 1964.3041 | 1960.0269 | 1954.6804 | 1948.2646 | 1942.9181 | 1937.5716 | 1931.1558 | 1926.8786 | 1923.6707 | 1920.4628 | 1919.3935 | 1917.2549 | 1916.1856 | 1912.9777 | 1910.8391 | 1908.7005 | 1907.6312 | 1906.5619
GenCost Global NZE by 2050 Wind | Wind | GenCost Global NZE by 2050 | 2825.0906 | 2827.2292 | 2695.7053 | 2569.5279 | 2448.697 | 2332.1433 | 2220.9361 | 2115.0754 | 2045.5709 | 2010.284 | 2009.2147 | 1995.3138 | 1967.512 | 1932.2251 | 1902.2847 | 1880.8987 | 1864.8592 | 1850.9583 | 1839.196 | 1827.4337 | 1817.81 | 1810.3249 | 1803.9091 | 1796.424 | 1787.8696 | 1779.3152 | 1770.7608 | 1762.2064 | 1755.7906 | 1751.5134 | 1750.4441 | 1748.3055
Green Energy Exports Wind | Wind | Green Energy Exports | 2825.0906 | 2827.2292 | 2695.7053 | 2569.5279 | 2448.697 | 2332.1433 | 2220.9361 | 2115.0754 | 2045.5709 | 2010.284 | 2009.2147 | 1995.3138 | 1967.512 | 1932.2251 | 1902.2847 | 1880.8987 | 1864.8592 | 1850.9583 | 1839.196 | 1827.4337 | 1817.81 | 1810.3249 | 1803.9091 | 1796.424 | 1787.8696 | 1779.3152 | 1770.7608 | 1762.2064 | 1755.7906 | 1751.5134 | 1750.4441 | 1748.3055
Step Change Wind | Wind | Step Change | 2825.0906 | 2827.2292 | 2693.5667 | 2564.1814 | 2442.2812 | 2323.5889 | 2210.2431 | 2103.3131 | 2031.67 | 1993.1752 | 1987.8287 | 1980.3436 | 1973.9278 | 1968.5813 | 1964.3041 | 1960.0269 | 1954.6804 | 1948.2646 | 1942.9181 | 1937.5716 | 1931.1558 | 1926.8786 | 1923.6707 | 1920.4628 | 1919.3935 | 1917.2549 | 1916.1856 | 1912.9777 | 1910.8391 | 1908.7005 | 1907.6312 | 1906.5619
Progressive Change Wind | Wind | Progressive Change | 2825.0906 | 2827.2292 | 2693.5667 | 2564.1814 | 2442.2812 | 2301.1336 | 2198.4808 | 2134.3228 | 2126.8377 | 2120.4219 | 2115.0754 | 2110.7982 | 2108.6596 | 2105.4517 | 2103.3131 | 2100.1052 | 2097.9666 | 2095.828 | 2094.7587 | 2091.5508 | 2088.3429 | 2084.0657 | 2079.7885 | 2074.442 | 2071.2341 | 2066.9569 | 2064.8183 | 2061.6104 | 2060.5411 | 2058.4025 | 2057.3332 | 2055.1946
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Wind - offshore (fixed) | Wind - offshore (fixed) | GenCost Current Policies | 6075.7626 | 5859.764 | 5654.4584 | 5456.6379 | 5265.2332 | 5168.9962 | 5131.5707 | 5151.8874 | 5135.8479 | 5120.8777 | 5104.8382 | 5088.7987 | 5073.8285 | 5057.789 | 5042.8188 | 5027.8486 | 5012.8784 | 4996.8389 | 4981.8687 | 4965.8292 | 4948.7204 | 4932.6809 | 4915.5721 | 4899.5326 | 4882.4238 | 4866.3843 | 4850.3448 | 4834.3053 | 4823.6123 | 4806.5035 | 4795.8105 | 4773.3552
GenCost Global NZE post 2050 Wind - offshore (fixed) | Wind - offshore (fixed) | GenCost Global NZE post 2050 | 6075.7626 | 5859.764 | 5654.4584 | 5456.6379 | 5265.2332 | 5085.5908 | 4918.78 | 4765.8701 | 4653.5936 | 4580.8812 | 4537.0399 | 4484.6442 | 4437.595 | 4400.1695 | 4383.0607 | 4353.1203 | 4331.7343 | 4295.3781 | 4264.3684 | 4223.735 | 4193.7946 | 4164.9235 | 4140.3296 | 4113.5971 | 4089.0032 | 4064.4093 | 4043.0233 | 4022.7066 | 4010.9443 | 3986.3504 | 3968.1723 | 3933.9547
GenCost Global NZE by 2050 Wind - offshore (fixed) | Wind - offshore (fixed) | GenCost Global NZE by 2050 | 6075.7626 | 5226.7384 | 4809.7114 | 4417.2783 | 4055.8549 | 3722.2333 | 3415.3442 | 3134.1183 | 2945.9215 | 2846.4766 | 2829.3678 | 2818.6748 | 2809.0511 | 2800.4967 | 2791.9423 | 2784.4572 | 2778.0414 | 2772.6949 | 2768.4177 | 2763.0712 | 2757.7247 | 2752.3782 | 2747.0317 | 2741.6852 | 2737.408 | 2732.0615 | 2725.6457 | 2719.2299 | 2714.9527 | 2708.5369 | 2705.329 | 2698.9132
Green Energy Exports Wind - offshore (fixed) | Wind - offshore (fixed) | Green Energy Exports | 6075.7626 | 5226.7384 | 4809.7114 | 4417.2783 | 4055.8549 | 3722.2333 | 3415.3442 | 3134.1183 | 2945.9215 | 2846.4766 | 2829.3678 | 2818.6748 | 2809.0511 | 2800.4967 | 2791.9423 | 2784.4572 | 2778.0414 | 2772.6949 | 2768.4177 | 2763.0712 | 2757.7247 | 2752.3782 | 2747.0317 | 2741.6852 | 2737.408 | 2732.0615 | 2725.6457 | 2719.2299 | 2714.9527 | 2708.5369 | 2705.329 | 2698.9132
Step Change Wind - offshore (fixed) | Wind - offshore (fixed) | Step Change | 6075.7626 | 5859.764 | 5654.4584 | 5456.6379 | 5265.2332 | 5085.5908 | 4918.78 | 4765.8701 | 4653.5936 | 4580.8812 | 4537.0399 | 4484.6442 | 4437.595 | 4400.1695 | 4383.0607 | 4353.1203 | 4331.7343 | 4295.3781 | 4264.3684 | 4223.735 | 4193.7946 | 4164.9235 | 4140.3296 | 4113.5971 | 4089.0032 | 4064.4093 | 4043.0233 | 4022.7066 | 4010.9443 | 3986.3504 | 3968.1723 | 3933.9547
Progressive Change Wind - offshore (fixed) | Wind - offshore (fixed) | Progressive Change | 6075.7626 | 5859.764 | 5654.4584 | 5456.6379 | 5265.2332 | 5168.9962 | 5131.5707 | 5151.8874 | 5135.8479 | 5120.8777 | 5104.8382 | 5088.7987 | 5073.8285 | 5057.789 | 5042.8188 | 5027.8486 | 5012.8784 | 4996.8389 | 4981.8687 | 4965.8292 | 4948.7204 | 4932.6809 | 4915.5721 | 4899.5326 | 4882.4238 | 4866.3843 | 4850.3448 | 4834.3053 | 4823.6123 | 4806.5035 | 4795.8105 | 4773.3552
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
GenCost Current Policies Wind - offshore (floating) | Wind - offshore (floating) | GenCost Current Policies | 8417.5296 | 8117.0563 | 7649.7722 | 7203.8741 | 6783.6392 | 6424.3544 | 6191.247 | 6078.9705 | 6049.0301 | 6034.0599 | 6031.9213 | 6021.2283 | 5988.08 | 5952.7931 | 5928.1992 | 5927.1299 | 5930.3378 | 5932.4764 | 5934.615 | 5933.5457 | 5932.4764 | 5931.4071 | 5929.2685 | 5927.1299 | 5924.9913 | 5923.922 | 5924.9913 | 5924.9913 | 5924.9913 | 5923.922 | 5923.922 | 5921.7834
GenCost Global NZE post 2050 Wind - offshore (floating) | Wind - offshore (floating) | GenCost Global NZE post 2050 | 8417.5296 | 8117.0563 | 7649.7722 | 7203.8741 | 6783.6392 | 6393.3447 | 6034.0599 | 5705.7848 | 5483.3704 | 5364.6781 | 5331.5298 | 5293.035 | 5206.4217 | 5127.2935 | 5065.2741 | 5043.8881 | 5029.9872 | 5004.324 | 4982.938 | 4951.9283 | 4930.5423 | 4910.2256 | 4894.1861 | 4873.8694 | 4856.7606 | 4840.7211 | 4825.7509 | 4812.9193 | 4804.3649 | 4787.2561 | 4774.4245 | 4749.8306
GenCost Global NZE by 2050 Wind - offshore (floating) | Wind - offshore (floating) | GenCost Global NZE by 2050 | 8417.5296 | 7240.2303 | 6530.2151 | 5868.3184 | 5274.8569 | 4736.999 | 4254.7447 | 3821.6782 | 3542.5909 | 3405.7205 | 3396.0968 | 3391.8196 | 3296.6519 | 3200.4149 | 3105.2472 | 3104.1779 | 3103.1086 | 3102.0393 | 3103.1086 | 3102.0393 | 3100.97 | 3100.97 | 3099.9007 | 3099.9007 | 3098.8314 | 2943.7829 | 2737.408 | 2510.7164 | 2438.004 | 2405.925 | 2395.232 | 2377.0539
Green Energy Exports Wind - offshore (floating) | Wind - offshore (floating) | Green Energy Exports | 8417.5296 | 7240.2303 | 6530.2151 | 5868.3184 | 5274.8569 | 4736.999 | 4254.7447 | 3821.6782 | 3542.5909 | 3405.7205 | 3396.0968 | 3391.8196 | 3296.6519 | 3200.4149 | 3105.2472 | 3104.1779 | 3103.1086 | 3102.0393 | 3103.1086 | 3102.0393 | 3100.97 | 3100.97 | 3099.9007 | 3099.9007 | 3098.8314 | 2943.7829 | 2737.408 | 2510.7164 | 2438.004 | 2405.925 | 2395.232 | 2377.0539
Step Change Wind - offshore (floating) | Wind - offshore (floating) | Step Change | 8417.5296 | 8117.0563 | 7649.7722 | 7203.8741 | 6783.6392 | 6393.3447 | 6034.0599 | 5705.7848 | 5483.3704 | 5364.6781 | 5331.5298 | 5293.035 | 5206.4217 | 5127.2935 | 5065.2741 | 5043.8881 | 5029.9872 | 5004.324 | 4982.938 | 4951.9283 | 4930.5423 | 4910.2256 | 4894.1861 | 4873.8694 | 4856.7606 | 4840.7211 | 4825.7509 | 4812.9193 | 4804.3649 | 4787.2561 | 4774.4245 | 4749.8306
Progressive Change Wind - offshore (floating) | Wind - offshore (floating) | Progressive Change | 8417.5296 | 8117.0563 | 7649.7722 | 7203.8741 | 6783.6392 | 6424.3544 | 6191.247 | 6078.9705 | 6049.0301 | 6034.0599 | 6031.9213 | 6021.2283 | 5988.08 | 5952.7931 | 5928.1992 | 5927.1299 | 5930.3378 | 5932.4764 | 5934.615 | 5933.5457 | 5932.4764 | 5931.4071 | 5929.2685 | 5927.1299 | 5924.9913 | 5923.922 | 5924.9913 | 5924.9913 | 5924.9913 | 5923.922 | 5923.922 | 5921.7834
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
All scenarios Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | All scenarios | 3355.4634 | 3290.2361 | 3227.1474 | 3164.0587 | 3100.97 | 3035.7427 | 2970.5154 | 2904.2188 | 2838.9915 | 2835.7836 | 2831.5064 | 2828.2985 | 2825.0906 | 2821.8827 | 2818.6748 | 2815.4669 | 2812.259 | 2809.0511 | 2805.8432 | 2801.566 | 2797.2888 | 2793.0116 | 2788.7344 | 2784.4572 | 2780.18 | 2775.9028 | 2771.6256 | 2768.4177 | 2764.1405 | 2758.794 | 2754.5168 | 2749.1703
Green Energy Exports Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Green Energy Exports | 3355.4634 | 3290.2361 | 3227.1474 | 3164.0587 | 3100.97 | 3035.7427 | 2970.5154 | 2904.2188 | 2838.9915 | 2835.7836 | 2831.5064 | 2828.2985 | 2825.0906 | 2821.8827 | 2818.6748 | 2815.4669 | 2812.259 | 2809.0511 | 2805.8432 | 2801.566 | 2797.2888 | 2793.0116 | 2788.7344 | 2784.4572 | 2780.18 | 2775.9028 | 2771.6256 | 2768.4177 | 2764.1405 | 2758.794 | 2754.5168 | 2749.1703
Step Change Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Step Change | 3355.4634 | 3290.2361 | 3227.1474 | 3164.0587 | 3100.97 | 3035.7427 | 2970.5154 | 2904.2188 | 2838.9915 | 2835.7836 | 2831.5064 | 2828.2985 | 2825.0906 | 2821.8827 | 2818.6748 | 2815.4669 | 2812.259 | 2809.0511 | 2805.8432 | 2801.566 | 2797.2888 | 2793.0116 | 2788.7344 | 2784.4572 | 2780.18 | 2775.9028 | 2771.6256 | 2768.4177 | 2764.1405 | 2758.794 | 2754.5168 | 2749.1703
Progressive Change Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Progressive Change | 3355.4634 | 3290.2361 | 3227.1474 | 3164.0587 | 3100.97 | 3035.7427 | 2970.5154 | 2904.2188 | 2838.9915 | 2835.7836 | 2831.5064 | 2828.2985 | 2825.0906 | 2821.8827 | 2818.6748 | 2815.4669 | 2812.259 | 2809.0511 | 2805.8432 | 2801.566 | 2797.2888 | 2793.0116 | 2788.7344 | 2784.4572 | 2780.18 | 2775.9028 | 2771.6256 | 2768.4177 | 2764.1405 | 2758.794 | 2754.5168 | 2749.1703
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
All scenarios Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | All scenarios | 4709.1972 | 4618.3067 | 4528.4855 | 4439.7336 | 4352.051 | 4260.0912 | 4168.1314 | 4076.1716 | 3984.2118 | 3978.8653 | 3974.5881 | 3969.2416 | 3964.9644 | 3960.6872 | 3955.3407 | 3951.0635 | 3946.7863 | 3942.5091 | 3938.2319 | 3931.8161 | 3926.4696 | 3920.0538 | 3913.638 | 3908.2915 | 3901.8757 | 3896.5292 | 3890.1134 | 3884.7669 | 3878.3511 | 3871.9353 | 3865.5195 | 3859.1037
Green Energy Exports Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Green Energy Exports | 4709.1972 | 4618.3067 | 4528.4855 | 4439.7336 | 4352.051 | 4260.0912 | 4168.1314 | 4076.1716 | 3984.2118 | 3978.8653 | 3974.5881 | 3969.2416 | 3964.9644 | 3960.6872 | 3955.3407 | 3951.0635 | 3946.7863 | 3942.5091 | 3938.2319 | 3931.8161 | 3926.4696 | 3920.0538 | 3913.638 | 3908.2915 | 3901.8757 | 3896.5292 | 3890.1134 | 3884.7669 | 3878.3511 | 3871.9353 | 3865.5195 | 3859.1037
Step Change Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Step Change | 4709.1972 | 4618.3067 | 4528.4855 | 4439.7336 | 4352.051 | 4260.0912 | 4168.1314 | 4076.1716 | 3984.2118 | 3978.8653 | 3974.5881 | 3969.2416 | 3964.9644 | 3960.6872 | 3955.3407 | 3951.0635 | 3946.7863 | 3942.5091 | 3938.2319 | 3931.8161 | 3926.4696 | 3920.0538 | 3913.638 | 3908.2915 | 3901.8757 | 3896.5292 | 3890.1134 | 3884.7669 | 3878.3511 | 3871.9353 | 3865.5195 | 3859.1037
Progressive Change Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Progressive Change | 4709.1972 | 4618.3067 | 4528.4855 | 4439.7336 | 4352.051 | 4260.0912 | 4168.1314 | 4076.1716 | 3984.2118 | 3978.8653 | 3974.5881 | 3969.2416 | 3964.9644 | 3960.6872 | 3955.3407 | 3951.0635 | 3946.7863 | 3942.5091 | 3938.2319 | 3931.8161 | 3926.4696 | 3920.0538 | 3913.638 | 3908.2915 | 3901.8757 | 3896.5292 | 3890.1134 | 3884.7669 | 3878.3511 | 3871.9353 | 3865.5195 | 3859.1037
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
All scenarios Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | All scenarios | 7074.4888 | 6937.6184 | 6801.8173 | 6670.2934 | 6537.7002 | 6399.7605 | 6261.8208 | 6122.8118 | 5984.8721 | 5977.387 | 5969.9019 | 5963.4861 | 5956.001 | 5949.5852 | 5942.1001 | 5935.6843 | 5929.2685 | 5922.8527 | 5915.3676 | 5906.8132 | 5898.2588 | 5888.6351 | 5880.0807 | 5870.457 | 5861.9026 | 5853.3482 | 5843.7245 | 5835.1701 | 5826.6157 | 5816.992 | 5806.299 | 5796.6753
Green Energy Exports Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Green Energy Exports | 7074.4888 | 6937.6184 | 6801.8173 | 6670.2934 | 6537.7002 | 6399.7605 | 6261.8208 | 6122.8118 | 5984.8721 | 5977.387 | 5969.9019 | 5963.4861 | 5956.001 | 5949.5852 | 5942.1001 | 5935.6843 | 5929.2685 | 5922.8527 | 5915.3676 | 5906.8132 | 5898.2588 | 5888.6351 | 5880.0807 | 5870.457 | 5861.9026 | 5853.3482 | 5843.7245 | 5835.1701 | 5826.6157 | 5816.992 | 5806.299 | 5796.6753
Step Change Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Step Change | 7074.4888 | 6937.6184 | 6801.8173 | 6670.2934 | 6537.7002 | 6399.7605 | 6261.8208 | 6122.8118 | 5984.8721 | 5977.387 | 5969.9019 | 5963.4861 | 5956.001 | 5949.5852 | 5942.1001 | 5935.6843 | 5929.2685 | 5922.8527 | 5915.3676 | 5906.8132 | 5898.2588 | 5888.6351 | 5880.0807 | 5870.457 | 5861.9026 | 5853.3482 | 5843.7245 | 5835.1701 | 5826.6157 | 5816.992 | 5806.299 | 5796.6753
Progressive Change Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Progressive Change | 7074.4888 | 6937.6184 | 6801.8173 | 6670.2934 | 6537.7002 | 6399.7605 | 6261.8208 | 6122.8118 | 5984.8721 | 5977.387 | 5969.9019 | 5963.4861 | 5956.001 | 5949.5852 | 5942.1001 | 5935.6843 | 5929.2685 | 5922.8527 | 5915.3676 | 5906.8132 | 5898.2588 | 5888.6351 | 5880.0807 | 5870.457 | 5861.9026 | 5853.3482 | 5843.7245 | 5835.1701 | 5826.6157 | 5816.992 | 5806.299 | 5796.6753
| Technology | Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
All scenarios BOTN - Cethana | BOTN - Cethana | All scenarios | 2400.7511 | 2358.5711 | 2316.789 | 2274.7354 | 2233.7663 | 2190.4524 | 2146.9843 | 2102.736 | 2058.9689 | 2059.8854 | 2061.3597 | 2061.6667 | 2063.1491 | 2064.6369 | 2064.9504 | 2066.4463 | 2067.9477 | 2068.8289 | 2070.3396 | 2070.7295 | 2071.0554 | 2071.4479 | 2071.8419 | 2072.1712 | 2072.5678 | 2072.8994 | 2073.2987 | 2073.6325 | 2074.0345 | 2074.4371 | 2074.8402 | 2075.244
Green Energy Exports BOTN - Cethana | BOTN - Cethana | Green Energy Exports | 2400.7511 | 2358.5711 | 2316.789 | 2274.7354 | 2233.7663 | 2190.4524 | 2146.9843 | 2102.736 | 2058.9689 | 2059.8854 | 2061.3597 | 2061.6667 | 2063.1491 | 2064.6369 | 2064.9504 | 2066.4463 | 2067.9477 | 2068.8289 | 2070.3396 | 2070.7295 | 2071.0554 | 2071.4479 | 2071.8419 | 2072.1712 | 2072.5678 | 2072.8994 | 2073.2987 | 2073.6325 | 2074.0345 | 2074.4371 | 2074.8402 | 2075.244
Step Change BOTN - Cethana | BOTN - Cethana | Step Change | 2400.7511 | 2358.5711 | 2316.789 | 2274.7354 | 2233.7663 | 2190.4524 | 2146.9843 | 2102.736 | 2058.9689 | 2059.8854 | 2061.3597 | 2061.6667 | 2063.1491 | 2064.6369 | 2064.9504 | 2066.4463 | 2067.9477 | 2068.8289 | 2070.3396 | 2070.7295 | 2071.0554 | 2071.4479 | 2071.8419 | 2072.1712 | 2072.5678 | 2072.8994 | 2073.2987 | 2073.6325 | 2074.0345 | 2074.4371 | 2074.8402 | 2075.244
Progressive Change BOTN - Cethana | BOTN - Cethana | Progressive Change | 2400.7511 | 2358.5711 | 2316.789 | 2274.7354 | 2233.7663 | 2190.4524 | 2146.9843 | 2102.736 | 2058.9689 | 2059.8854 | 2061.3597 | 2061.6667 | 2063.1491 | 2064.6369 | 2064.9504 | 2066.4463 | 2067.9477 | 2068.8289 | 2070.3396 | 2070.7295 | 2071.0554 | 2071.4479 | 2071.8419 | 2072.1712 | 2072.5678 | 2072.8994 | 2073.2987 | 2073.6325 | 2074.0345 | 2074.4371 | 2074.8402 | 2075.244

## Locational Cost Factors
Go to Assumptions Summary
Locational cost factors
Locationall cost factors for each cost zone and cost component were originally estimated by GHD to provide an indication of the variation in each cost component of the project costs between geographic regions. These cost factors have been adjusted to be rebased to one for each component in each zone.
The locational cost factors for the land and development cost component have been updated to be consistent with Mott Macdonald report: AEMO Transmission Cost Database, Building Blocks Costs and Risks Factors Update, to ensure a similar treatment of land costs for generation and transmission.
Technology cost break down ratios are estimated from the technology cost for each of the cost components given by Aurecon.
The technology-specific locational cost factors are calculated as the sum of the locational cost adjustments for each cost component. Each component's locational cost adjustment is the product of the component's share of the total capital cost and the appropriate locational cost factor for that cost component.
CSIRO build costs projections for new entrants are overnight costs for construction in a low cost zone. These locational cost factors are used to convert the CSIRO cost estimates to each region-specific cost estimate.
Refer to the Renewable Energy Zones Sheet for the definition of each cost zone.
Locational cost factors
Cost zones | Equipment costs | Fuel connection costs | Cost of land and development 2 | Installation costs | O&M costs 3
NSW Low | 100% | 100% | 100% | 100% | 100%
NSW Medium | 105% | 107% | 79% | 110% | 108% | `
NSW High | 110% | 116% | 21% | 120% | 117%
QLD Low | 100% | 100% | 100% | 100% | 100%
QLD Medium | 105% | 110% | 49% | 115% | 112%
QLD High | 110% | 121% | 21% | 131% | 125%
SA Low | 100% | 100% | 100% | 100% | 100%
SA Medium | 105% | 110% | 33% | 115% | 112%
SA High | 110% | 120% | 17% | 129% | 124%
TAS Low | 100% | 100% | 100% | 100% | 100%
TAS Medium | 105% | 107% | 72% | 110% | 109%
TAS High | 110% | 114% | 64% | 121% | 117%
VIC Low | 100% | 100% | 100% | 100% | 100%
VIC Medium | 103% | 103% | 69% | 103% | 103%
VIC High | 105% | 105% | 36% | 105% | 105%
Notes:
1. Sourced from GHD 2018 AEMO Costs and Technical Parameter Review, adjusted to be rebased to the region's low cost zone.
2. The locational cost factors for the land and development cost component have been updated to be consistent with Mott Macdonald report: AEMO Transmission Cost Database, Building Blocks Costs and Risks Factors Update
3. Locational cost factors for New entrants' O&M costs components are applied to fixed and variable operations and maintenance costs.
Technology cost breakdown ratios
Technology | Equipment costs | Fuel connection costs | Cost of land and development | Installation costs
OCGT (small GT) | 61% | 5% | 8% | 26%
OCGT (large GT) | 59% | 9% | 8% | 25%
CCGT | 62% | 3% | 8% | 27%
CCGT with CCS | 63% | 2% | 8% | 27%
Hydrogen reciprocating engines | 55% | 0% | 8% | 37%
Biomass | 55% | 0% | 8% | 37%
Battery storage (1hr storage) | 82% | 0% | 5% | 13%
Battery storage (2hrs storage) | 83% | 0% | 4% | 13%
Battery storage (4hrs storage) | 85% | 0% | 2% | 13%
Battery Storage (8hrs storage) | 85% | 0% | 1% | 13%
Large scale Solar PV | 57% | 0% | 6% | 38%
Solar Thermal (15hrs Storage) | 74% | 0% | 1% | 25%
Wind | 73% | 0% | 2% | 24%
Wind - Offshore (fixed) | 69% | 0% | 2% | 29%
Wind - offshore (floating) | 69% | 0% | 2% | 29%
Notes:
1. Calculated from technology component costs provided in Aurecon 2022 Costs and Technical Parameter Review.
Technology-specific locational cost factors
Cost zones / Sub-region | OCGT (small GT) | OCGT (large GT) | CCGT | CCGT with CCS | Biomass | Battery storage (1hr storage) | Battery storage (2hrs storage) | Battery storage (4hrs storage) | Battery Storage (8hrs storage) | Large scale Solar PV | Solar Thermal (15hrs storage) | Wind | Wind - Offshore (fixed) | Wind - offshore (floating) | Hydrogen reciprocating engines | Pumped Hydro (8hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (48hrs storage) | BOTN - Cethana
NSW Low | 1 | 1.01 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99 | 1.01 | 1 | 0.99 | 1 | 1 | 1
NSW Medium | 1.0432 | 1.054 | 1.0433 | 1.0431 | 1.0477 | 1.0435 | 1.0461 | 1.0513 | 1.0434 | 1.0639 | 1.0599 | 1.0463 | 1.0593 | 1.0593 | 1.0477
NSW High | 1.0578 | 1.0702 | 1.0576 | 1.057 | 1.0658 | 1.0685 | 1.0774 | 1.0952 | 1.0931 | 1.0956 | 1.1161 | 1.0952 | 1.1112 | 1.1112 | 1.0658
QLD Low | 1 | 1.01 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99 | 1.01 | 1 | 0.99 | 1 | 1 | 1
QLD Medium | 1.0337 | 1.0452 | 1.0337 | 1.0332 | 1.0422 | 1.035 | 1.0406 | 1.0518 | 1.0469 | 1.0649 | 1.0694 | 1.0523 | 1.0678 | 1.0678 | 1.0422
QLD High | 1.0889 | 1.1022 | 1.0888 | 1.0877 | 1.1065 | 1.0828 | 1.0917 | 1.1095 | 1.1074 | 1.1374 | 1.1436 | 1.1216 | 1.1431 | 1.1431 | 1.1065
SA Low | 1 | 1.01 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99 | 1.01 | 1 | 0.99 | 1 | 1 | 1
SA Medium | 1.0209 | 1.0324 | 1.0209 | 1.0204 | 1.0294 | 1.027 | 1.0342 | 1.0486 | 1.0453 | 1.0553 | 1.0678 | 1.0491 | 1.0646 | 1.0646 | 1.0294
SA High | 1.08 | 1.0931 | 1.0799 | 1.0789 | 1.0959 | 1.0782 | 1.0875 | 1.1061 | 1.1044 | 1.1274 | 1.1382 | 1.116 | 1.1365 | 1.1365 | 1.0959
TAS Low | 1 | 1.01 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99 | 1.01 | 1 | 0.99 | 1 | 1 | 1
TAS Medium | 1.0376 | 1.0484 | 1.0377 | 1.0375 | 1.0421 | 1.04 | 1.0433 | 1.0499 | 1.0427 | 1.0597 | 1.0592 | 1.0449 | 1.0579 | 1.0579 | 1.0421
TAS High | 1.0938 | 1.1053 | 1.0941 | 1.0937 | 1.1039 | 1.0913 | 1.0959 | 1.1051 | 1.0987 | 1.1252 | 1.1229 | 1.1062 | 1.1227 | 1.1227 | 1.1039
VIC Low | 1 | 1.01 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99 | 1.01 | 1 | 0.99 | 1 | 1 | 1
VIC Medium | 1.0028 | 1.0131 | 1.0028 | 1.0028 | 1.0028 | 1.013 | 1.0164 | 1.0232 | 1.0163 | 1.0199 | 1.0266 | 1.0129 | 1.0232 | 1.0232 | 1.0028
VIC High | 0.9948 | 1.0053 | 0.9948 | 0.9948 | 0.9948 | 1.0155 | 1.0224 | 1.0362 | 1.0326 | 1.0191 | 1.0431 | 1.0257 | 1.0362 | 1.0362 | 0.9948
NQ | [15 empty] | 1.01 | 0.88 | 0.864
CQ | [15 empty] | 1.01 | 0.88 | 0.864
GG
SQ | [15 empty] | 1.114 | 0.964 | 0.876
NNSW | [15 empty] | 0.881 | 0.822 | 0.624
CNSW | [15 empty] | 1.025 | 1.08 | 1.121
SNSW | [15 empty] | 1.044 | 1.004 | 0.911
SNW
VIC | [15 empty] | 1 | 1 | 1
CSA | [15 empty] | 1.351 | 1.667
SESA
TAS | [15 empty] | 0.748 | 0.618 | 0.464 | 1
Notes:
Pumped hydro sub-regional costs adjustments are derived from the build costs provided in Entura Pumped Hydro Cost Modelling. The cost adjustments are relative to the VIC cost for the specified storage size.

## Lead time and project life
Go to Assumptions Summary
Lead time and project life
Development lead time considers the time necessary to undertake feasibility studies, secure necessary development approvals, and to construct the project. For capacity planning therefore, the lead time reflects the shortest time before a technology can commence operation.
Parameters for all technologies except pumped hydro are sourced from Aurecon 2022 Costs and Technical Parameter Review. Pumped hydro parameters are sourced from GHD 2018 AEMO costs and technical parameter review, except the economic life which is sourced information provided by Hydro Tasmania.
Aurecon have provided lead time as a combination of lead time for development, total lead time and construction time. These values have been adjusted for some technologies to reflect the degree of active development interest, as demonstrated by the projects proposed, advancing or committed in AEMO's Generation Information page, particularly for Wind, Battery and Solar technologies.
Technology | Lead time for development (years)1, 2 | Lead time (years)3 | Construction time (years) | Total lead time (years)4 | Economic life (years) 5 | Technical life (years) 6
OCGT (small GT) | 2 | 0.75 | 1.25 | 4 | 25 | 40
OCGT (large GT) | 2 | 1 | 1.1154 | 4 | 25 | 40
CCGT | 2 | 1 | 1.5 | 5 | 25 | 40
CCGT with CCS | 3 | 1 | 1.5 | 6 | 25 | 40
Biomass | 3 | 1.75 | 1.25 | 6 | 30 | 50
Large scale Solar PV | 0 | 1 | 0.5 | 2 | 30 | 30
Solar Thermal (15hrs Storage) | 2 | 1.75 | 1.75 | 6 | 25 | 40
Battery storage (1hr storage) | 0 | 1 | 0.84615 | 2 | 20 | 20
Battery storage (2hrs storage) | 0 | 1.2 | 1 | 2 | 20 | 20
Battery storage (4hrs storage) | 0 | 1.4 | 1.1538 | 3 | 20 | 20
Battery Storage (8hrs storage) | 0 | 1.6 | 1.3077 | 3 | 20 | 20
Wind | 0 | 1 | 1 | 2 | 25 | 30
Wind - offshore (fixed) | 4 | 2 | 3 | 9 | 25 | 30
Wind - offshore (floating) | 4 | 2 | 3 | 9 | 25 | 30
Pumped Hydro (8hrs storage) | 2 | 0 | 4 | 6 | 40 | 50
Pumped Hydro (24hrs storage) | 2 | 0 | 4 | 6 | 40 | 50
Pumped Hydro (48hrs storage) | 2 | 0 | 4 | 6 | 40 | 50
BOTN - Cethana | 2 | 0 | 4 | 6 | 40 | 50
Hydrogen reciprocating engines | 2 | 1 | 1 | 4 | 25 | 40
Notes:
1. Aurecon has assumed that lead time for development is the time to undertake feasibility studies, procurement and contract negotiations, obtain permits and approvals, secure land agreements, fuel supply and obtain financing.
2. Given existing development activity in these technologies, AEMO has removed the lead time for development for onshore wind, batteries and large-scale solar PV as stated by Aurecon. The total lead time therefore reflects construction and lead time only.
3. Aurecon has assumed lead time as the time from issue of Notice to Proceed (NTP) to the EPC contractor up to the delivery of all major equipment to site.
4. Aurecon has provided some components of lead time in weeks or fractions of years. AEMO has rounded the total lead time to the nearest whole number of years for capacity planning.
5. Period of time required for the project to recover build costs.
6. Period of time the project is operational before life extension refurbishment or retirement.

## Financial parameters
Go to Assumptions Summary
Discount rate
The discount rate is used to determine the present value of future cash flows during the cost-benefit analysis process.
Weighted Average Cost of Capital (WACC) expresses the costs incurred to obtain finance for capital expenditure.
The discount rate presented is pre-tax, real.
| Lower bound | Central assumption | Upper bound
Discount rate (%) | 3% | 7% | 10.5%
WACC, all new generation and transmission (%) | 3% | 7% | 10.5%
Sources: Synergies Economic Consulting, Updating the 2022 ISP Discount rate; Oxford Economics Australia, Cost of Capital Survey 2023.
Value of customer reliability (VCR)
A VCR expresses the value that customers place on having a reliable supply of electricity.
Values of customer reliability are used to quantify the differences in market benefits between development pathways arising from changes in involuntary load shedding.
| New South Wales | Queensland | South Australia | Tasmania | Victoria
Value of customer reliability ($/MWh, real 2023) | 49215.6544 | 46773.5671 | 50512.6482 | 37577.7646 | 48152.3533
Source:
https://www.aer.gov.au/system/files/AER%20-%20Values%20of%20Customer%20Reliability%20Review%20-%20Final%20Report%20-%20December%202019.pdf
(Table 5.22)

## Capacity Factors
Go to Assumptions Summary
Capacity factors for new large-scale renewables
Approximate capacity factors of solar and wind technology based on renewable resource quality. Capacity factors depend on the reference year modelled and are presented below for reference years where data is available.
Capacity factors are static for all installations. Changes in capacity factor due to technology improvement or natural reduction in preferred installation sites are not modelled.
Capacity factors are only included for REZs and technologies where the build limit is above 0 MW.
Wind High | [16 empty] | Wind Medium
REZ ID | REZ Name | Region | Reference year (Financial year ending) | [12 empty] | Avg of ref years | REZ ID | REZ Name | Region | Reference year (Financial year ending) | [12 empty] | Avg of ref years
|  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |  |  |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Q1 | Far North QLD | QLD | 42.64% | 46.26% | 46.62% | 49.13% | 47.56% | 43.23% | 46.33% | 49.1% | 48.67% | 46.16% | 44.36% | 41.96% | 41.95% | 45.69% | Q1 | Far North QLD | QLD | 40.1% | 43.34% | 44.67% | 46.01% | 44.98% | 40.14% | 42.26% | 44.81% | 44.08% | 41.93% | 40.43% | 38.27% | 38.28% | 42.25%
Q2 | North Qld Clean Energy Hub | QLD | 41.41% | 42.19% | 43.28% | 45.44% | 42.85% | 39.11% | 40.63% | 43.5% | 44.78% | 41.41% | 41.09% | 37.69% | 38.9% | 41.71% | Q2 | North Qld Clean Energy Hub | QLD | 32.09% | 32.95% | 34.54% | 37.22% | 34.96% | 31.16% | 31.71% | 33.06% | 35.01% | 31.78% | 31.76% | 29.97% | 29.6% | 32.75%
Q3 | Northern Qld | QLD | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | Q3 | Northern Qld | QLD | Resource limit of 0 MW
Q4 | Isaac | QLD | 32.29% | 32.38% | 33.87% | 36.71% | 34.09% | 32.94% | 33.51% | 33.71% | 39.47% | 33.33% | 36.32% | 35.29% | 33.77% | 34.44% | Q4 | Isaac | QLD | 29.29% | 28.57% | 30.19% | 33.06% | 30.09% | 28.71% | 29.73% | 29.97% | 34.53% | 28.52% | 31.48% | 30.13% | 29.42% | 30.28%
Q5 | Barcaldine | QLD | 32.67% | 31.24% | 34.51% | 34.41% | 34.67% | 32.2% | 31.54% | 32.79% | 35.78% | 31.12% | 32.28% | 30.78% | 29.85% | 32.6% | Q5 | Barcaldine | QLD | 29.89% | 28.01% | 31.42% | 31.67% | 31.31% | 29.18% | 28.62% | 30.06% | 32.89% | 28.07% | 29.4% | 27.99% | 27.25% | 29.67%
Q6 | Fitzroy | QLD | 37.38% | 37.62% | 36.83% | 37.35% | 37.37% | 35.38% | 36.46% | 35.15% | 40.61% | 34.46% | 37.72% | 36.11% | 34.74% | 36.71% | Q6 | Fitzroy | QLD | 31.88% | 31.78% | 31.72% | 32.9% | 31.76% | 30.56% | 31.29% | 30.4% | 35.54% | 29.81% | 32.58% | 31.06% | 29.78% | 31.62%
Q7 | Wide Bay | QLD | 29.85% | 30.27% | 30.2% | 28.38% | 29.18% | 28.21% | 28.07% | 29.05% | 30.59% | 27.06% | 28.59% | 29.35% | 28.56% | 29.03% | Q7 | Wide Bay | QLD | 28.63% | 29.62% | 29.96% | 28.28% | 28.69% | 27.9% | 27.68% | 28.99% | 29.77% | 26.49% | 27.9% | 29.08% | 28.1% | 28.55%
Q8 | Darling Downs | QLD | 38.17% | 36.85% | 37.16% | 35.27% | 38.05% | 35.64% | 35.09% | 37.38% | 39.36% | 36.3% | 38.11% | 39.55% | 37.77% | 37.28% | Q8 | Darling Downs | QLD | 32.5% | 31.33% | 32.22% | 30.95% | 33.07% | 31.05% | 30.52% | 32.59% | 34.65% | 32.12% | 33.21% | 34.12% | 32.63% | 32.38%
Q9 | Banana | QLD | 30.43% | 29.75% | 30.18% | 29.27% | 30.29% | 28.33% | 28.89% | 29.83% | 31.98% | 28.24% | 29.59% | 29.54% | 28.26% | 29.58% | Q9 | Banana | QLD | 25.27% | 24.95% | 25.73% | 24.92% | 25.82% | 23.72% | 25.17% | 25.27% | 27.41% | 24.46% | 25.45% | 25.42% | 23.86% | 25.19%
N1 | North West NSW | NSW | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | N1 | North West NSW | NSW | Resource limit of 0 MW
N2 | New England | NSW | 39.38% | 36.16% | 37.73% | 35.84% | 37.32% | 36.62% | 36.5% | 37.91% | 39.14% | 38.44% | 39.81% | 41.09% | 39.39% | 38.1% | N2 | New England | NSW | 38.22% | 34.88% | 36.45% | 34.72% | 35.76% | 35.51% | 35.62% | 36.98% | 37.53% | 37.26% | 38.87% | 40.11% | 38.22% | 36.93%
N3 | Central-West Orana | NSW | 37.09% | 34.19% | 34.63% | 33.6% | 34.74% | 34.1% | 33.79% | 36.08% | 35.29% | 37.47% | 36.4% | 37.45% | 36.36% | 35.48% | N3 | Central-West Orana | NSW | 34.02% | 32.14% | 32.43% | 31.21% | 33.19% | 31.65% | 31.9% | 34.17% | 34.06% | 34.79% | 33.92% | 34.78% | 34.33% | 33.28%
N4 | Broken Hill | NSW | 30.19% | 31.89% | 32.14% | 33.35% | 31.73% | 31.35% | 30.69% | 32.79% | 31.37% | 32.27% | 32.13% | 31.86% | 30.8% | 31.73% | N4 | Broken Hill | NSW | 27.48% | 29.16% | 29.29% | 30.52% | 29.31% | 28.86% | 28.26% | 29.95% | 28.89% | 29.69% | 29.46% | 29.51% | 28.33% | 29.13%
N5 | South West NSW | NSW | 26.7% | 28.86% | 29.08% | 31.13% | 27.98% | 27.69% | 29.11% | 30.57% | 30.68% | 31.12% | 30.25% | 30.13% | 28.9% | 29.4% | N5 | South West NSW | NSW | 26.51% | 28.53% | 28.92% | 30.85% | 27.95% | 27.6% | 28.53% | 30.49% | 30.38% | 30.88% | 30.07% | 29.9% | 28.68% | 29.18%
N6 | Wagga Wagga | NSW | 26.93% | 26.68% | 26.45% | 28.07% | 26.82% | 26.33% | 26.03% | 27.9% | 27.94% | 27.95% | 26.73% | 26.7% | 27.12% | 27.05% | N6 | Wagga Wagga | NSW | 25.7% | 25.72% | 25.45% | 26.63% | 25.63% | 25.14% | 25.3% | 27% | 26.47% | 26.88% | 25.95% | 26.4% | 26.03% | 26.02%
N7 | Tumut | NSW | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | N7 | Tumut | NSW | Resource limit of 0 MW
N8 | Cooma-Monaro | NSW | 40.36% | 39.11% | 41.89% | 42.8% | 39.62% | 41.44% | 40.95% | 43.64% | 42.06% | 40.79% | 42.21% | 41.51% | 42.82% | 41.48% | N8 | Cooma-Monaro | NSW | 37.34% | 36.14% | 38.99% | 40.33% | 36.86% | 38.29% | 37.95% | 40.42% | 39.01% | 38.43% | 39.08% | 38.27% | 39.34% | 38.5%
N9 | Hunter-Central Coast | NSW | 36.56% | 32.04% | 34.43% | 32.53% | 32.72% | 33.47% | 33.47% | 36.2% | 31.86% | 34.13% | 35.29% | 35.04% | 33.29% | 33.92% | N9 | Hunter-Central Coast | NSW | 32.96% | 29.28% | 31.02% | 30.11% | 29.63% | 31.53% | 30.63% | 32.61% | 29.51% | 33.23% | 32.94% | 32.72% | 31.34% | 31.35%
N12 | Illawarra | NSW | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | N12 | Illawarra | VIC | Resource limit of 0 MW
V1 | Ovens Murray | VIC | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | V1 | Ovens Murray | VIC | Resource limit of 0 MW
V2 | Murray River | VIC | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | V2 | Murray River | VIC | Resource limit of 0 MW
V3 | Western Victoria | VIC | 37.81% | 41.13% | 39.48% | 43.36% | 38.83% | 38.87% | 39.18% | 40.91% | 40.45% | 42.55% | 41.54% | 42.54% | 40.48% | 40.55% | V3 | Western Victoria | VIC | 33.17% | 35.94% | 34.7% | 38.02% | 34.45% | 34% | 34.28% | 36.3% | 36.17% | 37.61% | 36.33% | 37.63% | 35.49% | 35.7%
V4 | South West Victoria | VIC | 36.39% | 39.4% | 37.78% | 41.86% | 36.79% | 36.4% | 37.75% | 39.41% | 39.47% | 41.49% | 38.34% | 41.07% | 38.32% | 38.81% | V4 | South West Victoria | VIC | 35.78% | 38.53% | 37.05% | 41.19% | 35.9% | 35.58% | 37.4% | 38.98% | 38.82% | 40.89% | 37.71% | 40.2% | 37.61% | 38.13%
V5 | Gippsland | VIC | 36.67% | 37.55% | 36.86% | 40.31% | 36.99% | 36.43% | 37.63% | 37.8% | 37.52% | 41.26% | 40.42% | 39.69% | 37.41% | 38.19% | V5 | Gippsland | VIC | 33.4% | 34.33% | 33.52% | 36.69% | 33.99% | 32.95% | 33.51% | 34.13% | 34.04% | 37.47% | 36.75% | 35.89% | 33.79% | 34.65%
V6 | Central North Vic | VIC | 30.16% | 31.78% | 31.16% | 33.49% | 32.77% | 32.74% | 30.32% | 33.51% | 32.88% | 33.51% | 33.49% | 32.6% | 31.32% | 32.29% | V6 | Central North Vic | VIC | 28.53% | 30.06% | 29.42% | 32.09% | 31.17% | 30.91% | 29.24% | 31.88% | 31.59% | 31.72% | 31.84% | 31.54% | 30.35% | 30.79%
S1 | South East SA | SA | 34.66% | 37.64% | 35.97% | 40.25% | 36.32% | 35.98% | 35.39% | 38.33% | 38.59% | 39.49% | 36.6% | 39.64% | 37.44% | 37.41% | S1 | South East SA | SA | 32.9% | 35.78% | 34.39% | 38.61% | 34.48% | 33.8% | 33.53% | 36.18% | 36.61% | 37.23% | 34.72% | 37.4% | 35.21% | 35.45%
S2 | Riverland | SA | 25.59% | 27.55% | 27.94% | 30.62% | 26.87% | 27.52% | 27.26% | 31% | 30.37% | 29.8% | 28.56% | 29.7% | 28.35% | 28.55% | S2 | Riverland | SA | 25.17% | 27.03% | 27.5% | 30.02% | 26.43% | 27.01% | 26.9% | 30.49% | 29.9% | 29.37% | 28.06% | 29.16% | 27.82% | 28.07%
S3 | Mid-North SA | SA | 34.66% | 36.81% | 36.44% | 39.9% | 35.5% | 35.86% | 35.41% | 40.1% | 39.17% | 38.37% | 36.81% | 38.73% | 38.43% | 37.4% | S3 | Mid-North SA | SA | 33.05% | 34.98% | 34.78% | 37.65% | 33.47% | 34.89% | 33.89% | 38.19% | 37.81% | 36.65% | 35.01% | 35.98% | 35.81% | 35.55%
S4 | Yorke Peninsula | SA | 33.23% | 34.5% | 33.45% | 39.01% | 33.74% | 34.83% | 33.48% | 38.04% | 37.53% | 35.75% | 35.39% | 37.81% | 36.39% | 35.63% | S4 | Yorke Peninsula | SA | 31.16% | 32.4% | 32.25% | 37.52% | 31.97% | 32.86% | 32.04% | 36.49% | 36.03% | 33.99% | 33.8% | 35.6% | 34.38% | 33.88%
S5 | Northern SA | SA | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | S5 | Northern SA | SA | Resource limit of 0 MW
S6 | Leigh Creek | SA | 40.99% | 40.58% | 40.97% | 41.57% | 39.97% | 39.18% | 37.78% | 40.24% | 38.96% | 39.28% | 39.96% | 39.45% | 38.85% | 39.83% | S6 | Leigh Creek | SA | 37.92% | 37.33% | 37.84% | 38.47% | 36.98% | 36.23% | 34.98% | 37.01% | 36.06% | 36.4% | 36.84% | 36.67% | 36.04% | 36.83%
S7 | Roxby Downs | SA | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | S7 | Roxby Downs | SA | Resource limit of 0 MW
S8 | Eastern Eyre Peninsula | SA | 35.89% | 36.68% | 36.01% | 41.6% | 36.09% | 36.32% | 35.17% | 39.69% | 38.72% | 37.2% | 38.38% | 39.51% | 37.84% | 37.62% | S8 | Eastern Eyre Peninsula | SA | 34.19% | 35.16% | 34.78% | 39.75% | 34.44% | 35.15% | 33.75% | 38.19% | 37.08% | 35.57% | 36.63% | 37.77% | 36.15% | 36.05%
S9 | Western Eyre Peninsula | SA | 36.49% | 37.14% | 37.07% | 42.18% | 37.02% | 36.73% | 35.64% | 39.89% | 39.66% | 37.51% | 39.82% | 39.47% | 37.55% | 38.17% | S9 | Western Eyre Peninsula | SA | 35% | 35.63% | 35.68% | 40.4% | 35.64% | 35.34% | 34.4% | 38.64% | 38.47% | 36.42% | 38.19% | 38.06% | 36.57% | 36.8%
T1 | North East Tasmania | TAS | 42.57% | 42.37% | 41.33% | 44.57% | 42.55% | 43.08% | 46.43% | 43.4% | 45.59% | 47.26% | 42.85% | 44.72% | 41.37% | 43.7% | T1 | North East Tasmania | TAS | 39.87% | 39.16% | 38.42% | 41.69% | 39.46% | 39.63% | 43.55% | 40.47% | 41.82% | 43.88% | 39.6% | 41.05% | 38.14% | 40.52%
T2 | North West Tasmania | TAS | 48.82% | 48.33% | 45.68% | 47.94% | 47.81% | 45.46% | 47.54% | 48.66% | 47.43% | 49.74% | 48.23% | 46.57% | 45.9% | 47.55% | T2 | North West Tasmania | TAS | 45.74% | 45.94% | 42.88% | 45.98% | 45.32% | 42.4% | 44.07% | 46.21% | 44.88% | 47.1% | 45.73% | 44.62% | 43.43% | 44.95%
T3 | Central Highlands | TAS | 53.31% | 54.02% | 51.29% | 53.04% | 52.45% | 50.64% | 52.51% | 52.59% | 53.52% | 56.37% | 51.67% | 50.77% | 48.76% | 52.38% | T3 | Central Highlands | TAS | 50.59% | 51% | 48.79% | 50.86% | 48.74% | 47.19% | 50.77% | 49.51% | 50.56% | 53.73% | 48.2% | 46.97% | 45.2% | 49.39%
N0 | New South Wales Non-REZ | NSW | 37.49% | 33.14% | 33.79% | 33.15% | 33.35% | 33.74% | 33.2% | 34.86% | 32.84% | 36.86% | 35.42% | 37.44% | 37.26% | 34.81% | N0 | New South Wales Non-REZ | NSW | 35.07% | 30.83% | 31.54% | 30.79% | 30.98% | 31.46% | 31.16% | 32.47% | 30.55% | 34.25% | 33.06% | 34.86% | 34.55% | 32.43%
V0 | Victoria Non-REZ | VIC | 35.43% | 38% | 36.46% | 42.3% | 35.62% | 36.39% | 38.18% | 38.73% | 37.63% | 41.21% | 39.18% | 40.94% | 38.11% | 38.32% | V0 | Victoria Non-REZ | VIC | 34.46% | 37.25% | 35.62% | 41.69% | 34.63% | 35.66% | 37.38% | 38.04% | 36.94% | 40.39% | 38.27% | 40.32% | 37.31% | 37.54%
Solar PV | [16 empty] | Solar Thermal (15hrs storage)
REZ ID | REZ Name | Region | Reference year (Financial year ending) 2011: Reference year (Financial year ending) | Avg of ref years | REZ ID | REZ Name | Region | Reference year (Financial year ending) | [12 empty] | Avg of ref years
|  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |  |  |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Q1 | Far North QLD | QLD | 23.03% | 25.99% | 27.24% | 26.03% | 28.53% | 28.2% | 27.6% | 28.31% | 27.38% | 29.04% | 27.15% | 26.63% | 26.65% | 27.06% | Q1 | Far North QLD | QLD | 33.1% | 41.01% | 44.23% | 41.06% | 45.71% | 44.9% | 44.96% | 46.82% | 44.38% | 47.67% | 44.92% | 42.09% | 45.33% | 43.55%
Q2 | North Qld Clean Energy Hub | QLD | 26.3% | 28.91% | 29.94% | 29.95% | 31.41% | 31.15% | 30.98% | 30.7% | 30.97% | 32.42% | 30.65% | 30.26% | 29.51% | 30.24% | Q2 | North Qld Clean Energy Hub | QLD | 39.69% | 47.54% | 49.78% | 50.44% | 56.14% | 52.72% | 52.01% | 52.18% | 52.48% | 57.78% | 52.22% | 50.63% | 48.93% | 50.97%
Q3 | Northern Qld | QLD | 22.58% | 26.17% | 28.08% | 27.13% | 29.02% | 29.74% | 29% | 29.12% | 28.77% | 30.82% | 28.06% | 29.18% | 27.85% | 28.12% | Q3 | Northern Qld | QLD | 28.35% | 35.26% | 39.49% | 37.66% | 41.66% | 44.5% | 43.75% | 45.1% | 44.36% | 49.1% | 41.88% | 43.78% | 41.93% | 41.29%
Q4 | Isaac | QLD | 23.44% | 26.95% | 27.98% | 28.55% | 29.69% | 29.71% | 28.95% | 29.65% | 29.25% | 30.94% | 28.74% | 29.12% | 27.93% | 28.53% | Q4 | Isaac | QLD | 33.41% | 40.6% | 44.6% | 46.46% | 49.15% | 48.76% | 49.01% | 50.75% | 49.29% | 53.06% | 48.1% | 47.97% | 44.95% | 46.62%
Q5 | Barcaldine | QLD | 27.71% | 29.74% | 31.5% | 32.37% | 33.12% | 32.13% | 31.35% | 32.48% | 33.3% | 33.27% | 32.41% | 31.53% | 30.28% | 31.63% | Q5 | Barcaldine | QLD | 45.06% | 49.88% | 55.53% | 58.41% | 61.19% | 56.69% | 56.46% | 58.37% | 62.02% | 61.25% | 58.62% | 55.91% | 53.28% | 56.36%
Q6 | Fitzroy | QLD | 23.35% | 26.58% | 27.3% | 28.99% | 28.89% | 29.55% | 28.76% | 29.08% | 29.27% | 30.38% | 28.65% | 28.13% | 27.26% | 28.17% | Q6 | Fitzroy | QLD | 33.04% | 39.09% | 41.82% | 46.71% | 45.37% | 45.56% | 43.58% | 44.3% | 42.97% | 47.89% | 43.08% | 41.58% | 41.75% | 42.83%
Q7 | Wide Bay | QLD | 22.19% | 24.92% | 25.99% | 27.6% | 26.73% | 27.62% | 27.56% | 27.87% | 27.81% | 28.68% | 26.94% | 25.8% | 25.22% | 26.53% | Q7 | Wide Bay | QLD | 31.11% | 36.99% | 39.17% | 42.88% | 41.12% | 41.86% | 41.81% | 42.19% | 39.74% | 42.58% | 37.81% | 35.79% | 35.9% | 39.15%
Q8 | Darling Downs | QLD | 23.1% | 25.57% | 27.2% | 28.59% | 27.56% | 28.25% | 28.49% | 29.25% | 29.4% | 29.73% | 27.89% | 26.61% | 27.19% | 27.6% | Q8 | Darling Downs | QLD | 34.98% | 39.69% | 44.57% | 48.2% | 45.69% | 47.72% | 49.91% | 52.25% | 49.79% | 51% | 45.82% | 41.83% | 44.5% | 45.84%
Q9 | Banana | QLD | 24.03% | 27.24% | 28.29% | 30.14% | 29.68% | 29.86% | 29.69% | 30.33% | 30.36% | 31.13% | 29.38% | 28.77% | 27.77% | 28.98% | Q9 | Banana | QLD | 35.99% | 43.25% | 47.18% | 52.12% | 51.25% | 51.19% | 52.26% | 54.86% | 52.68% | 54.48% | 50.26% | 48.5% | 47.23% | 49.33%
N1 | North West NSW | NSW | 25.15% | 26.51% | 29.27% | 29.83% | 29.17% | 29.71% | 28.81% | 30.56% | 30.82% | 29.56% | 28.52% | 27.68% | 28.99% | 28.81% | N1 | North West NSW | NSW | 39.24% | 45.51% | 51.34% | 54.38% | 52.68% | 51.08% | 49.98% | 56.34% | 55.74% | 52.28% | 50.5% | 46.86% | 51.99% | 50.61%
N2 | New England | NSW | 21.97% | 23.5% | 25.79% | 27.19% | 25.9% | 27.12% | 26% | 27.95% | 27.9% | 26.86% | 25.54% | 24.29% | 26.55% | 25.89% | N2 | New England | NSW | 30.96% | 34.73% | 42.44% | 48.05% | 41.85% | 45.27% | 41.76% | 47.33% | 45.8% | 41.94% | 40.06% | 35.89% | 43.06% | 41.47%
N3 | Central-West Orana | NSW | 23.74% | 24.93% | 28.22% | 28.22% | 27.79% | 27.88% | 27.81% | 29.33% | 29.29% | 28.53% | 27.42% | 25.23% | 26.97% | 27.33% | N3 | Central-West Orana | NSW | 37.84% | 43.04% | 51.39% | 52.24% | 50.34% | 47.84% | 49.29% | 53.34% | 54.28% | 50.03% | 48.5% | 39.64% | 45.45% | 47.94%
N4 | Broken Hill | NSW | 26.86% | 28.52% | 30.13% | 29.94% | 30.41% | 28.9% | 29.58% | 30.62% | 31.58% | 32.73% | 30.4% | 30% | 29.69% | 29.95% | N4 | Broken Hill | NSW | 44.24% | 49.46% | 53.75% | 54% | 55.83% | 49.29% | 52.26% | 54.82% | 58.84% | 61.6% | 55.15% | 53.52% | 52.37% | 53.47%
N5 | South West NSW | NSW | 24.8% | 26.36% | 27.86% | 26.78% | 28.17% | 27.51% | 27.06% | 28.23% | 28.81% | 28.7% | 27.78% | 26.7% | 26.66% | 27.34% | N5 | South West NSW | NSW | 39.96% | 43.16% | 46.62% | 43.56% | 47.79% | 46.47% | 44.69% | 48.52% | 50.78% | 50.31% | 47.77% | 44.34% | 43.59% | 45.96%
N6 | Wagga Wagga | NSW | 23.66% | 25.28% | 27.07% | 25.87% | 27.05% | 26.57% | 25.96% | 27.21% | 27.51% | 26.77% | 26.37% | 24.63% | 25.36% | 26.1% | N6 | Wagga Wagga | NSW | 38.37% | 41.23% | 46.77% | 43.49% | 46.68% | 44.97% | 42.14% | 46.75% | 47.12% | 42.45% | 44.83% | 37.58% | 39.95% | 43.25%
N7 | Tumut | NSW | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | N7 | Tumut | NSW | Resource limit of 0 MW
N8 | Cooma-Monaro | NSW | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | N8 | Cooma-Monaro | NSW | Resource limit of 0 MW
N9 | Hunter-Central Coast | NSW | 21.75% | 22.46% | 25.38% | 26.63% | 25.18% | 25.51% | 25.21% | 26.86% | 26.69% | 25.57% | 24.18% | 23.18% | 25.81% | 24.96% | N9 | Hunter-Central Coast | NSW | 32.13% | 34.9% | 42.69% | 45.84% | 41.46% | 41.05% | 38.91% | 44.57% | 44.25% | 39.52% | 37.99% | 33.26% | 41.71% | 39.87%
N12 | Illawarra | NSW | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | N12 | Illawarra | NSW | Resource limit of 0 MW
V1 | Ovens Murray | VIC | 21.46% | 23.1% | 24.35% | 22.34% | 24.4% | 24.59% | 23.54% | 24.8% | 24.62% | 24% | 24.21% | 22.86% | 22.85% | 23.62% | V1 | Ovens Murray | VIC | 36.6% | 39.42% | 43.1% | 36.28% | 44.1% | 42.85% | 40.23% | 44.12% | 42.67% | 39.41% | 42.59% | 36.54% | 36.9% | 40.37%
V2 | Murray River | VIC | 24.69% | 26.39% | 27.81% | 26.37% | 28.11% | 27.49% | 27.07% | 27.92% | 28.68% | 28.47% | 27.45% | 27.23% | 26.54% | 27.25% | V2 | Murray River | VIC | 41.58% | 45.13% | 48.62% | 46.66% | 51.49% | 46.97% | 46.88% | 49.81% | 51.66% | 49.87% | 47.42% | 46.65% | 44.4% | 47.47%
V3 | Western Victoria | VIC | 20.07% | 22.19% | 23.13% | 21.76% | 23.26% | 23.52% | 23.22% | 24.25% | 24.63% | 23.46% | 22.83% | 23.07% | 22.76% | 22.93% | V3 | Western Victoria | VIC | 31.52% | 37.72% | 38.81% | 36.12% | 41.84% | 39.78% | 37.99% | 39.48% | 41.7% | 37.87% | 38.77% | 37.95% | 36.6% | 38.16%
V4 | South West Victoria | VIC | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | V4 | South West Victoria | VIC | Resource limit of 0 MW
V5 | Gippsland | VIC | 19.56% | 20.18% | 22.1% | 20.95% | 21.22% | 21.79% | 22.5% | 22.89% | 22.73% | 21.91% | 21.5% | 20.6% | 22.13% | 21.54% | V5 | Gippsland | VIC | 21.59% | 23.23% | 26.66% | 24.68% | 26.44% | 26.68% | 27.91% | 28.86% | 29.08% | 24.47% | 26.22% | 24.3% | 26.84% | 25.92%
V6 | Central North Vic | VIC | 23.48% | 25.27% | 26.27% | 24.7% | 26.37% | 26.19% | 25.47% | 26.52% | 26.56% | 26.08% | 25.95% | 24.55% | 24.88% | 25.56% | V6 | Central North Vic | VIC | 36.28% | 41.81% | 44.4% | 39.95% | 44.48% | 43.19% | 41.67% | 44.59% | 44.04% | 41.28% | 42.9% | 37.35% | 39.88% | 41.68%
S1 | South East SA | SA | 21.19% | 23.37% | 23.8% | 22.67% | 23.47% | 24.03% | 23.7% | 24.07% | 24.42% | 24.18% | 23.85% | 24.31% | 23.68% | 23.6% | S1 | South East SA | SA | 33.75% | 38.78% | 40.29% | 39.08% | 40.15% | 39.21% | 38.23% | 39.41% | 42.13% | 40.62% | 39.2% | 41.8% | 37.19% | 39.22%
S2 | Riverland | SA | 24.34% | 25.93% | 27.19% | 26.6% | 27.79% | 27.44% | 27.1% | 27.61% | 28.72% | 29.01% | 27.78% | 27.7% | 26.91% | 27.24% | S2 | Riverland | SA | 37.85% | 42.44% | 45.42% | 44.85% | 49.72% | 45.36% | 45.41% | 45.68% | 49.2% | 47.48% | 45.92% | 45.4% | 42.03% | 45.14%
S3 | Mid-North SA | SA | 23.09% | 24.82% | 26.02% | 25.03% | 26.18% | 26.12% | 25.67% | 25.86% | 27.02% | 27.5% | 26.46% | 26.31% | 25.7% | 25.83% | S3 | Mid-North SA | SA | 32.48% | 35.12% | 38.23% | 36.97% | 38.5% | 39.12% | 37.26% | 37.36% | 39.52% | 39.89% | 39.3% | 38.95% | 36.53% | 37.63%
S4 | Yorke Peninsula | SA | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | S4 | Yorke Peninsula | SA | Resource limit of 0 MW
S5 | Northern SA | SA | 25.35% | 27.04% | 28.04% | 27.04% | 28.31% | 27.95% | 27.97% | 28.15% | 28.75% | 29.88% | 28.08% | 28.27% | 28.05% | 27.91% | S5 | Northern SA | SA | 41.67% | 46.36% | 46.14% | 44.07% | 50.47% | 47.26% | 49.76% | 49.05% | 50.93% | 54.76% | 48.95% | 50.03% | 50.07% | 48.43%
S6 | Leigh Creek | SA | 27% | 28.76% | 29.6% | 29.83% | 30.42% | 29.1% | 29.62% | 30.23% | 31.34% | 32.49% | 30.41% | 29.74% | 30.15% | 29.9% | S6 | Leigh Creek | SA | 47.57% | 53.09% | 54.08% | 57.36% | 59.61% | 52.13% | 53.25% | 56.98% | 62.2% | 64.29% | 58.45% | 56.44% | 58.9% | 56.49%
S7 | Roxby Downs | SA | 27.6% | 29.31% | 30.46% | 30.38% | 30.72% | 30.01% | 30.73% | 30.89% | 31.94% | 33.45% | 31.33% | 30.74% | 31.3% | 30.68% | S7 | Roxby Downs | SA | 45.76% | 50.97% | 53.42% | 53.84% | 55.04% | 50.43% | 52.86% | 55.7% | 59.32% | 65.43% | 59.09% | 57.44% | 60.17% | 55.34%
S8 | Eastern Eyre Peninsula | SA | 21.53% | 23.57% | 25.27% | 23.88% | 24.62% | 24.94% | 25.12% | 24.79% | 26.19% | 26.23% | 25.31% | 24.42% | 25.25% | 24.7% | S8 | Eastern Eyre Peninsula | SA | 26.65% | 31.19% | 35.06% | 32.45% | 31.95% | 31.53% | 32.64% | 31.51% | 35.27% | 34.21% | 32.46% | 30.46% | 31.62% | 32.08%
S9 | Western Eyre Peninsula | SA | 24.32% | 26.1% | 27.63% | 26.83% | 28.04% | 27.52% | 27.75% | 27.61% | 28.29% | 29.15% | 27.85% | 27.92% | 27.79% | 27.45% | S9 | Western Eyre Peninsula | SA | 36.69% | 41.28% | 45.55% | 43.86% | 47.86% | 43.74% | 45.58% | 45.11% | 46.88% | 48.58% | 45.73% | 45.27% | 45.02% | 44.7%
T1 | North East Tasmania | TAS | 20.18% | 21.19% | 22.11% | 20.03% | 21.3% | 22.79% | 23% | 23.66% | 22.83% | 22.16% | 22.37% | 22.09% | 22.74% | 22.03% | T1 | North East Tasmania | TAS | 28.5% | 30.73% | 32.66% | 28.32% | 31.84% | 34% | 35.01% | 36.95% | 33.81% | 30.92% | 33.21% | 31.45% | 33.87% | 32.41%
T2 | North West Tasmania | TAS | 17.23% | 19.12% | 19.44% | 18.11% | 18.5% | 20.77% | 19.65% | 20.29% | 20.07% | 19.55% | 20.06% | 19.62% | 20.72% | 19.47% | T2 | North West Tasmania | TAS | 21.77% | 26.49% | 26.79% | 22.55% | 24.8% | 29.07% | 26.47% | 27.39% | 25.84% | 23.46% | 27.28% | 27.44% | 28.54% | 25.99%
T3 | Central Highlands | TAS | 18.67% | 19% | 20.47% | 19.36% | 20.08% | 21.76% | 21.26% | 21.7% | 21.97% | 21.4% | 21.06% | 20.08% | 21.24% | 20.62% | T3 | Central Highlands | TAS | 25.61% | 25.87% | 29.55% | 26.34% | 30.48% | 32.55% | 31.58% | 33.28% | 31.2% | 29.58% | 30.19% | 27.86% | 30.06% | 29.55%
N0 | New South Wales Non-REZ | NSW | 19.09% | 20.3% | 23.76% | 24.25% | 23.38% | 23.48% | 23.86% | 25.1% | 24.41% | 24.13% | 23.47% | 21.5% | 23.69% | 23.11% | N0 | New South Wales Non-REZ | NSW | 29.81% | 34.57% | 43.54% | 45.19% | 40.85% | 43.3% | 41.76% | 47.45% | 45.61% | 41.44% | 39.34% | 32.68% | 40.73% | 40.48%
V0 | Victoria Non-REZ | VIC | 17.78% | 18.58% | 20.36% | 19.36% | 19.82% | 20.38% | 21.09% | 21.77% | 21.74% | 20.57% | 20.66% | 20.2% | 21.1% | 20.26% | V0 | Victoria Non-REZ | VIC | 21.59% | 23.23% | 26.66% | 24.68% | 26.44% | 26.68% | 27.91% | 28.86% | 29.08% | 24.47% | 26.22% | 24.3% | 26.84% | 25.92%
Offshore Wind - Fixed | [16 empty] | Offshore Wind - Floating
REZ ID | REZ Name | Region | Reference year (Financial year ending) 2011: Reference year (Financial year ending) | Avg of ref years | REZ ID | REZ Name | Region | Reference year (Financial year ending) | [12 empty] | Avg of ref years
|  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 |  |  |  |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
N10 | Hunter Coast | NSW | Reference year (Financial year ending) 2011: Resource limit of 0 MW |  | N10 | Hunter Coast | NSW | 45.28% | 38.63% | 43.51% | 40.25% | 40.83% | 41.75% | 43.99% | 42.67% | 43.54% | 42.19% | 45.12% | 44.52% | 41.44% | 42.59%
N11 | Illawarra Coast | NSW | 41.97% | 39.35% | 41.85% | 42.51% | 40.79% | 40.4% | 40.51% | 42.15% | 39.8% | 40.54% | 40.92% | 40.53% | 42.58% | 41.07% | N11 | Illawarra Coast | NSW | 43.73% | 41.29% | 43.77% | 43.14% | 42.46% | 41.87% | 42.33% | 43.72% | 41.1% | 41.88% | 42.29% | 41.98% | 43.49% | 42.54%
V7 | Gippsland Coast | VIC | 45.56% | 45.29% | 45% | 48.25% | 44.74% | 45.56% | 46.92% | 48.33% | 46.74% | 49.69% | 48.43% | 48.78% | 45.9% | 46.86% | V7 | Gippsland Coast | VIC | 47.32% | 48.85% | 46.88% | 50.54% | 45.11% | 47.55% | 48.94% | 50.15% | 49.09% | 53.31% | 49.51% | 50.03% | 46.89% | 48.78%
V8 | Portland Coast | VIC | 42.81% | 46.5% | 44.51% | 47.18% | 42.58% | 42.5% | 43.7% | 45.01% | 45.41% | 48.45% | 44.59% | 48.22% | 44.46% | 45.07% | V8 | Portland Coast | VIC | 42.95% | 46.7% | 44.48% | 47.25% | 42.53% | 42.53% | 44.26% | 45.05% | 45.56% | 48.83% | 45.06% | 48.53% | 44.67% | 45.26%
S10 | South East SA Coast | SA | 42.01% | 46.07% | 43.58% | 47.7% | 43.68% | 44.02% | 42.71% | 45.26% | 45.59% | 47.32% | 44.11% | 48.2% | 45.29% | 45.04% | S10 | South East SA Coast | SA | 42.03% | 46.12% | 43.55% | 47.36% | 43.39% | 43.75% | 42.57% | 45.08% | 45.28% | 47.37% | 43.91% | 48.11% | 45.08% | 44.89%
T4 | North Tasmanian Coast | TAS | 47.85% | 48.75% | 45.58% | 50.51% | 45.66% | 46.88% | 48.01% | 49.86% | 49.59% | 52.22% | 49.44% | 49.57% | 47.36% | 48.56% | T4 | North Tasmanian Coast | TAS | 47.16% | 47.07% | 45.1% | 48.98% | 44.27% | 46.67% | 48.51% | 48.93% | 48.58% | 52.04% | 47.51% | 48.02% | 45.51% | 47.57%
T5 | North East Tasmanian Coast | TAS | 47.66% | 47.5% | 45.87% | 49.75% | 46.69% | 47.38% | 51.11% | 50.55% | 50.52% | 53.31% | 48.79% | 49.68% | 46.36% | 48.86% | T5 | North East Tasmanian Coast | TAS | 47.51% | 47.04% | 45.72% | 49.4% | 44.67% | 47.33% | 49.94% | 49.74% | 49.09% | 52.48% | 47.59% | 47.92% | 45.43% | 47.99%

## Connection cost
Go to Assumptions Summary
Initial connection costs ($/kW)
Connection costs increase the build costs of new technologies to cater for transmission infrastructure to connect to the grid, and varies depending on the proximity to transmission assets
Final connection costs will be subject to modelling outcomes
Connection Costs for Wind and Solar
REZ names | Region | REZ network voltage (kV) | Connection capacity (MVA) | Feeder length (km) | Total cost ($M)2 | $/kW | System Strength connection cost ($/kW)3
Far North Queensland | QLD | 275 | 300 | 5 | 35 | 116.67 | 137
North Queensland Clean Energy Hub | QLD | 275 | 300 | 10 | 48 | 160 | 137
Northern Queensland | QLD | 275 | 300 | 5 | 35 | 116.67 | 137
Isaac | QLD | 275 | 300 | 5 | 34 | 113.33 | 137
Barcaldine | QLD | 275 | 300 | 10 | 45 | 150 | 0
Fitzroy | QLD | 275 | 300 | 5 | 34 | 113.33 | 137
Wide Bay | QLD | 275 | 300 | 5 | 34 | 113.33 | 0
Darling Downs | QLD | 275 | 300 | 5 | 35 | 116.67 | 0
Banana | QLD | 275 | 1800 | 100 | 414 | 230 | 137
North West New South Wales | NSW | 330 | 400 | 10 | 54 | 135 | 0
New England | NSW | 330 | 400 | 10 | 54 | 135 | 0
Central-West Orana | NSW | 330 | 400 | 10 | 54 | 135 | 0
Broken Hill | NSW | 220 | 250 | 10 | 44 | 176 | 0
South West New South Wales | NSW | 330 | 400 | 10 | 54 | 135 | 0
Wagga Wagga | NSW | 330 | 400 | 10 | 54 | 135 | 137
Tumut | NSW | 330 | 400 | 5 | 40 | 100 | 0
Cooma-Monaro | NSW | 330 | 400 | 5 | 40 | 100 | 0
Hunter-Central Coast | NSW | 330 | 400 | 10 | 40 | 100 | 0
Hunter Coast | NSW | Note 1
Illawarra Coast | NSW | Note 1
Illawarra | NSW | 330 | 400 | 5 | 40 | 100 | 0
Ovens Murray | VIC | 220 | 250 | 5 | 34 | 136 | 0
Murray River | VIC | 220 | 250 | 5 | 33 | 132 | 137
Western Victoria | VIC | 220 | 250 | 5 | 35 | 140 | 137
South West Victoria | VIC | 500 | 600 | 10 | 84 | 140 | 137
Gippsland | VIC | 220 | 2000 | 16 | 684 | 340 | 0
Central North Victoria | VIC | 220 | 250 | 10 | 46 | 184 | 137
Gippsland Coast | VIC | 220 | 2000 | 16 | 684 | 340 | 137
Southern Ocean | VIC | Note 1 |  |  |  |  | 137
South East South Australia | SA | 275 | 300 | 10 | 45 | 150 | 137
Riverland | SA | 275 | 300 | 10 | 50 | 166.67 | 0
Mid-North South Australia | SA | 275 | 300 | 5 | 36 | 120 | 137
Yorke Peninsula | SA | 275 | 300 | 5 | 36 | 120 | 0
Northern South Australia | SA | 275 | 300 | 5 | 34 | 113.337 | 137
Leigh Creek | SA | 275 | 300 | 10 | 46 | 153.33 | 0
Roxby Downs | SA | 275 | 300 | 10 | 44 | 146.67 | 137
Eastern Eyre Peninsula | SA | 275 | 300 | 10 | 44 | 146.67 | 137
Western Eyre Peninsula | SA | 275 | 300 | 10 | 44 | 146.67 | 0
South East South Australia Coast | SA | 275 | 1200 | 50 | 894 | 745 | 137
North East Tasmania | TAS | 220 | 150 | 5 | 41 | 273.33 | 137
North West Tasmania | TAS | 220 | 150 | 5 | 36 | 240 | 137
Central Highlands | TAS | 220 | 150 | 5 | 33 | 220 | 137
North Tasmania Coast | TAS | Note 1 |  |  |  |  | 137
North-East Tasmania Coast | TAS | Note 1 |  |  |  |  | 137
Notes:
1. The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report.
2. The connection costs for all REZs was reviewed and consulted on through the 2023 Transmission Expansion Options Report.
3. Where no costs are shown, these have been allocated to REZ expansion costs instead.
Other generation - regional connection costs derived from connection voltage1 ($/kW)
Region | CCGT2 | CCGT with CCS | Small OCGT2 | Large OCGT | Reciprocating engines | Hydrogen Reciprocating engines | Biomass | 1 hr Battery Storage | 2 hr Battery Storage | 4 hr Battery Storage | 8 hr Battery Storage | Pumped Hydro3 (8 hrs storage) | Pumped Hydro (24 hrs storage) | Pumped Hydro (48 hrs storage) | BOTN- Cethana
QLD | 110.4943 | 110.4943 | 110.4943 | 110.4943 | 110.4943 | 110.4943 | 110.4943 | 103.3657 | 103.3657 | 103.3657 | 103.3657 | 0 | 0 | 0 | 0
NSW | 85.544 | 85.544 | 85.544 | 85.544 | 85.544 | 85.544 | 85.544 | 77.5242 | 77.5242 | 77.5242 | 77.5242 | 0 | 0 | 0 | 0
VIC | 80.1975 | 80.1975 | 115.4844 | 115.4844 | 115.4844 | 115.4844 | 115.4844 | 106.93 | 106.93 | 106.93 | 106.93 | 0 | 0 | 0 | 0
SA | 110.4943 | 110.4943 | 110.4943 | 110.4943 | 110.4943 | 110.4943 | 110.4943 | 103.3657 | 103.3657 | 103.3657 | 103.3657 | 0 | 0 | 0 | 0
TAS | 115.4844 | 115.4844 | 115.4844 | 115.4844 | 115.4844 | 115.4844 | 115.4844 | 106.93 | 106.93 | 106.93 | 106.93 | 0 | 0 | 0 | 0
Notes
1. The connection costs was reviewed and consulted on through the 2023 Transmission Expansion Options Report.
2. CCGT and OCGT - The physical location of these regional connections will depend on fuel / network infrastructure. For Victoria, OCGTs are assumed to connect to the 220 kV network, and larger CCGTs to the 500 kV network.
3. Pumped Hydro - Connection costs for Pumped Hydro are included in the capital costs provided by Entura.

## Connection Costs forecast
Go to Assumptions Summary
Connection costs forecast per REZ (real 2023 dollars)
Connection costs increase the build costs of new technologies to cater for transmission infrastructure to connect to the grid, and varies depending on the proximity to transmission assets
Final connection costs will be subject to modelling outcomes. The below connection costs are forecasted escalated costs based on real 2023 dollars.
AEMO has applied escalation factors to REZ augmentation project cost estimates for the ISP, consistent with its transmission cost forecasting approach. Details are available in the 2023 Transmisson Expansion Options Report.
The worksheet has Progressive and Step Change/Green Energy Export cost forecast. These cost escalations are year on year cost esclations.
Step Change/ Green Energy Scenario
Connection Costs for Wind and Solar
REZ names | Region | REZ network voltage (kV) | Connection capacity (MVA) | Feeder length (km) | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Far North Queensland | QLD | 275 | 300 | 5 | 35436406.88 | 35759696.3054 | 36569383.426 | 37331812.9454 | 37806797.9173 | 38024518.1676 | 38285581.8516 | 38550576.2697 | 38817739.7674 | 38930262.3889 | 38992825.1555 | 39056535.8628 | 39121394.5107 | 39187401.0993 | 39254268.6434 | 39322571.1134 | 39392021.524 | 39462619.8753 | 39534366.1673 | 39605251.5037 | 39676423.8254 | 39747596.147 | 39818481.4834 | 39889653.8051 | 39960826.1267 | 40031998.4483 | 40103170.7699 | 40174343.0916 | 40245515.4132 | 40316687.7348 | 40387860.0564 | 40459032.3781 | 40530204.7
North Queensland Clean Energy Hub | QLD | 275 | 300 | 10 | 48332528.62 | 48742135.432 | 49791885.6945 | 50850114.5721 | 51597695.0138 | 51936669.1737 | 52330195.4 | 52719574.9315 | 53105278.6563 | 53333852.165 | 53458937.9728 | 53586318.933 | 53715995.0457 | 53847966.3108 | 53981658.9402 | 54118220.5101 | 54257077.2325 | 54398229.1074 | 54541676.1347 | 54683401.7976 | 54825701.2487 | 54968000.6997 | 55109726.3627 | 55252025.8137 | 55394325.2648 | 55536624.7158 | 55678924.1669 | 55821223.6179 | 55963523.069 | 56105822.52 | 56248121.9711 | 56390421.4221 | 56532720.87
Northern Queensland | QLD | 275 | 300 | 5 | 35436406.88 | 35759696.3054 | 36569383.426 | 37331812.9454 | 37806797.9173 | 38024518.1676 | 38285581.8516 | 38550576.2697 | 38817739.7674 | 38930262.3889 | 38992825.1555 | 39056535.8628 | 39121394.5107 | 39187401.0993 | 39254268.6434 | 39322571.1134 | 39392021.524 | 39462619.8753 | 39534366.1673 | 39605251.5037 | 39676423.8254 | 39747596.147 | 39818481.4834 | 39889653.8051 | 39960826.1267 | 40031998.4483 | 40103170.7699 | 40174343.0916 | 40245515.4132 | 40316687.7348 | 40387860.0564 | 40459032.3781 | 40530204.7
Isaac | QLD | 275 | 300 | 5 | 33740128.77 | 34025420.5245 | 34774305.9122 | 35443103.5306 | 35818443.6251 | 36002956.5212 | 36229770.2181 | 36459609.0928 | 36690821.8782 | 36767364.5372 | 36797590.215 | 36828370.4924 | 36859705.3694 | 36891594.846 | 36923900.2723 | 36956898.9481 | 36990452.2235 | 37024560.0984 | 37059222.573 | 37093469.0979 | 37127854.2726 | 37162239.4474 | 37196485.9723 | 37230871.147 | 37265256.3218 | 37299641.4965 | 37334026.6713 | 37368411.8461 | 37402797.0208 | 37437182.1956 | 37471567.3704 | 37505952.5451 | 37540337.72
Barcaldine | QLD | 275 | 300 | 10 | 44964433.75 | 45298190.0154 | 46226779.2234 | 47098234.3529 | 47646928.9349 | 47919681.9196 | 48244925.2624 | 48564196.8686 | 48878191.9586 | 49030956.3739 | 49091443.0242 | 49153039.5212 | 49215745.865 | 49279562.0556 | 49344210.6313 | 49410246.5155 | 49477392.2465 | 49545647.8242 | 49615013.2488 | 49683546.2883 | 49752356.7894 | 49821167.2906 | 49889700.3301 | 49958510.8313 | 50027321.3324 | 50096131.8336 | 50164942.3348 | 50233752.836 | 50302563.3371 | 50371373.8383 | 50440184.3395 | 50508994.8406 | 50577805.34
Fitzroy | QLD | 275 | 300 | 5 | 33740128.77 | 34025420.5245 | 34774305.9122 | 35443103.5306 | 35818443.6251 | 36002956.5212 | 36229770.2181 | 36459609.0928 | 36690821.8782 | 36767364.5372 | 36797590.215 | 36828370.4924 | 36859705.3694 | 36891594.846 | 36923900.2723 | 36956898.9481 | 36990452.2235 | 37024560.0984 | 37059222.573 | 37093469.0979 | 37127854.2726 | 37162239.4474 | 37196485.9723 | 37230871.147 | 37265256.3218 | 37299641.4965 | 37334026.6713 | 37368411.8461 | 37402797.0208 | 37437182.1956 | 37471567.3704 | 37505952.5451 | 37540337.72
Wide Bay | QLD | 275 | 300 | 5 | 33740128.77 | 34025420.5245 | 34774305.9122 | 35443103.5306 | 35818443.6251 | 36002956.5212 | 36229770.2181 | 36459609.0928 | 36690821.8782 | 36767364.5372 | 36797590.215 | 36828370.4924 | 36859705.3694 | 36891594.846 | 36923900.2723 | 36956898.9481 | 36990452.2235 | 37024560.0984 | 37059222.573 | 37093469.0979 | 37127854.2726 | 37162239.4474 | 37196485.9723 | 37230871.147 | 37265256.3218 | 37299641.4965 | 37334026.6713 | 37368411.8461 | 37402797.0208 | 37437182.1956 | 37471567.3704 | 37505952.5451 | 37540337.72
Darling Downs | QLD | 275 | 300 | 5 | 35300491.06 | 35620737.1466 | 36425553.7115 | 37180484.0961 | 37647489.2651 | 37862550.032 | 38120870.6274 | 38383049.4284 | 38647333.6521 | 38756990.4085 | 38816963.786 | 38878037.5925 | 38940211.8279 | 39003486.4922 | 39067586.4782 | 39133062.0005 | 39199637.9516 | 39267314.3318 | 39336091.1408 | 39404042.6282 | 39472269.2228 | 39540495.8174 | 39608447.3047 | 39676673.8993 | 39744900.4939 | 39813127.0885 | 39881353.6831 | 39949580.2777 | 40017806.8722 | 40086033.4668 | 40154260.0614 | 40222486.656 | 40290713.25
Banana | QLD | 275 | 1800 | 100 | 413993266.52 | 415972385.1915 | 422971745.2715 | 429884999.933 | 434869020.1538 | 437590853.1976 | 440747563.3817 | 443659668.6638 | 446380568.4772 | 447813534.412 | 448418293.0251 | 449034148.1266 | 449661099.7164 | 450299147.7945 | 450945518.2389 | 451605759.2936 | 452277096.8366 | 452959530.868 | 453653061.3877 | 454338269.5411 | 455026251.8167 | 455714234.0922 | 456399442.2456 | 457087424.5212 | 457775406.7967 | 458463389.0722 | 459151371.3478 | 459839353.6233 | 460527335.8988 | 461215318.1743 | 461903300.4499 | 462591282.7254 | 463279265
North West New South Wales | NSW | 330 | 400 | 10 | 53975030.78 | 54372620.4312 | 55489852.1438 | 56568966.643 | 57287183.6883 | 57632082.33 | 58039503.7983 | 56979711.5349 | 57362651.0228 | 57724554.8134 | 57821842.1876 | 57920914.6513 | 58021772.2043 | 58124414.8469 | 58228396.3064 | 58334609.1278 | 58442607.0386 | 58552390.0389 | 58663958.1286 | 58774187.4012 | 58884862.9461 | 58995538.4911 | 59105767.7637 | 59216443.3087 | 59327118.8536 | 59437794.3986 | 59548469.9436 | 59659145.4885 | 59769821.0335 | 59880496.5784 | 59991172.1234 | 60101847.6684 | 60212523.21
New England | NSW | 330 | 400 | 10 | 53975030.78 | 54372620.4312 | 55489852.1438 | 56568966.643 | 57287183.6883 | 57632082.33 | 58039503.7983 | 56979711.5349 | 57362651.0228 | 57724554.8134 | 57821842.1876 | 57920914.6513 | 58021772.2043 | 58124414.8469 | 58228396.3064 | 58334609.1278 | 58442607.0386 | 58552390.0389 | 58663958.1286 | 58774187.4012 | 58884862.9461 | 58995538.4911 | 59105767.7637 | 59216443.3087 | 59327118.8536 | 59437794.3986 | 59548469.9436 | 59659145.4885 | 59769821.0335 | 59880496.5784 | 59991172.1234 | 60101847.6684 | 60212523.21
Central-West Orana | NSW | 330 | 400 | 10 | 53975030.78 | 54372620.4312 | 55489852.1438 | 56568966.643 | 57287183.6883 | 57632082.33 | 58039503.7983 | 56979711.5349 | 57362651.0228 | 57724554.8134 | 57821842.1876 | 57920914.6513 | 58021772.2043 | 58124414.8469 | 58228396.3064 | 58334609.1278 | 58442607.0386 | 58552390.0389 | 58663958.1286 | 58774187.4012 | 58884862.9461 | 58995538.4911 | 59105767.7637 | 59216443.3087 | 59327118.8536 | 59437794.3986 | 59548469.9436 | 59659145.4885 | 59769821.0335 | 59880496.5784 | 59991172.1234 | 60101847.6684 | 60212523.21
Broken Hill | NSW | 220 | 250 | 10 | 43752178.64 | 44076329.5106 | 44919472.4124 | 45684543.255 | 46117196.392 | 46354460.9433 | 46639560.3384 | 46918565.6745 | 47192573.4857 | 47486297.167 | 47507331.725 | 47528752.2382 | 47550558.7065 | 47572751.1301 | 47595233.02 | 47618197.354 | 47641547.6431 | 47665283.8874 | 47689406.0869 | 47713238.82 | 47737168.0419 | 47761097.2639 | 47784929.997 | 47808859.2189 | 47832788.4408 | 47856717.6627 | 47880646.8846 | 47904576.1065 | 47928505.3284 | 47952434.5504 | 47976363.7723 | 48000292.9942 | 48024222.22
South West New South Wales | NSW | 330 | 400 | 10 | 54480227.02 | 54889611.6222 | 56025436.6939 | 57133535.0736 | 57882829.9505 | 58238022.8767 | 57192045.6022 | 57592590.8016 | 57986409.6986 | 58364858.7581 | 58472308.5584 | 58581729.9148 | 58693122.8271 | 58806487.2954 | 58921330.4307 | 59038638.0109 | 59157917.1471 | 59279167.8392 | 59402390.0874 | 59524133.6685 | 59646370.1387 | 59768606.6089 | 59890350.19 | 60012586.6602 | 60134823.1303 | 60257059.6005 | 60379296.0706 | 60501532.5408 | 60623769.0109 | 60746005.4811 | 60868241.9512 | 60990478.4214 | 61112714.89
Wagga Wagga | NSW | 330 | 400 | 10 | 54480227.02 | 54889611.6222 | 56025436.6939 | 57133535.0736 | 57882829.9505 | 58238022.8767 | 57192045.6022 | 57592590.8016 | 57986409.6986 | 58364858.7581 | 58472308.5584 | 58581729.9148 | 58693122.8271 | 58806487.2954 | 58921330.4307 | 59038638.0109 | 59157917.1471 | 59279167.8392 | 59402390.0874 | 59524133.6685 | 59646370.1387 | 59768606.6089 | 59890350.19 | 60012586.6602 | 60134823.1303 | 60257059.6005 | 60379296.0706 | 60501532.5408 | 60623769.0109 | 60746005.4811 | 60868241.9512 | 60990478.4214 | 61112714.89
Tumut | NSW | 330 | 400 | 5 | 39610964.56 | 39950571.1499 | 40845370.5799 | 41680377.3374 | 42196810.2779 | 42435812.1307 | 42724125.2897 | 43015418.5883 | 43307934.801 | 43566596.4076 | 43631974.3539 | 43698551.8956 | 43766329.0327 | 43835305.765 | 43905182.1939 | 43976558.117 | 44049133.6354 | 44122908.7492 | 44197883.4583 | 44271958.4709 | 44346333.3824 | 44420708.2938 | 44494783.3064 | 44569158.2178 | 44643533.1293 | 44717908.0407 | 44792282.9521 | 44866657.8636 | 44941032.775 | 45015407.6865 | 45089782.5979 | 45164157.5093 | 45238532.42
Cooma-Monaro | NSW | 330 | 400 | 5 | 39610964.56 | 39950571.1499 | 40845370.5799 | 41680377.3374 | 42196810.2779 | 42435812.1307 | 42724125.2897 | 43015418.5883 | 43307934.801 | 43566596.4076 | 43631974.3539 | 43698551.8956 | 43766329.0327 | 43835305.765 | 43905182.1939 | 43976558.117 | 44049133.6354 | 44122908.7492 | 44197883.4583 | 44271958.4709 | 44346333.3824 | 44420708.2938 | 44494783.3064 | 44569158.2178 | 44643533.1293 | 44717908.0407 | 44792282.9521 | 44866657.8636 | 44941032.775 | 45015407.6865 | 45089782.5979 | 45164157.5093 | 45238532.42
Hunter-Central Coast | NSW | 330 | 400 | 10 | 39610964.56 | 39950571.1499 | 40845370.5799 | 41680377.3374 | 42196810.2779 | 42435812.1307 | 42724125.2897 | 43015418.5883 | 43307934.801 | 43566596.4076 | 43631974.3539 | 43698551.8956 | 43766329.0327 | 43835305.765 | 43905182.1939 | 43976558.117 | 44049133.6354 | 44122908.7492 | 44197883.4583 | 44271958.4709 | 44346333.3824 | 44420708.2938 | 44494783.3064 | 44569158.2178 | 44643533.1293 | 44717908.0407 | 44792282.9521 | 44866657.8636 | 44941032.775 | 45015407.6865 | 45089782.5979 | 45164157.5093 | 45238532.42
Hunter Coast | NSW | Note 1
Illawarra Coast | NSW
Illawarra | NSW | 330 | 400 | 5 | 39610964.56 | 39950571.1499 | 40845370.5799 | 41680377.3374 | 42196810.2779 | 42435812.1307 | 42724125.2897 | 43015418.5883 | 43307934.801 | 43566596.4076 | 43631974.3539 | 43698551.8956 | 43766329.0327 | 43835305.765 | 43905182.1939 | 43976558.117 | 44049133.6354 | 44122908.7492 | 44197883.4583 | 44271958.4709 | 44346333.3824 | 44420708.2938 | 44494783.3064 | 44569158.2178 | 44643533.1293 | 44717908.0407 | 44792282.9521 | 44866657.8636 | 44941032.775 | 45015407.6865 | 45089782.5979 | 45164157.5093 | 45238532.42
Ovens Murray | VIC | 220 | 250 | 5 | 34130501.23 | 34459987.1801 | 35214634.8084 | 35933051.3573 | 36375172.3474 | 36582495.9569 | 36828555.4381 | 37078581.9911 | 37331192.4653 | 37462369.9219 | 37516690.3984 | 37572007.581 | 37628321.4695 | 37685632.064 | 37743690.188 | 37802994.1945 | 37863294.907 | 37924592.3255 | 37986886.4499 | 38048433.0449 | 38110228.8164 | 38172024.5879 | 38233571.1829 | 38295366.9543 | 38357162.7258 | 38418958.4973 | 38480754.2688 | 38542550.0402 | 38604345.8117 | 38666141.5832 | 38727937.3547 | 38789733.1261 | 38851528.9
Murray River | VIC | 220 | 250 | 5 | 32771847.97 | 33070749.3628 | 33776507.0928 | 34419485.3571 | 34781204.81 | 34961758.058 | 35180216.7426 | 35401912.0107 | 35625549.6185 | 35725586.9557 | 35753781.5571 | 35782493.4907 | 35811722.7564 | 35841469.3543 | 35871603.9512 | 35902385.2134 | 35933683.8076 | 35965499.734 | 35997832.9926 | 36029778.252 | 36061852.8445 | 36093927.4369 | 36125872.6964 | 36157947.2888 | 36190021.8813 | 36222096.4738 | 36254171.0662 | 36286245.6587 | 36318320.2512 | 36350394.8436 | 36382469.4361 | 36414544.0286 | 36446618.62
Western Victoria | VIC | 220 | 250 | 5 | 35489154.48 | 35849191.1612 | 36652692.1557 | 37446456.2333 | 37968857.0771 | 38202915.1694 | 38476540.9472 | 38754863.1859 | 39036409.8628 | 39198241.8291 | 39278641.7495 | 39360516.8978 | 39443867.274 | 39528692.8781 | 39614624.9032 | 39702400.9631 | 39791652.2509 | 39882378.7666 | 39974580.5102 | 40065675.8329 | 40157139.9625 | 40248604.0922 | 40339699.4149 | 40431163.5445 | 40522627.6742 | 40614091.8038 | 40705555.9335 | 40797020.0631 | 40888484.1928 | 40979948.3224 | 41071412.4521 | 41162876.5817 | 41254340.71
South West Victoria | VIC | 500 | 600 | 10 | 84212105.58 | 84642020.3236 | 86355520.4954 | 88053881.3045 | 89145011.5845 | 89603857.427 | 90186798.7044 | 90774577.2398 | 91367270.3513 | 91664982.8837 | 91825194.389 | 91988345.555 | 92154436.3817 | 92323466.869 | 92494702.1017 | 92669611.9103 | 92847461.3796 | 93028250.5095 | 93211979.3 | 93393503.3451 | 93575762.3053 | 93758021.2655 | 93939545.3105 | 94121804.2708 | 94304063.231 | 94486322.1912 | 94668581.1514 | 94850840.1116 | 95033099.0718 | 95215358.032 | 95397616.9923 | 95579875.9525 | 95762134.91
Gippsland | VIC | 220 | 250 | 10 | 48730088.25 | 49197728.3709 | 50257790.794 | 51377745.4667 | 52203011.8868 | 52567402.498 | 52982040.898 | 53394572.1988 | 53805588.1762 | 54129240.8253 | 54282404.0959 | 54438377.7017 | 54597161.6428 | 54758755.9191 | 54922457.9468 | 55089672.8936 | 55259698.1756 | 55432533.7928 | 55608179.7453 | 55781717.9464 | 55955958.7313 | 56130199.5162 | 56303737.7172 | 56477978.5021 | 56652219.287 | 56826460.0718 | 57000700.8567 | 57174941.6416 | 57349182.4265 | 57523423.2113 | 57697663.9962 | 57871904.7811 | 58046145.57
Central North Victoria | VIC | 220 | 250 | 10 | 46448767.23 | 46864747.0171 | 47842364.2537 | 48835001.3968 | 49524509.0949 | 49843745.2666 | 50211838.6365 | 50576575.4069 | 50938701.5739 | 51206810.1809 | 51315819.493 | 51426828.9761 | 51539838.63 | 51654848.4548 | 51771358.4077 | 51890368.5742 | 52011378.9116 | 52134389.4199 | 52259400.099 | 52382910.6499 | 52506921.2436 | 52630931.8373 | 52754442.3883 | 52878452.9819 | 53002463.5756 | 53126474.1693 | 53250484.763 | 53374495.3566 | 53498505.9503 | 53622516.544 | 53746527.1377 | 53870537.7314 | 53994548.33
Gippsland Coast | VIC | 220 | 2000 | 16 | 683642065.32 | 687274431.7386 | 699091025.4306 | 711959377.7071 | 720980072.358 | 723153503.8392 | 724445291.7968 | 725771149.1034 | 727126887.2944 | 728510001.4694 | 729918701.6957 | 731353249.6325 | 732813645.2799 | 734299888.6379 | 735805517.7789 | 737343456.558 | 738907243.0477 | 740496877.248 | 742112359.1588 | 743708455.2868 | 745311013.3423 | 746913571.3979 | 748509667.5258 | 750112225.5814 | 751714783.637 | 753317341.6925 | 754919899.7481 | 756522457.8037 | 758125015.8593 | 759727573.9148 | 761330131.9704 | 762932690.026 | 764535248.0815
Southern Ocean | VIC | Note 1
South East South Australia | SA | 275 | 300 | 10 | 45188973.41 | 45527791.61 | 46464463.53 | 47348382.75 | 47910352.63 | 48187525.07 | 48517325.12 | 48841275.35 | 49160055.98 | 49317940.58 | 49382740.02 | 49448728.44 | 49515905.85 | 49584272.23 | 49653530.35 | 49724274.7 | 49796208.03 | 49869330.33 | 49943641.62 | 50017061.18 | 50090777.97 | 50164494.77 | 50237914.32 | 50311631.12 | 50385347.92 | 50459064.72 | 50532781.52 | 50606498.31 | 50680215.11 | 50753931.91 | 50827648.71 | 50901365.5 | 50975082.3
Riverland | SA | 275 | 300 | 10 | 49870060.3 | 50314242.25 | 51419251.08 | 52562621.16 | 53400835.88 | 53769994.41 | 54194648.03 | 54615985.81 | 55034376.53 | 55296918.09 | 55451433.61 | 55608784.28 | 55768970.1 | 55931991.07 | 56097138.39 | 56265829.65 | 56437356.06 | 56611717.61 | 56788914.31 | 56963984.65 | 57139763.78 | 57315542.91 | 57490613.25 | 57666392.38 | 57842171.5 | 58017950.63 | 58193729.76 | 58369508.89 | 58545288.01 | 58721067.14 | 58896846.27 | 59072625.4 | 59248404.53
Mid-North South Australia | SA | 275 | 300 | 5 | 36228003.33 | 36569013.55 | 37407063.61 | 38213158.96 | 38734605.77 | 38967811.21 | 39244847.16 | 39526236.06 | 39810164.79 | 39939323.82 | 40016962.31 | 40096025.36 | 40176512.96 | 40258425.13 | 40341405.72 | 40426167 | 40512352.85 | 40599963.25 | 40688998.22 | 40776964.76 | 40865287.45 | 40953610.13 | 41041576.68 | 41129899.36 | 41218222.05 | 41306544.73 | 41394867.42 | 41483190.1 | 41571512.78 | 41659835.47 | 41748158.15 | 41836480.84 | 41924803.52
Yorke Peninsula | SA | 275 | 300 | 5 | 36228003.33 | 36569013.55 | 37407063.61 | 38213158.96 | 38734605.77 | 38967811.21 | 39244847.16 | 39526236.06 | 39810164.79 | 39939323.82 | 40016962.31 | 40096025.36 | 40176512.96 | 40258425.13 | 40341405.72 | 40426167 | 40512352.85 | 40599963.25 | 40688998.22 | 40776964.76 | 40865287.45 | 40953610.13 | 41041576.68 | 41129899.36 | 41218222.05 | 41306544.73 | 41394867.42 | 41483190.1 | 41571512.78 | 41659835.47 | 41748158.15 | 41836480.84 | 41924803.52
Northern South Australia | SA | 275 | 300 | 5 | 34305554.81 | 34603516.38 | 35372672.87 | 36072691.08 | 36481259.56 | 36676845.55 | 36915079.7 | 37156641.01 | 37399841.41 | 37488430.35 | 37529440.18 | 37571202.48 | 37613717.26 | 37656984.51 | 37700816.11 | 37745588.31 | 37791112.98 | 37837390.12 | 37884419.74 | 37930885 | 37977538.38 | 38024191.76 | 38070657.03 | 38117310.41 | 38163963.79 | 38210617.17 | 38257270.55 | 38303923.93 | 38350577.31 | 38397230.69 | 38443884.08 | 38490537.46 | 38537190.84
Leigh Creek | SA | 275 | 300 | 10 | 46087132.04 | 46446190.14 | 47415184.96 | 48348941.78 | 48963988.48 | 49258831.69 | 49606851.81 | 49949509.38 | 50287424.71 | 50465690.6 | 50547731.94 | 50631278.63 | 50716330.66 | 50802888.04 | 50890574.43 | 50980142.5 | 51071215.92 | 51163794.68 | 51257878.79 | 51350833.89 | 51444165.33 | 51537496.76 | 51630451.86 | 51723783.3 | 51817114.73 | 51910446.17 | 52003777.61 | 52097109.04 | 52190440.48 | 52283771.91 | 52377103.35 | 52470434.78 | 52563766.22
Roxby Downs | SA | 275 | 300 | 10 | 43841735.47 | 44150169.66 | 45038332.71 | 45847437.78 | 46329717.43 | 46580361.97 | 46882811.04 | 47178678.32 | 47468733.98 | 47595740.31 | 47634648.35 | 47674270.31 | 47714606.17 | 47755655.95 | 47797241.15 | 47839718.75 | 47882910.25 | 47926815.66 | 47971434.98 | 48015518.87 | 48059781.23 | 48104043.6 | 48148127.48 | 48192389.85 | 48236652.21 | 48280914.58 | 48325176.94 | 48369439.31 | 48413701.67 | 48457964.04 | 48502226.4 | 48546488.77 | 48590751.13
Eastern Eyre Peninsula | SA | 275 | 300 | 10 | 43841735.47 | 44150169.66 | 45038332.71 | 45847437.78 | 46329717.43 | 46580361.97 | 46882811.04 | 47178678.32 | 47468733.98 | 47595740.31 | 47634648.35 | 47674270.31 | 47714606.17 | 47755655.95 | 47797241.15 | 47839718.75 | 47882910.25 | 47926815.66 | 47971434.98 | 48015518.87 | 48059781.23 | 48104043.6 | 48148127.48 | 48192389.85 | 48236652.21 | 48280914.58 | 48325176.94 | 48369439.31 | 48413701.67 | 48457964.04 | 48502226.4 | 48546488.77 | 48590751.13
Western Eyre Peninsula | SA | 275 | 300 | 10 | 43841735.47 | 44150169.66 | 45038332.71 | 45847437.78 | 46329717.43 | 46580361.97 | 46882811.04 | 47178678.32 | 47468733.98 | 47595740.31 | 47634648.35 | 47674270.31 | 47714606.17 | 47755655.95 | 47797241.15 | 47839718.75 | 47882910.25 | 47926815.66 | 47971434.98 | 48015518.87 | 48059781.23 | 48104043.6 | 48148127.48 | 48192389.85 | 48236652.21 | 48280914.58 | 48325176.94 | 48369439.31 | 48413701.67 | 48457964.04 | 48502226.4 | 48546488.77 | 48590751.13
South East South Australia Coast | SA | 275 | 1200 | 50 | 893932195.16 | 891599865.03 | 863363084.47 | 852507472.34 | 859524040.83 | 870463527.67 | 879973622.55 | 885397853.12 | 887987929.45 | 887988332.6 | 887988792.31 | 887989260.46 | 887989737.04 | 887990222.05 | 887990713.39 | 887991215.27 | 887991725.59 | 887992244.35 | 887992771.54 | 887993292.4 | 887993815.37 | 887994338.34 | 887994859.2 | 887995382.18 | 887995905.15 | 887996428.12 | 887996951.09 | 887997474.06 | 887997997.03 | 887998520.01 | 887999042.98 | 887999565.95 | 888000088.92
North East Tasmania | TAS | 220 | 150 | 5 | 41401222.03 | 41736183.11 | 42851281.26 | 43817129.15 | 44380568.7 | 44615857.77 | 44918039.27 | 45233025.66 | 45554948.94 | 45678461.97 | 45753984.76 | 45830893.29 | 45909187.56 | 45988867.56 | 46069586.87 | 46152038.36 | 46235875.58 | 46321098.54 | 46407707.25 | 46493276.64 | 46579192.48 | 46665108.31 | 46750677.71 | 46836593.54 | 46922509.37 | 47008425.2 | 47094341.04 | 47180256.87 | 47266172.7 | 47352088.53 | 47438004.37 | 47523920.2 | 47609836.03
North West Tasmania | TAS | 220 | 150 | 5 | 36367282.18 | 36752075.42 | 37593173.16 | 38448818.12 | 39039977.26 | 39296407.63 | 39592819.54 | 39894553.04 | 40200067.84 | 40353643.05 | 40457160.3 | 40562576.95 | 40669893 | 40779108.46 | 40889748.46 | 41002762.71 | 41117676.35 | 41234489.4 | 41353201.85 | 41470489.75 | 41588252.49 | 41706015.24 | 41823303.14 | 41941065.88 | 42058828.63 | 42176591.38 | 42294354.13 | 42412116.87 | 42529879.62 | 42647642.37 | 42765405.12 | 42883167.86 | 43000930.61
Central Highlands | TAS | 220 | 150 | 5 | 33440952.1 | 33760299.89 | 34496559.96 | 35190872.46 | 35610400.02 | 35809625.64 | 36047026.79 | 36288190.21 | 36531766.3 | 36624334.29 | 36672168.21 | 36720879.81 | 36770469.1 | 36820936.07 | 36872061.31 | 36924283.66 | 36977383.7 | 37031361.42 | 37086216.83 | 37140413.97 | 37194830.54 | 37249247.1 | 37303444.25 | 37357860.81 | 37412277.38 | 37466693.94 | 37521110.51 | 37575527.07 | 37629943.64 | 37684360.2 | 37738776.77 | 37793193.33 | 37847609.9
North Tasmania Coast | TAS | Note 1
North-East Tasmania Coast | TAS
Notes:
1. The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report.
2. The connection costs for all REZs was reviewed and consulted on through the 2023 Transmission Expansion Options Report.
3. Where no costs are shown, these have been allocated to REZ expansion costs instead.
System strength services cost options | bar: 2028-29 to 2049-50
Description |  |  |  |  | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
80 MVA synchronous condenser |  |  |  |  | 71110178.14 | 70562025.8936 | 71191930.8478 | 71957603.1723 | 72366158.2102 | 72477364.4324 | 72735403.2327 | 72985614.6934 | 73242549.8779 | 73244232.7778 | 73244478.1197 | 73244727.9633 | 73244982.3086 | 73245241.1556 | 73245503.3788 | 73245771.2292 | 73246043.5812 | 73246320.4349 | 73246601.7903 | 73246879.7695 | 73247158.874 | 73247437.9786 | 73247715.9577 | 73247995.0623 | 73248274.1669 | 73248553.2714 | 73248832.376 | 73249111.4806 | 73249390.5851 | 73249669.6897 | 73249948.7942 | 73250227.8988 | 73250507.0034
125 MVA synchronous condenser |  |  |  |  | 95716613.18 | 94935548.9477 | 95778235.8184 | 96804182.4267 | 97350452.1276 | 97493797.9261 | 97838239.9972 | 98171491.3298 | 98513526.6926 | 98515172.4662 | 98515417.7655 | 98515667.5657 | 98515921.8668 | 98516180.6688 | 98516442.8464 | 98516710.6502 | 98516982.9549 | 98517259.7605 | 98517541.067 | 98517818.9978 | 98518098.0539 | 98518377.1099 | 98518655.0407 | 98518934.0968 | 98519213.1528 | 98519492.2089 | 98519771.2649 | 98520050.321 | 98520329.377 | 98520608.4331 | 98520887.4891 | 98521166.5452 | 98521445.6012
200 MVA synchronous condenser |  |  |  |  | 131824581.075 | $ 132 M | 131670296.8734 | 133049199.0475 | 133779862.9414 | 133940206.5024 | 134395731.9665 | 134833004.3787 | 135281718.0662 | 135282468.7016 | 135282591.312 | 135282716.1722 | 135282843.282 | 135282972.6416 | 135283103.6885 | 135283237.5476 | 135283373.6564 | 135283512.0149 | 135283652.6232 | 135283791.5442 | 135283931.0276 | 135284070.511 | 135284209.4319 | 135284348.9153 | 135284488.3987 | 135284627.8821 | 135284767.3655 | 135284906.8489 | 135285046.3323 | 135285185.8157 | 135285325.2991 | 135285464.7825 | 135285604.2659
250 MVA synchronous condenser |  |  |  |  | 181879920.55 | 181879920.55 | 181867033.525 | 183803998.2025 | 184832201.6506 | 185087564.5916 | 185734326.4566 | 186358065.7887 | 186997781.5319 | 186999374.8996 | 186999620.1405 | 186999869.8813 | 187000124.1218 | 187000382.8623 | 187000644.9775 | 187000912.7176 | 187001184.9575 | 187001461.6973 | 187001742.9369 | 187002020.8016 | 187002299.7912 | 187002578.7809 | 187002856.6456 | 187003135.6352 | 187003414.6249 | 187003693.6146 | 187003972.6042 | 187004251.5939 | 187004530.5835 | 187004809.5732 | 187005088.5629 | 187005367.5525 | 187005646.5422
Non-REZ connection costs
Non-REZ name | Region | Network voltage (kV) | Connection capacity (MVA) | Feeder length (km) | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
New South Wales Non-REZ | NSW | 500 | 600 | 20 | 148000000 | 148000000 | 151168480.8432 | 154336961.6863 | 156449282.2485 | 157505442.5295 | 158561602.8106 | 159617763.0916 | 160673923.3727 | 161769660.0089 | 162160728.7037 | 162558972.971 | 162964392.8106 | 163376988.2226 | 163794965.3139 | 164221911.8707 | 164656033.9999 | 165097331.7014 | 165545804.9754 | 165988896.57 | 166433782.0577 | 166878667.5455 | 167321759.1401 | 167766644.6278 | 168211530.1156 | 168656415.6033 | 169101301.0911 | 169546186.5788 | 169991072.0665 | 170435957.5543 | 170880843.042 | 171325728.5297 | 171770614.0175
Victoria Non-REZ | VIC | 500 | 600 | 20 | 134000000 | 135024600.6149 | 138098402.4595 | 141172204.3042 | 143221405.534 | 144246006.1489 | 145270606.7637 | 146295207.3786 | 148344408.6084 | 149151682.7119 | 149614481.7767 | 150085772.5675 | 150565555.0842 | 151053829.3269 | 151548472.3641 | 152053730.0587 | 152567479.4793 | 153089720.6259 | 153620453.4984 | 154144817.5764 | 154671304.5859 | 155197791.5955 | 155722155.6735 | 156248642.683 | 156775129.6925 | 157301616.7021 | 157828103.7116 | 158354590.7211 | 158881077.7306 | 159407564.7402 | 159934051.7497 | 160460538.7592 | 160987025.7687
Notes:
1. A land use limit of 5% for onshore wind and 1% for solar is applied for all scenarios.
2. Where no costs are shown, these have been allocated to REZ expansion costs instead
Progressive Change Scenario
Connection Costs for Wind and Solar
REZ names | Region | REZ network voltage (kV) | Connection capacity (MVA) | Feeder length (km) | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Far North Queensland | QLD | 275 | 300 | 5 | 35436406.88 | 35759696.3054 | 36569383.426 | 37331812.9454 | 37806797.9173 | 37898196.725 | 37955567.2327 | 38014450.8032 | 38074661.4337 | 38136087.8643 | 38198650.6308 | 38262361.3381 | 38327219.986 | 38393226.5746 | 38460094.1188 | 38528396.5887 | 38597846.9993 | 38668445.3506 | 38740191.6426 | 38811076.979 | 38882249.3007 | 38953421.6223 | 39024306.9587 | 39095479.2804 | 39166651.602 | 39237823.9236 | 39308996.2453 | 39380168.5669 | 39451340.8885 | 39522513.2101 | 39593685.5318 | 39664857.8534 | 39736030.175
North Queensland Clean Energy Hub | QLD | 275 | 300 | 10 | 48332528.62 | 48742135.432 | 49791885.6945 | 50850114.5721 | 51597695.0138 | 51781171.1625 | 51895875.7276 | 52013605.4947 | 52133988.5214 | 52256802.4157 | 52381888.2235 | 52509269.1837 | 52638945.2963 | 52770916.5614 | 52904609.1909 | 53041170.7608 | 53180027.4832 | 53321179.3581 | 53464626.3853 | 53606352.0483 | 53748651.4993 | 53890950.9504 | 54032676.6133 | 54174976.0644 | 54317275.5154 | 54459574.9665 | 54601874.4175 | 54744173.8686 | 54886473.3196 | 55028772.7707 | 55171072.2217 | 55313371.6728 | 55455671.1239
Northern Queensland | QLD | 275 | 300 | 5 | 35436406.88 | 35759696.3054 | 36569383.426 | 37331812.9454 | 37806797.9173 | 37898196.725 | 37955567.2327 | 38014450.8032 | 38074661.4337 | 38136087.8643 | 38198650.6308 | 38262361.3381 | 38327219.986 | 38393226.5746 | 38460094.1188 | 38528396.5887 | 38597846.9993 | 38668445.3506 | 38740191.6426 | 38811076.979 | 38882249.3007 | 38953421.6223 | 39024306.9587 | 39095479.2804 | 39166651.602 | 39237823.9236 | 39308996.2453 | 39380168.5669 | 39451340.8885 | 39522513.2101 | 39593685.5318 | 39664857.8534 | 39736030.175
Isaac | QLD | 275 | 300 | 5 | 33740128.77 | 34025420.5245 | 34774305.9122 | 35443103.5306 | 35818443.6251 | 35878305.3282 | 35906022.4925 | 35934470.6563 | 35963559.9568 | 35993236.6415 | 36023462.3193 | 36054242.5968 | 36085577.4738 | 36117466.9504 | 36149772.3767 | 36182771.0524 | 36216324.3278 | 36250432.2028 | 36285094.6773 | 36319341.2022 | 36353726.377 | 36388111.5517 | 36422358.0766 | 36456743.2514 | 36491128.4261 | 36525513.6009 | 36559898.7757 | 36594283.9504 | 36628669.1252 | 36663054.3 | 36697439.4747 | 36731824.6495 | 36766209.8243
Barcaldine | QLD | 275 | 300 | 10 | 44964433.75 | 45298190.0154 | 46226779.2234 | 47098234.3529 | 47646928.9349 | 47764664.0824 | 47820130.7658 | 47877060.3198 | 47935272.8873 | 47994660.9282 | 48055147.5784 | 48116744.0754 | 48179450.4192 | 48243266.6098 | 48307915.1855 | 48373951.0697 | 48441096.8007 | 48509352.3785 | 48578717.8031 | 48647250.8425 | 48716061.3437 | 48784871.8449 | 48853404.8843 | 48922215.3855 | 48991025.8867 | 49059836.3879 | 49128646.889 | 49197457.3902 | 49266267.8914 | 49335078.3925 | 49403888.8937 | 49472699.3949 | 49541509.8961
Fitzroy | QLD | 275 | 300 | 5 | 33740128.77 | 34025420.5245 | 34774305.9122 | 35443103.5306 | 35818443.6251 | 35878305.3282 | 35906022.4925 | 35934470.6563 | 35963559.9568 | 35993236.6415 | 36023462.3193 | 36054242.5968 | 36085577.4738 | 36117466.9504 | 36149772.3767 | 36182771.0524 | 36216324.3278 | 36250432.2028 | 36285094.6773 | 36319341.2022 | 36353726.377 | 36388111.5517 | 36422358.0766 | 36456743.2514 | 36491128.4261 | 36525513.6009 | 36559898.7757 | 36594283.9504 | 36628669.1252 | 36663054.3 | 36697439.4747 | 36731824.6495 | 36766209.8243
Wide Bay | QLD | 275 | 300 | 5 | 33740128.77 | 34025420.5245 | 34774305.9122 | 35443103.5306 | 35818443.6251 | 35878305.3282 | 35906022.4925 | 35934470.6563 | 35963559.9568 | 35993236.6415 | 36023462.3193 | 36054242.5968 | 36085577.4738 | 36117466.9504 | 36149772.3767 | 36182771.0524 | 36216324.3278 | 36250432.2028 | 36285094.6773 | 36319341.2022 | 36353726.377 | 36388111.5517 | 36422358.0766 | 36456743.2514 | 36491128.4261 | 36525513.6009 | 36559898.7757 | 36594283.9504 | 36628669.1252 | 36663054.3 | 36697439.4747 | 36731824.6495 | 36766209.8243
Darling Downs | QLD | 275 | 300 | 5 | 35300491.06 | 35620737.1466 | 36425553.7115 | 37180484.0961 | 37647489.2651 | 37736372.8587 | 37791368.8789 | 37847815.3337 | 37905533.9259 | 37964418.0025 | 38024391.38 | 38085465.1865 | 38147639.4219 | 38210914.0862 | 38275014.0723 | 38340489.5945 | 38407065.5457 | 38474741.9258 | 38543518.7348 | 38611470.2222 | 38679696.8168 | 38747923.4114 | 38815874.8987 | 38884101.4933 | 38952328.0879 | 39020554.6825 | 39088781.2771 | 39157007.8717 | 39225234.4663 | 39293461.0609 | 39361687.6555 | 39429914.25 | 39498140.8446
Banana | QLD | 275 | 1800 | 100 | 413993266.52 | 415972385.1915 | 422971745.2715 | 429884999.933 | 434869020.1538 | 437590853.1976 | 440747563.3817 | 443659668.6638 | 446380568.4772 | 447813534.412 | 448418293.0251 | 449034148.1266 | 449661099.7164 | 450299147.7945 | 450945518.2389 | 451605759.2936 | 452277096.8366 | 452959530.868 | 453653061.3877 | 454338269.5411 | 455026251.8167 | 455714234.0922 | 456399442.2456 | 457087424.5212 | 457775406.7967 | 458463389.0722 | 459151371.3478 | 459839353.6233 | 460527335.8988 | 461215318.1743 | 461903300.4499 | 462591282.7254 | 463279265.0009
North West New South Wales | NSW | 330 | 400 | 10 | 53975030.78 | 54372620.4312 | 55489852.1438 | 56568966.643 | 57287183.6883 | 57634060.5224 | 57723273.7339 | 57814839.8274 | 57908469.547 | 58003989.8923 | 58101277.2665 | 58200349.7301 | 58301207.2832 | 58403849.9257 | 58507831.3853 | 58614044.2066 | 58722042.1174 | 58831825.1177 | 58943393.2074 | 59053622.48 | 59164298.0249 | 59274973.5699 | 59385202.8425 | 59495878.3875 | 59606553.9324 | 59717229.4774 | 59827905.0224 | 59938580.5673 | 60049256.1123 | 60159931.6573 | 60270607.2022 | 60381282.7472 | 60491958.2922
New England | NSW | 330 | 400 | 10 | 53975030.78 | 54372620.4312 | 55489852.1438 | 56568966.643 | 57287183.6883 | 57634060.5224 | 57723273.7339 | 57814839.8274 | 57908469.547 | 58003989.8923 | 58101277.2665 | 58200349.7301 | 58301207.2832 | 58403849.9257 | 58507831.3853 | 58614044.2066 | 58722042.1174 | 58831825.1177 | 58943393.2074 | 59053622.48 | 59164298.0249 | 59274973.5699 | 59385202.8425 | 59495878.3875 | 59606553.9324 | 59717229.4774 | 59827905.0224 | 59938580.5673 | 60049256.1123 | 60159931.6573 | 60270607.2022 | 60381282.7472 | 60491958.2922
Central-West Orana | NSW | 330 | 400 | 10 | 53975030.78 | 54372620.4312 | 55489852.1438 | 56568966.643 | 57287183.6883 | 57634060.5224 | 57723273.7339 | 57814839.8274 | 57908469.547 | 58003989.8923 | 58101277.2665 | 58200349.7301 | 58301207.2832 | 58403849.9257 | 58507831.3853 | 58614044.2066 | 58722042.1174 | 58831825.1177 | 58943393.2074 | 59053622.48 | 59164298.0249 | 59274973.5699 | 59385202.8425 | 59495878.3875 | 59606553.9324 | 59717229.4774 | 59827905.0224 | 59938580.5673 | 60049256.1123 | 60159931.6573 | 60270607.2022 | 60381282.7472 | 60491958.2922
Broken Hill | NSW | 220 | 250 | 10 | 43752178.64 | 44076329.5106 | 44919472.4124 | 45684543.255 | 46117196.392 | 46323599.2727 | 46342888.1089 | 46362685.6666 | 46382929.4001 | 46403581.9108 | 46424616.4688 | 46446036.9819 | 46467843.4503 | 46490035.8738 | 46512517.7638 | 46535482.0977 | 46558832.3868 | 46582568.6312 | 46606690.8307 | 46630523.5638 | 46654452.7857 | 46678382.0076 | 46702214.7407 | 46726143.9626 | 46750073.1845 | 46774002.4065 | 46797931.6284 | 46821860.8503 | 46845790.0722 | 46869719.2941 | 46893648.516 | 46917577.7379 | 46941506.9598
South West New South Wales | NSW | 330 | 400 | 10 | 54480227.02 | 54889611.6222 | 56025436.6939 | 57133535.0736 | 57882829.9505 | 58243173.0627 | 58341705.2911 | 58442836.1782 | 58546246.2534 | 58651744.4449 | 58759194.2453 | 58868615.6016 | 58980008.5139 | 59093372.9822 | 59208216.1175 | 59325523.6977 | 59444802.8339 | 59566053.5261 | 59689275.7742 | 59811019.3554 | 59933255.8255 | 60055492.2957 | 60177235.8768 | 60299472.347 | 60421708.8172 | 60543945.2873 | 60666181.7575 | 60788418.2276 | 60910654.6978 | 61032891.1679 | 61155127.6381 | 61277364.1082 | 61399600.5784
Wagga Wagga | NSW | 330 | 400 | 10 | 54480227.02 | 54889611.6222 | 56025436.6939 | 57133535.0736 | 57882829.9505 | 58243173.0627 | 58341705.2911 | 58442836.1782 | 58546246.2534 | 58651744.4449 | 58759194.2453 | 58868615.6016 | 58980008.5139 | 59093372.9822 | 59208216.1175 | 59325523.6977 | 59444802.8339 | 59566053.5261 | 59689275.7742 | 59811019.3554 | 59933255.8255 | 60055492.2957 | 60177235.8768 | 60299472.347 | 60421708.8172 | 60543945.2873 | 60666181.7575 | 60788418.2276 | 60910654.6978 | 61032891.1679 | 61155127.6381 | 61277364.1082 | 61399600.5784
Tumut | NSW | 330 | 400 | 5 | 39610964.56 | 39950571.1499 | 40845370.5799 | 41680377.3374 | 42196810.2779 | 42390913.2457 | 42450865.2958 | 42512398.4853 | 42575318.4681 | 42639508.9524 | 42704886.8987 | 42771464.4404 | 42839241.5774 | 42908218.3098 | 42978094.7387 | 43049470.6618 | 43122046.1802 | 43195821.294 | 43270796.0031 | 43344871.0157 | 43419245.9271 | 43493620.8386 | 43567695.8512 | 43642070.7626 | 43716445.674 | 43790820.5855 | 43865195.4969 | 43939570.4084 | 44013945.3198 | 44088320.2312 | 44162695.1427 | 44237070.0541 | 44311444.9656
Cooma-Monaro | NSW | 330 | 400 | 5 | 39610964.56 | 39950571.1499 | 40845370.5799 | 41680377.3374 | 42196810.2779 | 42390913.2457 | 42450865.2958 | 42512398.4853 | 42575318.4681 | 42639508.9524 | 42704886.8987 | 42771464.4404 | 42839241.5774 | 42908218.3098 | 42978094.7387 | 43049470.6618 | 43122046.1802 | 43195821.294 | 43270796.0031 | 43344871.0157 | 43419245.9271 | 43493620.8386 | 43567695.8512 | 43642070.7626 | 43716445.674 | 43790820.5855 | 43865195.4969 | 43939570.4084 | 44013945.3198 | 44088320.2312 | 44162695.1427 | 44237070.0541 | 44311444.9656
Hunter-Central Coast | NSW | 330 | 400 | 10 | 39610964.56 | 39950571.1499 | 40845370.5799 | 41680377.3374 | 42196810.2779 | 42390913.2457 | 42450865.2958 | 42512398.4853 | 42575318.4681 | 42639508.9524 | 42704886.8987 | 42771464.4404 | 42839241.5774 | 42908218.3098 | 42978094.7387 | 43049470.6618 | 43122046.1802 | 43195821.294 | 43270796.0031 | 43344871.0157 | 43419245.9271 | 43493620.8386 | 43567695.8512 | 43642070.7626 | 43716445.674 | 43790820.5855 | 43865195.4969 | 43939570.4084 | 44013945.3198 | 44088320.2312 | 44162695.1427 | 44237070.0541 | 44311444.9656
Hunter Coast | NSW | Note 1
Illawarra Coast | NSW
Illawarra | NSW | 330 | 400 | 5 | 45188973.41 | 45527791.6102 | 46464463.5305 | 47348382.7474 | 47910352.6281 | 48032516.5902 | 48091938.1352 | 48152926.8557 | 48215290.0705 | 48278912.5718 | 48343712.015 | 48409700.4389 | 48476877.8433 | 48545244.2284 | 48614502.3489 | 48685246.6952 | 48757180.0221 | 48830302.3296 | 48904613.6177 | 48978033.1703 | 49051749.9681 | 49125466.7659 | 49198886.3186 | 49272603.1164 | 49346319.9142 | 49420036.712 | 49493753.5098 | 49567470.3076 | 49641187.1054 | 49714903.9032 | 49788620.701 | 49862337.4988 | 49936054.2966
Ovens Murray | VIC | 220 | 250 | 5 | 34130501.23 | 34459987.1801 | 35214634.8084 | 35933051.3573 | 36375172.3474 | 36478021.6725 | 36527833.9271 | 36578959.9396 | 36631238.1604 | 36684572.0193 | 36738892.4959 | 36794209.6784 | 36850523.5669 | 36907834.1614 | 36965892.2854 | 37025196.2919 | 37085497.0044 | 37146794.4229 | 37209088.5474 | 37270635.1423 | 37332430.9138 | 37394226.6853 | 37455773.2803 | 37517569.0517 | 37579364.8232 | 37641160.5947 | 37702956.3662 | 37764752.1376 | 37826547.9091 | 37888343.6806 | 37950139.4521 | 38011935.2235 | 38073730.995
Murray River | VIC | 220 | 250 | 5 | 32771847.97 | 33070749.3628 | 33776507.0928 | 34419485.3571 | 34781204.81 | 34857198.8952 | 34883053.5407 | 34909590.0816 | 34936724.6668 | 34964407.1724 | 34992601.7738 | 35021313.7074 | 35050542.9731 | 35080289.571 | 35110424.1679 | 35141205.4301 | 35172504.0243 | 35204319.9507 | 35236653.2093 | 35268598.4687 | 35300673.0612 | 35332747.6536 | 35364692.9131 | 35396767.5055 | 35428842.098 | 35460916.6905 | 35492991.2829 | 35525065.8754 | 35557140.4679 | 35589215.0604 | 35621289.6528 | 35653364.2453 | 35685438.8378
Western Victoria | VIC | 220 | 250 | 5 | 35489154.48 | 35849191.1612 | 36652692.1557 | 37446456.2333 | 37968857.0771 | 38098228.1246 | 38171955.4105 | 38247627.1939 | 38325004.3648 | 38403943.9891 | 38484343.9095 | 38566219.0579 | 38649569.4341 | 38734395.0382 | 38820327.0632 | 38908103.1231 | 38997354.4109 | 39088080.9266 | 39180282.6702 | 39271377.9929 | 39362842.1226 | 39454306.2522 | 39545401.5749 | 39636865.7046 | 39728329.8342 | 39819793.9639 | 39911258.0935 | 40002722.2232 | 40094186.3528 | 40185650.4825 | 40277114.6121 | 40368578.7418 | 40460042.8714
South West Victoria | VIC | 500 | 600 | 10 | 84212105.58 | 84642020.3236 | 86355520.4954 | 88053881.3045 | 89145011.5845 | 89384141.5177 | 89531056.5812 | 89681846.3469 | 89836034.4719 | 89993336.1102 | 90153547.6155 | 90316698.7815 | 90482789.6082 | 90651820.0955 | 90823055.3282 | 90997965.1368 | 91175814.6061 | 91356603.736 | 91540332.5265 | 91721856.5716 | 91904115.5318 | 92086374.492 | 92267898.537 | 92450157.4972 | 92632416.4575 | 92814675.4177 | 92996934.3779 | 93179193.3381 | 93361452.2983 | 93543711.2585 | 93725970.2187 | 93908229.179 | 94090488.1392
Gippsland | VIC | 220 | 250 | 10 | 48730088.25 | 49197728.3709 | 50257790.794 | 51377745.4667 | 52203011.8868 | 52457639.6936 | 52598091.4797 | 52742247.5249 | 52889652.4018 | 53040033.7928 | 53193197.0634 | 53349170.6692 | 53507954.6103 | 53669548.8866 | 53833250.9143 | 54000465.8611 | 54170491.1431 | 54343326.7604 | 54518972.7128 | 54692510.9139 | 54866751.6988 | 55040992.4837 | 55214530.6847 | 55388771.4696 | 55563012.2545 | 55737253.0394 | 55911493.8242 | 56085734.6091 | 56259975.394 | 56434216.1789 | 56608456.9637 | 56782697.7486 | 56956938.5335
Central North Victoria | VIC | 220 | 250 | 10 | 46448767.23 | 46864747.0171 | 47842364.2537 | 48835001.3968 | 49524509.0949 | 49731694.4773 | 49831656.7759 | 49934255.4686 | 50039166.4188 | 50146195.8126 | 50255205.1248 | 50366214.6078 | 50479224.2617 | 50594234.0865 | 50710744.0394 | 50829754.2059 | 50950764.5433 | 51073775.0516 | 51198785.7307 | 51322296.2816 | 51446306.8753 | 51570317.469 | 51693828.02 | 51817838.6136 | 51941849.2073 | 52065859.801 | 52189870.3947 | 52313880.9884 | 52437891.582 | 52561902.1757 | 52685912.7694 | 52809923.3631 | 52933933.9567
Gippsland Coast | VIC | Note 1
Southern Ocean | VIC
South East South Australia | SA | 275 | 300 | 10 | 45188973.41 | 45527791.6102 | 46464463.5305 | 47348382.7474 | 47910352.6281 | 48032516.5902 | 48091938.1352 | 48152926.8557 | 48215290.0705 | 48278912.5718 | 48343712.015 | 48409700.4389 | 48476877.8433 | 48545244.2284 | 48614502.3489 | 48685246.6952 | 48757180.0221 | 48830302.3296 | 48904613.6177 | 48978033.1703 | 49051749.9681 | 49125466.7659 | 49198886.3186 | 49272603.1164 | 49346319.9142 | 49420036.712 | 49493753.5098 | 49567470.3076 | 49641187.1054 | 49714903.9032 | 49788620.701 | 49862337.4988 | 49936054.2966
Riverland | SA | 275 | 300 | 10 | 49870060.3 | 50314242.2473 | 51419251.0775 | 52562621.1592 | 53400835.8845 | 53613878.4013 | 53755570.2238 | 53900998.9998 | 54049705.2882 | 54201414.3767 | 54355929.9001 | 54513280.5707 | 54673466.3886 | 54836487.3537 | 55001634.6792 | 55170325.9387 | 55341852.3454 | 55516213.8994 | 55693410.6006 | 55868480.9413 | 56044260.0689 | 56220039.1965 | 56395109.5372 | 56570888.6648 | 56746667.7924 | 56922446.9199 | 57098226.0475 | 57274005.1751 | 57449784.3027 | 57625563.4302 | 57801342.5578 | 57977121.6854 | 58152900.8129
Mid-North South Australia | SA | 275 | 300 | 5 | 36228003.33 | 36569013.5516 | 37407063.6075 | 38213158.9598 | 38734605.775 | 38840615.931 | 38911810.9847 | 38984883.7031 | 39059603.2626 | 39135831.593 | 39213470.0819 | 39292533.1301 | 39373020.7378 | 39454932.9049 | 39537913.4916 | 39622674.7775 | 39708860.6229 | 39796471.0277 | 39885505.992 | 39973472.5366 | 40061795.2212 | 40150117.9057 | 40238084.4504 | 40326407.1349 | 40414729.8194 | 40503052.504 | 40591375.1885 | 40679697.873 | 40768020.5575 | 40856343.2421 | 40944665.9266 | 41032988.6111 | 41121311.2957
Yorke Peninsula | SA | 275 | 300 | 5 | 36228003.33 | 36569013.5516 | 37407063.6075 | 38213158.9598 | 38734605.775 | 38840615.931 | 38911810.9847 | 38984883.7031 | 39059603.2626 | 39135831.593 | 39213470.0819 | 39292533.1301 | 39373020.7378 | 39454932.9049 | 39537913.4916 | 39622674.7775 | 39708860.6229 | 39796471.0277 | 39885505.992 | 39973472.5366 | 40061795.2212 | 40150117.9057 | 40238084.4504 | 40326407.1349 | 40414729.8194 | 40503052.504 | 40591375.1885 | 40679697.873 | 40768020.5575 | 40856343.2421 | 40944665.9266 | 41032988.6111 | 41121311.2957
Northern South Australia | SA | 275 | 300 | 5 | 34305554.81 | 34603516.3811 | 35372672.8659 | 36072691.0802 | 36481259.5559 | 36551670.0165 | 36589276.3233 | 36627874.4412 | 36667342.4454 | 36707607.4054 | 36748617.2324 | 36790379.5332 | 36832894.308 | 36876161.5567 | 36919993.1607 | 36964765.3572 | 37010290.0275 | 37056567.1717 | 37103596.7898 | 37150062.0525 | 37196715.4337 | 37243368.8149 | 37289834.0776 | 37336487.4587 | 37383140.8399 | 37429794.221 | 37476447.6022 | 37523100.9834 | 37569754.3645 | 37616407.7457 | 37663061.1269 | 37709714.508 | 37756367.8892
Leigh Creek | SA | 275 | 300 | 10 | 46087132.04 | 46446190.1401 | 47415184.964 | 48348941.7761 | 48963988.4846 | 49103798.5283 | 49179031.0164 | 49256247.6756 | 49335204.5559 | 49415755.7949 | 49497797.1377 | 49581343.8262 | 49666395.8605 | 49752953.2405 | 49840639.6298 | 49930207.7013 | 50021281.1185 | 50113859.8815 | 50207943.9902 | 50300899.0896 | 50394230.5254 | 50487561.9613 | 50580517.0607 | 50673848.4965 | 50767179.9323 | 50860511.3682 | 50953842.804 | 51047174.2398 | 51140505.6757 | 51233837.1115 | 51327168.5473 | 51420499.9832 | 51513831.419
Roxby Downs | SA | 275 | 300 | 10 | 43841735.47 | 44150169.6591 | 45038332.7096 | 45847437.7828 | 46329717.4299 | 46425199.1788 | 46460878.1312 | 46497498.0752 | 46534943.3179 | 46573144.684 | 46612052.7307 | 46651674.6865 | 46692010.5514 | 46733060.3255 | 46774645.5314 | 46817123.1236 | 46860314.625 | 46904220.0355 | 46948839.3551 | 46992923.2429 | 47037185.608 | 47081447.9731 | 47125531.8608 | 47169794.2259 | 47214056.591 | 47258318.956 | 47302581.3211 | 47346843.6862 | 47391106.0512 | 47435368.4163 | 47479630.7813 | 47523893.1464 | 47568155.5115
Eastern Eyre Peninsula | SA | 275 | 300 | 10 | 43841735.47 | 44150169.6591 | 45038332.7096 | 45847437.7828 | 46329717.4299 | 46425199.1788 | 46460878.1312 | 46497498.0752 | 46534943.3179 | 46573144.684 | 46612052.7307 | 46651674.6865 | 46692010.5514 | 46733060.3255 | 46774645.5314 | 46817123.1236 | 46860314.625 | 46904220.0355 | 46948839.3551 | 46992923.2429 | 47037185.608 | 47081447.9731 | 47125531.8608 | 47169794.2259 | 47214056.591 | 47258318.956 | 47302581.3211 | 47346843.6862 | 47391106.0512 | 47435368.4163 | 47479630.7813 | 47523893.1464 | 47568155.5115
Western Eyre Peninsula | SA | 275 | 300 | 10 | 43841735.47 | 44150169.6591 | 45038332.7096 | 45847437.7828 | 46329717.4299 | 46425199.1788 | 46460878.1312 | 46497498.0752 | 46534943.3179 | 46573144.684 | 46612052.7307 | 46651674.6865 | 46692010.5514 | 46733060.3255 | 46774645.5314 | 46817123.1236 | 46860314.625 | 46904220.0355 | 46948839.3551 | 46992923.2429 | 47037185.608 | 47081447.9731 | 47125531.8608 | 47169794.2259 | 47214056.591 | 47258318.956 | 47302581.3211 | 47346843.6862 | 47391106.0512 | 47435368.4163 | 47479630.7813 | 47523893.1464 | 47568155.5115
South East South Australia Coast | SA | 275 | 1200 | 50 | 893932195.16 | 891599865.026 | 863363084.4696 | 852507472.336 | 859524040.8269 | 859524170.1797 | 859524591.735 | 859525024.4131 | 859525466.8394 | 859525918.1946 | 859526377.9034 | 859526846.0473 | 859527322.6261 | 859527807.64 | 859528298.9802 | 859528800.8641 | 859529311.1831 | 859529829.9371 | 859530357.1261 | 859530877.9888 | 859531400.9603 | 859531923.9318 | 859532444.7946 | 859532967.7661 | 859533490.7376 | 859534013.7091 | 859534536.6806 | 859535059.6521 | 859535582.6236 | 859536105.5951 | 859536628.5665 | 859537151.538 | 859537674.5095
North East Tasmania | TAS | 220 | 150 | 5 | 41401222.03 | 41736183.1137 | 42851281.2619 | 43817129.1536 | 44380568.6966 | 44483067.1663 | 44552322.0881 | 44623403.5523 | 44696086.9538 | 44770238.0287 | 44845760.8169 | 44922669.3443 | 45000963.611 | 45080643.6169 | 45161362.9272 | 45243814.4116 | 45327651.6352 | 45412874.598 | 45499483.3001 | 45585052.6977 | 45670968.5301 | 45756884.3626 | 45842453.7602 | 45928369.5926 | 46014285.4251 | 46100201.2575 | 46186117.09 | 46272032.9224 | 46357948.7549 | 46443864.5873 | 46529780.4197 | 46615696.2522 | 46701612.0846
North West Tasmania | TAS | 220 | 150 | 5 | 36367282.18 | 36752075.4236 | 37593173.1647 | 38448818.1198 | 39039977.2622 | 39168157.1597 | 39263083.2008 | 39360512.8395 | 39460138.2146 | 39561775.2941 | 39665292.5477 | 39770709.2005 | 39878025.2524 | 39987240.7035 | 40097880.7039 | 40210894.9533 | 40325808.6018 | 40442621.6494 | 40561334.0963 | 40678621.9937 | 40796384.7409 | 40914147.4882 | 41031435.3856 | 41149198.1329 | 41266960.8801 | 41384723.6273 | 41502486.3746 | 41620249.1218 | 41738011.869 | 41855774.6163 | 41973537.3635 | 42091300.1108 | 42209062.858
Central Highlands | TAS | 220 | 150 | 5 | 33440952.1 | 33760299.8925 | 34496559.9552 | 35190872.459 | 35610400.015 | 35684903.2196 | 35728767.2532 | 35773788.1651 | 35819823.697 | 35866788.8103 | 35914622.7263 | 35963334.329 | 36012923.6181 | 36063390.5938 | 36114515.8344 | 36166738.1832 | 36219838.2185 | 36273815.9403 | 36328671.3486 | 36382868.4921 | 36437285.0572 | 36491701.6223 | 36545898.7658 | 36600315.3309 | 36654731.8959 | 36709148.461 | 36763565.0261 | 36817981.5912 | 36872398.1563 | 36926814.7214 | 36981231.2865 | 37035647.8516 | 37090064.4167
North Tasmania Coast | TAS | Note 1
North-East Tasmania Coast | TAS
Notes:
1. The connection costs for the new offshore REZs are determined as per the 2023 Transmission Expansion Options Report.
2. The connection costs for all REZs was reviewed and consulted on through the 2023 Transmission Expansion Options Report.
3. Where no costs are shown, these have been allocated to REZ expansion costs instead.
System strength services cost options | bar: 2028-29 to 2049-50
Description |  |  |  |  | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
80 MVA synchronous condenser |  |  |  |  | 71110178.14 | 70562025.8936 | 71191930.8478 | 71957603.1723 | 72366158.2102 | 72367225.52 | 72367450.4997 | 72367681.4125 | 72367917.5308 | 72368158.4183 | 72368403.7603 | 72368653.6039 | 72368907.9491 | 72369166.7961 | 72369429.0194 | 72369696.8697 | 72369969.2217 | 72370246.0755 | 72370527.4309 | 72370805.41 | 72371084.5146 | 72371363.6191 | 72371641.5983 | 72371920.7028 | 72372199.8074 | 72372478.912 | 72372758.0165 | 72373037.1211 | 72373316.2257 | 72373595.3302 | 72373874.4348 | 72374153.5393 | 72374432.6439
125 MVA synchronous condenser |  |  |  |  | 95716613.18 | 94935548.9477 | 95778235.8184 | 96804182.4267 | 97350452.1276 | 97351490.7451 | 97351715.6857 | 97351946.5583 | 97352182.6356 | 97352423.4813 | 97352668.7806 | 97352918.5807 | 97353172.8818 | 97353431.6838 | 97353693.8615 | 97353961.6652 | 97354233.9699 | 97354510.7755 | 97354792.082 | 97355070.0129 | 97355349.0689 | 97355628.125 | 97355906.0558 | 97356185.1118 | 97356464.1679 | 97356743.2239 | 97357022.28 | 97357301.336 | 97357580.3921 | 97357859.4481 | 97358138.5042 | 97358417.5602 | 97358696.6163
200 MVA synchronous condenser |  |  |  |  | 131824581.075 | 130515079.4907 | 131670296.8734 | 133049199.0475 | 133779862.9414 | 133780328.3218 | 133780440.7562 | 133780556.1555 | 133780674.1564 | 133780794.5407 | 133780917.1512 | 133781042.0113 | 133781169.1212 | 133781298.4808 | 133781429.5277 | 133781563.3867 | 133781699.4955 | 133781837.8541 | 133781978.4623 | 133782117.3833 | 133782256.8667 | 133782396.3501 | 133782535.271 | 133782674.7544 | 133782814.2378 | 133782953.7212 | 133783093.2046 | 133783232.688 | 133783372.1714 | 133783511.6548 | 133783651.1382 | 133783790.6216 | 135285604.2659
250 MVA synchronous condenser |  |  |  |  | 181879920.55 | 180279675.6393 | 181867033.525 | 183803998.2025 | 184832201.6506 | 184833199.7633 | 184833424.6504 | 184833655.468 | 184833891.4892 | 184834132.2775 | 184834377.5184 | 184834627.2592 | 184834881.4998 | 184835140.2402 | 184835402.3555 | 184835670.0955 | 184835942.3354 | 184836219.0752 | 184836500.3148 | 184836778.1795 | 184837057.1691 | 184837336.1588 | 184837614.0235 | 184837893.0132 | 184838172.0028 | 184838450.9925 | 184838729.9821 | 184839008.9718 | 184839287.9615 | 184839566.9511 | 184839845.9408 | 184840124.9304 | 184840403.9201
Non-REZ connection costs
Non-REZ name | Region | Network voltage (kV) | Connection capacity (MVA) | Feeder length (km) | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
New South Wales Non-REZ | NSW | 500 | 600 | 20 | 148000000 | 148000000 | 151168480.8432 | 154336961.6863 | 156449282.2485 | 157271211.7894 | 157629824.6759 | 157997895.4777 | 158374261.3623 | 158758226.8998 | 159149295.5947 | 159547539.8619 | 159952959.7016 | 160365555.1136 | 160783532.2049 | 161210478.7617 | 161644600.8908 | 162085898.5924 | 162534371.8663 | 162977463.4609 | 163422348.9487 | 163867234.4364 | 164310326.031 | 164755211.5188 | 165200097.0065 | 165644982.4943 | 166089867.982 | 166534753.4697 | 166979638.9575 | 167424524.4452 | 167869409.9329 | 168314295.4207 | 168759180.9084
Victoria Non-REZ | VIC | 500 | 600 | 20 | 134000000 | 135024600.6149 | 138098402.4595 | 141172204.3042 | 143221405.534 | 143859397.2198 | 144283786.7944 | 144719370.1308 | 145164769.1411 | 145619161.9727 | 146081961.0375 | 146553251.8283 | 147033034.345 | 147521308.5877 | 148015951.6249 | 148521209.3195 | 149034958.7401 | 149557199.8867 | 150087932.7592 | 150612296.8372 | 151138783.8467 | 151665270.8562 | 152189634.9343 | 152716121.9438 | 153242608.9533 | 153769095.9629 | 154295582.9724 | 154822069.9819 | 155348556.9914 | 155875044.001 | 156401531.0105 | 156928018.02 | 157454505.0295
Notes:
1. A land use limit of 5% for onshore wind and 1% for solar is applied for all scenarios.
2. Where no costs are shown, these have been allocated to REZ expansion costs instead

## REZ Augmentations Options
Go to Assumptions Summary
REZ Augmentation Options
Existing Network Capacities shown are inclusive of existing generation, and not additional headroom
The transfer capacity increase represents increased limit at the time of high summer demand in the importing region. Tasmania peak demand occurs in winter and increased notional transfer capacity of VIC-TAS interconnector represents for winter as well.
Transfer capacities in the table are for long-term simulations in the generation and transmission expansion model.
Transfer capacities vary with generation dispatch, load and weather conditions. Similar to NEMDE, these variabilities are captured in the network constraint equations for simulations in short-term models using time-sequential half-hourly modelling.
Transfer capacity increase in this table are indicative and will be updated with input from TNSPs and additional power system studies.
All cost estimates are indicative and sourced from the 2023 Transission Expansion Options Report unless otherwise noted
REZ augmentation options presented in this spreadsheet are sourced from the 2023 Transmission Expansion Options Report. REZ augmentation options and costs were reviewed and consulted as part of 2023 Transmission Expansion Options Report consultation.
QLD
REZ / Constraint ID | REZ Name | Option | Description | Additional network capacity (MW) | Expected cost ($ million) | Cost estimate source | Cost estimate class | $M/MW | Easement Length (km) | Lead time | System strength connection costs ($M/MW)
Q1 | Far North QLD | Option 1 | • Establish a new 275 kV substation north of Millstream. • Build a 275 kV double-circuit line from Chalumbin to Millstream. • Rebuild the double-circuit Chalumbin–Ross 275 kV line at a higher capacity (possibly timed with asset replacement). • Build additional Chalumbin-Ross 275 kV double-circuit tower but switch as a single-circuit line (energise second line as generation develops) | 1290 | 1836 | AEMO TCD | Class 5b | 1.4233 | 275 | Long | Included as connection cost
|  | Option 2 | • Establish a new 275 kV substation in the Lakeland area • Build a double-circuit 275 kV line from Walkamin to the new substation near Lakeland. • Build a new 275 kV Chalumbin–Walkamin single-circuit line. • Rebuild the double-circuit Chalumbin–Ross 275 kV line at a higher capacity (possibly timed with asset replacement). • Build additional Chalumbin-Ross 275 kV double-circuit tower but switch as a single-circuit line (energise second line as generation develops) | 1290 | 2780 | AEMO TCD | Class 5b | 2.155 | 535 | Long
Q2 | North Qld Clean Energy Hub | CopperString | CopperString 2032: • Establish a new 500 kV substation south of Townsville (NQ 500 kV Substation) • Install 2x500/275 kV, 1500 MVA transformers at NQ 500kV substation • Establish a new NQ 275 kV substation • Cut-in the Strathmore to Ross 275kV DCST and SCST lines to the NQ 275kV Substation. • Establish a new 500 kV substation at Hughenden with associated switchgear and bays. • Establish a new 500kV substation (mid-point between NQ 500 kV and Hughenden substations) with associated switchgear and bays. • A new 500 kV transmission line from south of Townsville to Hughenden • A new 330 kV transmission line from Hughenden to Cloncurry • A new 220 kV transmission line from Cloncurry to Mount Isa • Up to six new substation sites | 1,500 nominal 2,300 if NQCQ Option 2 is selected. | This project is considered to be anticipated and so is not included as an option here. The scope of the project is listed here for context only.
|  | Option 1 | • Establish a 275 kV yard at Kidston substation near Forsayth. • Build a 275 kV double-circuit line from Kidston to Guybal Munjan Substation (energise only a single line until generation in the REZ develops). | 500 | 651 | AEMO TCD | Class 5b | 0.434 | 190 | Medium | Included as connection cost
|  | Option 2 | • Energise the second circuit on the line established in Option 1. • Additional reactors if required. Pre-requisite: Q2 Option 1 | 1000 | 0 | AEMO TCD | Class 5b | 0 | N/A | Medium
Q3 | Northern Qld | See NQ-CQ subregional augmentations | [8 empty] | Included as connection cost
Q4 | Isaac | See NQ2 group constraint augmentations | [8 empty] | Included as connection cost
Q5 | Barcaldine | Option 1 | • Establish a 275 kV substation in the Barcaldine region • Build a 340 km 275 kV double-circuit line from Lilyvale to Barcaldine (energise only a single line until generation in the REZ develops). | 500 | 1068 | AEMO TCD | Class 5b | 0.79111 | 340 | Long | 0.137
|  | Option 2 | • Energise the second circuit on the line established in Option 1. • Additional substation bays and reactors. Pre-requisite: Q5 Option 1 | 850 | 0 | AEMO TCD | Class 5b | 0 | N/A | Medium
Q6 | Fitzroy | See CQ-GG subregional augmentations
Q7 | Wide Bay | See SQ1 group constraint augmentations
Q8 | Darling Downs | See SWQLD1 Transmission Limit constraint augmentations
Q9 | Banana | Option 1 | • Establish a new 500 kV substation within the Banana REZ. • 200 km double-circuit 500 kV line from the Banana REZ to CQ substation associated with CQ-SQ Option 5. • Additional 500/275 kV 1,500 MVA transformer at the CQ substation. • Switchgear at CQ substation. Pre-requisite: CQ-SQ Option 5 | 3000 | 1078 | AEMO TCD | Class 5b | 0.35933 | 200 | Long | Included as connection cost
|  | Option 2 | • Establish a new 275 kV substation within the Banana REZ. • 100 km high capacity double-circuit 275 kV line from Banana REZ to Calvale Substation. • Associated switchgear • Limit extension special protection scheme (similar to a virtual transmission line). Cost of non-network service agreement excluded. | 1800 | 414 | AEMO TCD | Class 5b | 0.23 | 100 | Medium
|  | Option 3 | • Establish a new 275 kV substation within the Banana REZ. • 195 km double-circuit 275 kV line from Banana REZ to Wandoan South. • Switchgear at Wandoan South. | 1000 | 663 | AEMO TCD | Class 5b | 0.663 | 195 | Medium
NQ2 | Group constraint - Facilitating power to Central Queensland | Option 1 | • Construct additional 275 kV circuit from Bouldercombe – Stanwell. • String and energise the second Broadsound-Stanwell 275 kV additional circuit (on existing DCST). | 400 | 173 | AEMO TCD | Class 5b | 0.4325 | 18 | Medium | Included in individual REZ expansion cost
|  | Option 2 | • Additional 275 kV double-circuit lines between Central and North Queensland | 1400 | 1008 | AEMO TCD | Class 5b | 0.72 | 295 | Medium
SQ1 | Group Constraint - Wide Bay | Option 1 | • Rebuild Woolooga – Palmwood - South Pine 275 kV single-circuit line as a high-capacity double-circuit line. • 100 MVAr reactor for voltage control. | 1100 | 536 | AEMO TCD | Class 5b | 0.48727 | N/A | Long | 0.137
|  | Option 2 | • Rebuild Woolooga – South Pine 275 kV single-circuit line as a high-capacity double-circuit line • 100 MVAr reactor for voltage control | 1100 | 583 | AEMO TCD | Class 5b | 0.53 | N/A | Long
|  | Option 3 | • Prerequisite is CQ-SQ Option 5 • New 500 kV substation works at Borumba substation • Cut-in Halys-Woolooga West 500 kV line at Borumba | 1700 | 110 | AEMO TCD | Class 5b | 0.064706 | N/A | Long
SWQLD1 | Transmission Limit Constraint - Darling Downs | Option 1 | • Replace existing 1,300 MVA 330/275 kV transformer at Middle Ridge with 1,500 MVA 330/275 kV transformer. • Limit extension special protection system splitting scheme. Cost of non-service agreement excluded | 500 | 28.342 | Powerlink | Class 5 | 0.056684 | N/A | Short | 0.137
|  | Option 2 | • Limit extension special protection scheme – run-back of generation in SWQ with 300MW BESS response in SEQ (similar to a virtual transmission line). | 330 | To be provided by interested parties
|  | Option 3 | • Prerequisite is NNSW-SQ Option 5 and CQ-SQ Option 5 and SQ1 option 3 • New 2x 500/275 kV 1,500 MVA transformers at Western Downs with associated switchgear and bays • Cut-in 500 kV DCST lines from Halys to NNSW and associated switchgear and bays | 1500 | 184 | AEMO TCD | Class 5b | 0.12267 | N/A | Long
NSW
REZ / Constraint ID | REZ Name | Option | Description | Additional network capacity (MW) | Expected cost ($ million) | Estimate source | Cost estimate class | $M/MW | Easement Length (km) | Lead time | System strength connection costs ($M/MW)
N1 | North West NSW | Option 1 | • Two new 500 kV circuits from Orana REZ to locality of Gilgandra to locality of Boggabri to locality of Moree. • A new single 500 kV circuit from Orana REZ to Wollar. • New 500/330 kV substations in locality of Boggabri and Moree. • A new 500 kV switching station in locality of Gilgandra. • A new 330 kV single-circuit from Sapphire to locality of Moree. • A new 330 kV circuit from Tamworth to locality of Boggabri. • Line shunt reactors at both ends of Orana REZ-locality of Gilgandra, locality of Gilgandra-locality of Boggabri, locality of Boggabri-locality of Moree 500 kV circuits. | 1660 | 4684 | AEMO TCD | Class 5b | 2.8217 | 810 | Long | 0.137
N2 | New England | Option 1 | • New 330 kV Northern (Hub 10), Central South (Hub 1) and East (Hub 4) switching stations. • New 500 kV built and initially 330 kV operated DCST line from Central (Hub 5) to Central South (Hub1) with Quad Orange conductor. • New 500 kV built and initially 330 kV operated DCST line from Central (Hub 5) to Northern (Hub 10) with Quad Orange conductor. • New 330 kV DCST line between Central (Hub 5) and East (Hub 4) with Twin Olive conductor. | 1000 | 370 | AEMO TCD | Class 5b | 0.37 | 60 | Medium | 0.137
|  | Option 2 | • New North switching station and cuts into Sapphire - Armidale and Dumaresq - Armidale line. • New 500 kV built and initially 330 kV operated double-circuit line from North switching station to Hub 5. • Augment Hub 5 with one additional 500/330 kV transformer. • New 500 kV double-circuit line, strung on one side between Hub 5 to Hub 1. • New 330 kV DCST line from Hub 8 to Hub 5. • New Hub 8 switching station. (Pre-requisite: CNSW-NNSW Option 3) | 1500 | 1004 | AEMO TCD | Class 5b | 0.66933 | 140 | Long
|  | Option 3 | • New Hub 9 switching station. • Establish a new Lower Creek 330/132 kV substation with 1 x 330/132 kV 375 MVA transformer. • Rebuild part of Line 965 as 330 kV double-circuit from Armidale to Lower Creek. • Relocate existing 132 kV 200 MVA phase shift transformer on Line 965 from Armidale to Lower Creek. • New 330 kV double-circuit from Lower Creek to Hub 9. • Cut-in of Line 965 at new Lower Creek substation | 900 | 647 | AEMO TCD | Class 5b | 0.71889 | 20 | Medium
N3 | Central-West Orana | Central West Orana REZ transmission link | • New Merotherie 500/330 kV substation with 4 x 500/330/33 kV 1,500 MVA transformers. • New 330 kV Uarbry East, Uarbry West, Elong Elong switching stations. • New 500 kV Wollar switching station. • 2 x 500 kV double-circuit line from Wollar to Merotherie. • 330 kV double-circuit line from Merotherie to Uarbry East. • 330 kV double-circuit from Merotherie to Uarbry West. • 2 x 500 kV double-circuit and initially operated at 330 kV from Merotherie to Elong Elong. • 5 x 100 MVAr synchronous condensers at Elong Elong switching station. • 5 x 100 MVAr synchronous condensers at Merotherie substation. • Provision of switchbays for future generator connections. • An additional 330 kV single-circuit line from Bayswater to Liddell. • An additional 330 kV single-circuit line from Mt Piper to Wallerawang. • New 330 kV Uungula switching station and cut into Line 79 Wellington – Wollar • 1 x 330 kV DCST from Elong Elong to Uungula with Twin Olive conductor • 2 x 100 MVAr synchronous condensers at Uarbry West switching station • 3 x 100 MVAr synchronous condensers at Uarbry East switching station Note: Hunter Transmission Project is a pre-requisite for allowing network transfer greater than 3 GW. | 4500 | This project is considered to be anticipated and so is not included as an option here. The scope of the project is listed here for context so that the subsequent options can be understood. Option 1 includes expansions and augmentations to this project. | [5 empty] | Included as part of network build
|  | Option 1 | • Expand Elong Elong substation with 3 x 500/330/33 kV 1,500MVA transformers • Operate 4 circuits between Elong Elong and Merotherie to 500 kV (Pre-requisite: CWO REZ transmission link project) Note: Hunter Transmission Project will be required to get up to 6 GW total network capacity as pre-requisite. Note: Hunter Transmission Project is a pre-requisite for allowing network transfer greater than 3 GW. Note: 3 x 1,500 MVA transformers provide for 3 GW at Elong Elong however REZ network capacity is limited to 6 GW | 1500 | 243 | AEMO TCD | Class 5b | 0.162 | N/A | Medium
|  | Option 2 | • New 330 kV Stubbo switching station and cuts into Wellington - Wollar • New 330 kV single-circuit line between Wollar and Stubbo • Expand Wollar substation with 330 kV busbar and 1 x 500/300/33 kV 1,500 MVA transformer | 500 | 330 | AEMO TCD | Class 5b | 0.66 | 55 | Medium
|  | Option 3 | • New 330 kV Burrendong switching station and cuts into Line Wellington - Mt Piper • New Uungula switching station and cuts into Wollar - Wellington • New 330 kV double-circuit line from Burrendong switching station to Uungula | 500 | 273 | AEMO TCD | Class 5b | 0.546 | 45 | Medium
N4 | Broken Hill | Option 1 | • 500 kV double-circuit line from Bannaby – Broken Hill (>850 km). • Two mid-point switching stations and reactive plant. | 1750 | 5098 | AEMO TCD | Class 5b | 2.9131 | 849 | Long | 0.137
|  | Option 2 | 500 kV double-circuit HVDC line from Bannaby – Broken Hill (>850 km). • New HVDC converter stationss at Bannaby and Broken Hill | 1750 | 4576 | AEMO TCD | Class 5b | 2.6149 | 850 | Long
N5 | South West NSW | Option 1 | • Expand Dinawan 330 kV switching station to 500/330 kV substation with 3 x 500/330/33 kV, 1,500 MVA transformers • Operate 500 kV build and 330 kV operated double-circuit line from Dinawan to Wagga to 500 kV (Pre-requisite: EnergyConnect and HumeLink) | 2500 | 1418 | AEMO TCD | Class 5b | 0.5672 | 0 | Long | 0.137
|  | Option 2 | • New Conargo 330 kV switching station • New 330 kV double-circuit line from Conargo to Dinawan (Pre-requisite: Dinawan - Wagga 500 kV upgrade) | 800 | 383 | AEMO TCD | Class 5b | 0.47875 | 69 | Long
|  | Option 3 | • New Marbins Well 330 kV switching station • New 330 kV DCST line from Mabins Well to Dinawan (Pre-requisite: Dinawan - Wagga 500 kV upgrade) | 1400 | 300 | AEMO TCD | Class 5b | 0.21429 | 50 | Long
|  | Option 4 | • New The Plains 330 kV switching station • New 330 kV double-circuit line and strung on one side from The Plains to Dinawan (Pre-requisite: South West REZ Option 1) | 1400 | 417 | AEMO TCD | Class 5b | 0.29786 | 88 | Long
|  | Option 5 | • New Hays Plain 330 kV switching station • New Abercrombie 330 kV switching station • New 330 kV double-circuit line from Hays Plain to Abercrombie • New 330 kV double-circuit line from Abercrombie to The Plain • String the other side of 330 kV line from The Plain to Dinawan (Pre-requisite: South West REZ Option 4) | 1400 | 1047 | AEMO TCD | Class 5b | 0.74786 | 280 | Long
SWNSW1 | Secondary Transmission Limit - South West NSW | Option 1 | • Establish a new Darlington Point to Dinawan 330 kV transmission line, post Project EnergyConnect (Pre-requisite: Project EnergyConnect and HumeLink) | 600 | 167 | Transgrid | Class 5a | 0.27833 | 90 | Short
N6 | Wagga Wagga | Option 1 | Refer to SNSW-CNSW Option 3 and 4 subregional augmentations | [7 empty] | 0.137
N7 | Tumut | Option 1 | Refer to SNSW-CNSW Option 1 subregional augmentations | [7 empty] | Included as connection cost
N8 | Cooma-Monaro | Option 1 | • 132 kV single-circuit Williamsdale to Cooma-Monaro substation (located near generation interest) | 150 | 202 | AEMO TCD | Class 5b | 1.3467 | 81 | Medium | 0.137
|  | Option 2 | • 330 kV line Cooma-Williamdale-Stockdill • Two 330/132 kV transformers at Cooma | 500 | 512 | AEMO TCD | Class 5b | 1.024 | 126 | Medium
N9 | Hunter-Central Coast | Option 1 | • Rebuild the existing Line 83 Liddell - Muswellbrook as 330 kV double-circuit line • 1 x 330 kV double-circuit from East Hub to Muswellbrook • 1 x 330 kV double-circuit from West Hub to Muswellbrook | 950 | 307 | AEMO TCD | Class 5b | 0.32316 | 39 | Medium | 0.137
|  | Option 1A | • Install a new 330 kV circuit between Liddell and Muswellbrook, Twin Olive conductor • 1 x 330 kV DCST from East Hub to Muswellbrook conductor • 1 x 330 kV DCST from West Hub to Muswellbrook | 950 | 283 | AEMO TCD | Class 5b | 0.29789 | 57 | Medium
|  | Option 1AB | • Install a new 330 kV circuit between Liddell and Muswellbrook • 1 x 330 kV DCST from East Muswellbrook Hub to Muswellbrook • Build 330/132 kV 375 MVA transformer at West Muswellbrook Hub • 1 x 132 kV DCST from West Muswellbrook Hub to Muswellbrook | 850 | 274 | AEMO TCD | Class 5b | 0.32235 | 57 | Medium
|  | Option 1B | • Rebuild the existing Line 83 Liddell - Muswellbrook as 330 kV double-circuit line • 1 x 330 kV DCST from East Muswellbrook Hub to Muswellbrook • Build 330/132 kV 375MVA transformer at West Muswellbrook Hub • 1 x 132 kV DCST from West Muswellbrook Hub to Muswellbrook | 850 | 298 | AEMO TCD | Class 5b | 0.35059 | 39 | Medium
|  | Option 2 | • New 330 kV Singleton switching station and cuts into line 82 Liddell - Tomago | 500 | 59 | AEMO TCD | Class 5b | 0.118 | N/A | Short
|  | Option 2A | • New 330/132 kV 375 MVA Singleton two transformer substation and cuts into line 82 Liddell - Tomago and connected to Ausgrid's Singleton 132 kV substation switching station | 375 | 106 | AEMO TCD | Class 5b | 0.28267 | N/A | Medium
N10 | Hunter Coast | Option 1 | Refer to CNSW-SNW Option 1 subregional augmentations | [7 empty] | 0.137
N11 | Illawarra Coast | Option 1 | • 500 kV double-circuit line from Dapto – Bannaby. • Two 500/330 kV 1,500 MVA transformers at Dapto. (Pre-requisite: CNSW – SNW Option 2) | 2000 | 814 | AEMO TCD | Class 5b | 0.407 | 100 | Long | 0.137
N12 | Illawarra | Option 1 | • 500 kV double-circuit line from Dapto – Bannaby. • Two 500/330 kV 1,500 MVA transformers at Dapto. (Pre-requisite: CNSW – SNW Option 2) | 2000 | 814 | AEMO TCD | Class 5b | 0.407 | 100 | Long | 0.137
SA
REZ / Constraint ID | REZ Name | Option | Description | Additional network capacity (MW) | Expected cost ($ million) | Estimate source | Cost estimate class | $M/MW | Easement Length (km) | Lead time | System strength connection costs ($M/MW)
S1 | South East SA | See S1-TBMO transmission limit constraint augmentation and VIC-SESA and SESA-SA sub-regional augmentations
S2 | Riverland | Option 1 | (Post PEC) : • Co-ordinate new connections through turn in of Bundey – Buronga 330 kV No. 1 and No. 2 lines into a new substation at Riverland. | 700 | 100 | AEMO TCD | Class 5a | 0.14286 | N/A | Short | 0.137
S3 | Mid-North SA | See MN1 group constraint augmentations
S4 | Yorke Peninsula | Option 1 | • String first circuit of a 275 kV double-circuit line from Blythe West into new Yorke Peninsula substation. Pre-requisite: S3 Option 1 | 450 | 566 | AEMO TCD | Class 5b | 1.2578 | 162 | Medium | 0.137
|  | Option 2 | • String second circuit of a 275 kV double-circuit line from Blythe West into new Yorke Peninsula substation. • Cut in of Templers West into Bundey-Para 275 kV line. Pre-requisite: S3 Option 1, Option 1 | 450 | 156 | AEMO TCD | Class 5b | 0.34667 | 185 | Long
S5 | Northern SA | See NSA1 group constraint augmentations
S6 | Leigh Creek | Option 1 | • Build 275 kV double-circuit line from Davenport to new Leigh Creek substation. | 950 | 838 | AEMO TCD | Class 5b | 0.88211 | 235 | Short | 0.137
S7 | Roxby Downs | Option 1 | • Build 275 kV double-circuit line from Davenport to new Roxby Downs substation. | 950 | 541 | AEMO TCD | Class 5b | 0.56947 | 139 | Short | Included as connection cost
S8 | Eastern Eyre Peninsula | Option 1 | • Operate the future Cultana Yadnarie 132 kV double-circuit line (built as part of the Eyre Peninsula Link RIT T) at 275 kV by establishing a 275 kV substation at Yadnarie. | 300 | 100 | ElectraNet | Class 5a | 0.33333 | N/A | Short | Included as connection cost
S9 | Western Eyre Peninsula | Option 1 | • 275 kV double-circuit line from Cultana/Corraberra Hill to a new Elliston substation. | 950 | 862 | AEMO TCD | Class 5b | 0.90737 | 254 | Long | 0.137
|  | Option 2 | • 275 kV single-circuit line from Yadnarie to a new Elliston substation. | 500 | 424 | AEMO TCD | Class 5b | 0.848 | 144 | Long
|  | Option 3 | • New Elliston substation. • Single-circuit 275 kV line from Cultana/Corraberra Hill to Elliston. • Single-circuit 275 kV line from Yadnarie to Elliston. | 1000 | 1058 | AEMO TCD | Class 5b | 1.058 | 398 | Long
S10 | South East SA Coast | See VIC-SESA and SESA-SA sub-regional augmentations | [8 empty] | Included as connection cost
MN1 | Group Constraint - facilitating power out of mid-north SA | S3 Option 1 | • Build a 275 kV double-circuit line between Bundey and Para. • Disconnect existing Waterloo-Templers 132 kV line at each end. • Build a 132 kV single-circuit line from Templers West to Templers. • 1 x 160 MVA, 275/132 kV transformer at Templers West | 1200 | 389 | ElectraNet | Class 5b | 0.32417 | 136 | Short | Included as connection cost
|  | S3 Option 1a | Build a 275 kV double-circuit line between Bundey and Para. | 1200 | 350 | ElectraNet | Class 5b | 0.29167 | 126 | Short
|  | S3 Option 1b | Build a 275 kV double-circuit line from Brinkworth to cut into Bungama-Blyth West 275 kV circuit. | 100 | 70 | ElectraNet | Class 5b | 0.7 | 10 | Short
|  | S3 Option 2 | • Build a 330 kV double-circuit line from Bundey to Globe Derby. • Turn in the following lines to new Globe Derby 275 kV substation: Pelican Point - Parafield Gardens West, Torrens Island - Cherry Gardens, Torrens Island - Magill, Torrens Island - Para. | 1150 | 740 | AEMO TCD | Class 5b | 0.64348 | 150 | Short
|  | S3 Option 3 | • Build a 275 kV double-circuit line from Bundey to Cultana. – Stage 1: 275 kV double-circuit from Bundey to a new substation near Yunta. – Stage 2: 275 kV double-circuit from a new substation near Yunta to Cultana. | 800 | 1434 | AEMO TCD | Class 5b | 1.7925 | 430 | Short
|  | S3 Option 4 | • 330 kV double-circuit lines between Bundey to Cultana | 1000 | 1434 | AEMO TCD | Class 5b | 1.434 | 390 | Short
NSA1 | Group Constraint - facilitating power out of north SA | Option 1 | • Build a 275 kV double-circuit line from Davenport-Cultana | 1200 | 268 | AEMO TCD | Class 5b | 0.22333 | 62 | Short | Included as connection cost
|  | Option 2 | • Operate the future Cultana Yadnarie 132 kV double-circuit line (built as part of the Eyre Peninsula Link RIT T) at 275 kV by establishing a 275 kV substation at Yadnarie. | 300 | 100 | ElectraNet | Class 5a | 0.33333 | N/A | Short
S1-TBMO | Transmission Limit Constraint - | Option 1 | (part of preparatory activities): • String vacant circuit on the 275 kV Tungkillo – Tailem Bend line. | 120 | 34 | ElectraNet | Class 5b | 0.28333 | N/A | Short | Included as connection cost
TAS
REZ / Constraint ID | REZ Name | Option | Description | Additional network capacity (MW) | Expected cost ($ million) | Estimate source | Cost estimate class | $M/MW | Easement Length (km) | Lead time | System strength connection costs ($M/MW)
T1 | North East Tasmania | Option 1 | • 220 kV double-circuit line between a new substation in George Town area, and a new substation in far north-east Tasmania. • 220 kV double-circuit line connecting the new George Town substation to the existing George Town substation. | 800 | 400 | AEMO TCD | Class 5b | 0.5 | 85 | Medium | Included as connection cost
|  |  | • Second 220 kV double-circuit line between the new substations in George Town and far north-east Tasmania, strung one side only. Prerequisite: T1 Option 1 | 800 | 269 | AEMO TCD | Class 5b | 0.33625 | 80 | Long
T2 | North West Tasmania | Option 1 | • Build a new 220 kV switching station at Staverton and cut-in all Sheffield-Mersey Forth 220 kV lines at Staverton. • Build a new double-circuit Staverton-Hampshire Hills 220 kV line. • Build new Hampshire Hills wind collector station. | 800 | 304 | AEMO TCD | Class 4 | 0.38 | 59 (without Marinus Link) | Short | Included as connection cost
|  | Option 2 | • Build new “Farrell 2” wind collector station on west coast Tasmania (nearby existing Farrell substation) and establish new double-circuit Farrell2-Hampshire Hills 220 kV line. Pre-requisite: TAS-VIC Option 2, T2 Option 1. | 500 | 258 | AEMO TCD | Class 5a | 0.516 | 65 | Long
|  | Option 3 | • Build double-circuit West Montagu-Hampshire 220 kV line. • Build a second 220 kV double-circuit line from Hampshire Hills to Burnie to Heybridge. Pre-requisite: TAS-VIC Option 2, T2 Option 1. | 800 | 534 | AEMO TCD | Class 5a | 0.6675 | 132 | Medium
T3 | Central Highlands | Option 1 | • Build a Palmerston-Waddamana 220 kV double-circuit line. Prior to (without) MarinusLink: • If before Marinus Link 1, bring forward the rebuild of Palmerston-Sheffield 220 kV line as double-circuit and build 2 x power flow controllers on the 2 x 220 kV transmission lines from Palmerston-Sheffield. With MarinusLink: • If after Marinus Link 1, build 2 x power flow controllers on the 2 x 220 kV transmission lines from Palmerton-Sheffield. | 690 | 201 (with Marinus Link) 434 (without Marinus Link) | AEMO TCD | Class 5a | 0.62899 | 0 (with Marinus Link) 0 (without Marinus Link) | Short | Included as connection cost
|  | Option 2 | • Build a second Palmerston-Sheffield 220 kV double-circuit line. Pre-requisite: TAS-VIC Option 2, T3 Option 1. | 675 | 274 | AEMO TCD | Class 5a | 0.40593 | 79 | Long
T4 | North Tasmania Coast | Option 1 | • Build a new Burnie-Heybridge-Sheffield 220 kV double-circuit line. Pre-requisites: TAS-VIC Option 2. | 1360 | 206 | AEMO TCD | Class 5a | 0.15147 | 53 | Long | Included as connection cost
|  | Option 2 | • Build a new George Town-Sheffield 220 kV double-circuit line. • Build 2 x power flow controllers on the 2 x 220 kV double-circuit line between George Town-Hadspen. Pre-requisite: TAS-VIC Option 2. | 900 | 307 | AEMO TCD | Class 5a | 0.34111 | 68 | Long | Included as connection cost
VIC
REZ / Constraint ID | REZ Name | Option | Description | Additional network capacity (MW) | Expected cost ($ million) | Estimate source | Cost estimate class | $M/MW | Easement Length (km) | Lead time | System strength connection costs ($M/MW)
V2 | Murray River | Option 1 | • New 220 kV double-circuit line between Red Cliffs – Wemen – Kerang. • Establish new substations close to Redcliff and Kerang. Pre-requisite: VNI West (Bulgana) | 800 | 912 | AEMO TCD | Class 5b | 1.14 | 275 | Long | Included as connection cost
V3 | Western Victoria | See V3-EAST secondary transmission limit constraint augmentations
V4 | South West Victoria | See SWV1 group constraint augmentations
V5 | Gippsland | See SEVIC1 transmission limit constraint augmentations
V6 | Central North Vic | Option 1 | • New double-circuit 220 kV line from Shepparton to Dederang via Glenrowan. | 250 | 709 | AEMO TCD | Class 5b | 2.836 | 175 | Long | Included as connection cost
|  | Option 2 | • New double-circuit 220 kV line from Near Shepparton – Near Bendigo – Near Kerang. | 500 | 1110 | AEMO TCD | Class 5b | 2.22 | 290 | Long
|  | Option 3 | • New double-circuit 500 kV line from Shepparton – Near Kerang. | 1500 | 1077 | AEMO TCD | Class 5b | 0.718 | 160 | Long
V7 | Gippsland Coast | Option 1 | • New 500 kV double-circuit line from Hazelwood to vicinity of Gippsland coast. • Two 500/220 kV transformers. | 2000 | 684 | AEMO TCD | Class 5b | 0.342 | 16 | Long | Included as connection cost
|  | Option 2 | • New 500 kV double-circuit line from Hazelwood to vicinity of Gippsland coast. • Two 500/220 kV transformers. Pre requisite: Option 1 | 6000 | 684 | AEMO TCD | Class 5b | 0.114 | 16 | Long
V8 | Southern Ocean | See SWV1 group constraint augmentations
SWV1 | Group Constraint - South West Victoria | Option 1 | • Moorabool-Geelong 220 kV line upratings via terminal station augmentations. Pre-requisite: Mortlake turn-in |  | 64 | AEMO Victorian Planning | Class 5a |  | 0 | Long | Included as connection cost
|  | Option 1A | • New 500 kV single-circuit line from Mortlake – Moorabool • Sydenham line upratings Pre requisite: Option 1 | 1500 | 725 | AEMO Victorian Planning | Class 5a | 0.526 | 170 | Long
|  | Option 1B | • Moorabool-Sydenham 500 kV single-circuit Pre requisite: Option 1A | 1750 | 1013 | AEMO Victorian Planning | Class 5a | 0.57886 | 64 | Long
|  | Option 1C | • Heywood- Mortlake 500 kV single-circuit Pre requisite: Option 1B | 1750 | 1372 | AEMO Victorian Planning | Class 5a | 0.784 | 96 | Long
|  | Option 2A | • New Mortlake – Bulgana 500 kV single circuit Pre requisite: Option 1 | 1950 | 618 | AEMO Victorian Planning | Class 5a | 0.34974 | 147 | Long
|  | Option 2B | • New Mortlake – Bulgana 500 kV double circuit Pre requisite: Option 1 | 2900 | 803 | AEMO Victorian Planning | Class 5a | 0.29897 | 147 | Long
|  | Option 3A | • New Heywood - Bulgana 500 kV single-circuit • New Alcoa Portland - Heywood 500 kV single circuit Pre requisite: Option 1 | 1800 | 1076 | AEMO Victorian Planning | Class 5a | 0.63333 | 271 | Long
|  | Option 3B | • New Heywood - Bulgana 500 kV double-circuit • New Alcoa Portland - Heywood 500 kV single circuit Pre requisite: Option 1 | 2800 | 1325 | AEMO Victorian Planning | Class 5a | 0.49607 | 271 | Long
SEVIC1 | Transmission Limit Constraint - Gippsland | Option 1 | •Modified parallel switching arrangement at Hazelwood 220 kV switchyard (for details refer 2023 Victorian Annual Planning Report). •New 220 kV double circuit line between Hazelwood and Yallourn (~10 km). •New additional 500/220 kV transformer in Melbourne eastern metropolitan area. | 2000 | 297 | AEMO TCD | Class 5b | 0.1485 | 10 | Medium | Included as connection cost
|  | Option 2 | • New 500 kV single circuit from Loy Yang – South Morang within the existing easement corridor. • 250 MVAr dynamic reactive compensation Pre requisite: Option 1 | 1700 | 948 | AEMO TCD | Class 5b | 0.55765 | 0 | Long
V3-East | Secondary Transmission Limit - Western Victoria | Option 1 | • New 220 kV single-circuit line from Elaine to Moorabool. | 600 | 163 | AEMO TCD | Class 5b | 0.27167 | 43 | Medium | Included as connection cost

## REZ Costs forecast
Go to Assumptions Summary
REZ Augmentation Costs forecast (real 2023 dollars)
AEMO has applied escalation factors to REZ augmentation project cost estimates for the ISP, consistent with its transmission cost forecasting approach.
See 2023 Transmission Expansion Options Report for further details.
The worksheet has Progressive and Step Change/Green Energy Export cost forecast. These cost escalations are year on year cost esclations.
Step Change/ Green Energy Scenario
QLD
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Q1 | Far North QLD | Option 1 | 1836460949.12 | 1840509947.3547 | 1867338369.8277 | 1895989521.1736 | 1919762563.4121 | 1934044517.7873 | 1950207978.2927 | 1964932157.9789 | 1978350155.7351 | 1986859875.8398 | 1990713684.951 | 1994284936.9346 | 1997905053.7611 | 2001600328.4401 | 2005358731.4815 | 2009209556.8416 | 2013141255.8972 | 2017153631.0048 | 2021247455.2752 | 2025318850.0443 | 2029418076.4846 | 2033534957.0883 | 2037653582.1203 | 2041802527.0042 | 2045969707.912 | 2050154029.7539 | 2054355476.5945 | 2058574141.1314 | 2062810127.8897 | 2067063543.3979 | 2071334495.1794 | 2075623091.6553 | 2079929442.1413
|  | Option 2 | 2780404941.45 | 2787008577.506 | 2829626637.5262 | 2873316623.4515 | 2907958882.2277 | 2927247079.154 | 2949656167.2983 | 2969640753.2468 | 2987695621.6796 | 2998016287.8656 | 3002929844.0925 | 3007933557.3144 | 3013027427.5313 | 3018211454.7432 | 3023463099.7013 | 3028827440.9031 | 3034281939.1 | 3039826594.2918 | 3045461406.4786 | 3051028600.9192 | 3056618334.6085 | 3062208068.2979 | 3067775262.7385 | 3073364996.4278 | 3078954730.1171 | 3084544463.8064 | 3090134197.4958 | 3095723931.1851 | 3101313664.8744 | 3106903398.5638 | 3112493132.2531 | 3118082865.9424 | 3123672599.6317
Q2 | North Qld Clean Energy Hub | CopperString | Anticipated
|  | Option 1 | 651469275.09 | 652700510.9376 | 662339271.2732 | 671732473.9855 | 678734095.8021 | 682890752.6076 | 687782290.3411 | 692107007.4213 | 695986214.2354 | 697852785.5143 | 698535252.9074 | 699230242.638 | 699937754.7062 | 700657789.1118 | 701387215.2705 | 702132294.3511 | 702889895.7691 | 703660019.5247 | 704442665.6177 | 705215919.9577 | 705992304.882 | 706768689.8063 | 707541944.1462 | 708318329.0705 | 709094713.9948 | 709871098.9191 | 710647483.8434 | 711423868.7677 | 712200253.692 | 712976638.6163 | 713753023.5406 | 714529408.4649 | 715305793.3892
Q3 | Northern Qld | See NQ-CQ subregional augmentations
Q4 | Isaac | See NQ2 group constraint augmentations
Q5 | Barcaldine | Option 1 | 1068420080.45 | 1066891118.0219 | 1080128369.428 | 1080560292.2772 | 1087376309.251 | 1092925705.039 | 1099828938.7015 | 1105549178.7741 | 1110312731.051 | 1111097432.5109 | 1110434808.0919 | 1109760025.4268 | 1109073084.5154 | 1108373985.3578 | 1107665767.5155 | 1106942351.8655 | 1106206777.9692 | 1105459045.8267 | 1104699155.438 | 1103948383.734 | 1103194572.4684 | 1102440761.2028 | 1101689989.4987 | 1100936178.2331 | 1100182366.9675 | 1099428555.702 | 1098674744.4364 | 1097920933.1708 | 1097167121.9052 | 1096413310.6396 | 1095659499.374 | 1094905688.1084 | 1094151876.8428
Q6 | Fitzroy | See CQ-GG subregional augmentations
Q7 | Wide Bay | See SQ1 group constraint augmentations
Q8 | Darling Downs | Preparatory Activities- See note below
Q9 | Banana | Option 1 | 1078371762.27 | 1072548800.2958 | 1088460048.8349 | 1105428244.3114 | 1117615093.71 | 1124379181.3184 | 1132281006.2042 | 1139526104.6273 | 1146266012.9236 | 1149230575.3241 | 1150643684.0232 | 1152082721.3222 | 1153547687.2212 | 1155038581.7202 | 1156548922.6692 | 1158091674.3681 | 1159660354.667 | 1161254963.566 | 1162875501.0649 | 1164476592.1138 | 1166084165.3127 | 1167691738.5116 | 1169292829.5605 | 1170900402.7594 | 1172507975.9583 | 1174115549.1572 | 1175723122.3561 | 1177330695.555 | 1178938268.7539 | 1180545841.9528 | 1182153415.1517 | 1183760988.3507 | 1185368561.5496
|  | Option 2 | 413993266.52 | 415972385.1915 | 422971745.2715 | 429884999.933 | 434869020.1538 | 437590853.1976 | 440747563.3817 | 443659668.6638 | 446380568.4772 | 447813534.412 | 448418293.0251 | 449034148.1266 | 449661099.7164 | 450299147.7945 | 450945518.2389 | 451605759.2936 | 452277096.8366 | 452959530.868 | 453653061.3877 | 454338269.5411 | 455026251.8167 | 455714234.0922 | 456399442.2456 | 457087424.5212 | 457775406.7967 | 458463389.0722 | 459151371.3478 | 459839353.6233 | 460527335.8988 | 461215318.1743 | 461903300.4499 | 462591282.7254 | 463279265.0009
|  | Option 3 | 663241042.44 | 665451267.4768 | 676039252.5965 | 686867674.2085 | 695257486.2025 | 699846325.3849 | 705153489.1134 | 709947709.0052 | 714338104.3665 | 717114154.1594 | 718296163.0432 | 719499860.1634 | 720725245.5201 | 721972319.1131 | 723235658.8835 | 724526108.9493 | 725838247.2516 | 727172073.7902 | 728527588.5653 | 729866837.163 | 731211507.8199 | 732556178.4767 | 733895427.0745 | 735240097.7313 | 736584768.3882 | 737929439.045 | 739274109.7019 | 740618780.3587 | 741963451.0156 | 743308121.6725 | 744652792.3293 | 745997462.9862 | 747342133.643
NQ2 | Group constraint - Facilitating power to Central Queensland | Option 1 | 173333535.69 | 173537087.36 | 176680169.51 | 179174943.14 | 180727275.42 | 181720971.21 | 182886865.67 | 183905427 | 184829978.61 | 184815171.5841 | 184800090.644 | 184784732.9895 | 184769098.6204 | 184753187.5369 | 184737068.9174 | 184720604.4049 | 184703863.1779 | 184686845.2364 | 184669550.5803 | 184652463.4602 | 184635307.1614 | 184618150.8626 | 184601063.7425 | 184583907.4437 | 184566751.1449 | 184549594.8462 | 184532438.5474 | 184515282.2486 | 184498125.9498 | 184480969.6511 | 184463813.3523 | 184446657.0535 | 184429500.7547
|  | Option 2 | 1007783813.12 | 1008038253.7148 | 1021051360.2668 | 1032520088.7934 | 1040123938.7591 | 1045812167.61 | 1052651594.6436 | 1058436637.9657 | 1063384634.7515 | 1064881439.0279 | 1064626453.4969 | 1064366789.3322 | 1064102446.534 | 1063833425.1022 | 1063560894.6952 | 1063282515.9962 | 1062999458.6635 | 1062711722.6973 | 1062419308.0975 | 1062130402.4729 | 1061840327.1899 | 1061550251.9069 | 1061261346.2823 | 1060971270.9993 | 1060681195.7163 | 1060391120.4333 | 1060101045.1503 | 1059810969.8673 | 1059520894.5843 | 1059230819.3013 | 1058940744.0183 | 1058650668.7352 | 1058360593.4522
SQ1 | Group Constraint - Wide Bay | Option 1 | 536895468.1127 | 538132049.0398 | 545570177.645 | 552673588.8889 | 557503794.049 | 560696772.0066 | 564437029.2214 | 567712110.2348 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616 | 570633514.5616
|  | Option 2 | 583066283.0134 | 585656817.1795 | 594817859.4493 | 605105160.064 | 613599306.4407 | 618000398.3453 | 622949700.3969 | 627458775.1598 | 631638805.0155 | 633362126.231 | 634786593.2469 | 636237197.2722 | 637713938.307 | 639216816.3512 | 640739297.1526 | 642294449.2158 | 643875738.2884 | 645483164.3705 | 647116727.4621 | 648730687.7966 | 650351182.3835 | 651971676.9703 | 653585637.3048 | 655206131.8916 | 656826626.4785 | 658447121.0653 | 660067615.6522 | 661688110.239 | 663308604.8259 | 664929099.4127 | 666549593.9996 | 668170088.5864 | 669790583.1733
|  | Option 3 | 110057013.87 | 110871562.9718 | 110568687.3193 | 112940289.5849 | 113959388.5844 | 114386666.1204 | 115022048.8024 | 115716650.7803 | 116444157.9994 | 116482013.0396 | 116508894.8904 | 116536269.9863 | 116564138.3271 | 116592499.9128 | 116621231.4323 | 116650579.5081 | 116680420.8287 | 116710755.3944 | 116741583.205 | 116772041.0819 | 116802622.2701 | 116833203.4582 | 116863661.3351 | 116894242.5232 | 116924823.7114 | 116955404.8995 | 116985986.0877 | 117016567.2758 | 117047148.4639 | 117077729.6521 | 117108310.8402 | 117138892.0284 | 117169473.2165
SWQLD1 | Transmission Limit Constraint - Darling Downs | Option 1 | Preparatory Activities- See note below
|  | Option 2 | Non-network projects are not estimated in capital costs
|  | Option 3 | 184026844.16 | 183493336.2729 | 186887794.4916 | 189822632.1016 | 191163843.7508 | 191598261.5051 | 192445115.9259 | 193324076.6067 | 194233668.7181 | 194261741.5817 | 194281237.0431 | 194301090.2194 | 194321301.1105 | 194341869.7166 | 194362706.6088 | 194383990.6446 | 194405632.3953 | 194427631.8609 | 194449989.0414 | 194472077.9358 | 194494256.2588 | 194516434.5818 | 194538523.4762 | 194560701.7992 | 194582880.1223 | 194605058.4453 | 194627236.7684 | 194649415.0914 | 194671593.4144 | 194693771.7375 | 194715950.0605 | 194738128.3836 | 194760306.7066
NSW
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
N1 | North West NSW | Option 1 | 4683570694.16 | 4703516536.5876 | 4775599569.9091 | 4855161748.7584 | 4914331441.0457 | 4944752228.9214 | 4980211168.8202 | 5013161859.2531 | 5044274310.5121 | 5086983852.3775 | 5095732142.1076 | 5104640950.9153 | 5113710278.8006 | 5122940125.7635 | 5132290362.0347 | 5141841247.1528 | 5151552651.3486 | 5161424574.622 | 5171457016.973 | 5181369070.0158 | 5191321252.828 | 5201273435.6402 | 5211185488.683 | 5221137671.4952 | 5231089854.3074 | 5241042037.1196 | 5250994219.9318 | 5260946402.744 | 5270898585.5562 | 5280850768.3684 | 5290802951.1806 | 5300755133.9928 | 5310707316.8049
N2 | New England | Option 1 | 370392725.98 | 372722679.4855 | 379824215.2964 | 386767380.232 | 391487462.1087 | 393870708.9946 | 396672750.1754 | 399355739.3182 | 401941997.472 | 405273274.0293 | 405901299.656 | 406540848.6887 | 407191921.1274 | 407854516.9721 | 408525755.3713 | 409211398.028 | 409908564.0906 | 410617253.5593 | 411337466.4339 | 412049036.7541 | 412763487.9258 | 413477939.0974 | 414189509.4176 | 414903960.5892 | 415618411.7609 | 416332862.9325 | 417047314.1042 | 417761765.2759 | 418476216.4475 | 419190667.6192 | 419905118.7908 | 420619569.9625 | 421334021.1341
|  | Option 2 | 1004401782 | 1011204959.0609 | 1030510596.3865 | 1051698711.1525 | 1067967373.7034 | 1075384724.442 | 1083891439.3726 | 1080930713.9663 | 1088835747.5479 | 1098338157.6225 | 1101521443.5996 | 1104763138.4938 | 1108063242.3049 | 1111421755.033 | 1114824074.4489 | 1118299405.0111 | 1121833144.4903 | 1125425292.8865 | 1129075850.1997 | 1132682600.8251 | 1136303953.6798 | 1139925306.5345 | 1143532057.16 | 1147153410.0147 | 1150774762.8694 | 1154396115.7241 | 1158017468.5788 | 1161638821.4335 | 1165260174.2882 | 1168881527.1429 | 1172502879.9976 | 1176124232.8523 | 1179745585.707
|  | Option 3 | 647203680.09 | 651990774.0912 | 664965036.4824 | 679100470.3607 | 690132640.2294 | 695099176.6696 | 700758267.7186 | 706235776.1618 | 711574725.4968 | 719240649.0631 | 721505406.3418 | 723811718.7999 | 726159586.4375 | 728549009.2544 | 730969598.456 | 733442131.6318 | 735956219.9871 | 738511863.5218 | 741109062.2359 | 743675094.5654 | 746251515.6898 | 748827936.8142 | 751393969.1438 | 753970390.2682 | 756546811.3926 | 759123232.517 | 761699653.6414 | 764276074.7658 | 766852495.8902 | 769428917.0146 | 772005338.139 | 774581759.2634 | 777158180.3878
N3 | Central-West Orana | Central West Orana REZ transmission link | Anticipated project
|  | Option 1 | 243410039.19 | 242986106.2847 | 247406498.6209 | 251298062.3826 | 253040851.2868 | 253610745.6513 | 254692821.9521 | 255832786.3497 | 257031912.3413 | 257043196.7037 | 257046109.9704 | 257049076.6915 | 257052096.8671 | 257055170.4971 | 257058284.2179 | 257061464.7568 | 257064698.7501 | 257067986.1978 | 257071327.1 | 257074627.9114 | 257077942.0863 | 257081256.2613 | 257084557.0727 | 257087871.2476 | 257091185.4226 | 257094499.5975 | 257097813.7725 | 257101127.9475 | 257104442.1224 | 257107756.2974 | 257111070.4724 | 257114384.6473 | 257117698.8223
|  | Option 2 | 329782042.82 | 331112953.9979 | 336959977.875 | 342841615.7431 | 346859456.104 | 348774840.1678 | 351114398.0343 | 353358435.9742 | 355534331.4406 | 358388504.1917 | 358936636.9319 | 359494827.1534 | 360063074.8565 | 360641380.041 | 361227228.3366 | 361825648.4841 | 362434126.113 | 363052661.2234 | 363681253.8153 | 364302303.296 | 364925867.1472 | 365549430.9983 | 366170480.4791 | 366794044.3302 | 367417608.1813 | 368041172.0325 | 368664735.8836 | 369288299.7347 | 369911863.5859 | 370535427.437 | 371158991.2881 | 371782555.1393 | 372406118.9904
|  | Option 3 | 272858295.37 | 274691352.4723 | 280108848.3425 | 285335945.4057 | 288803657.6605 | 290527255.9155 | 292568214.3966 | 294544174.2947 | 296464843.7777 | 299050274.0025 | 299506845.8004 | 299971795.0624 | 300445121.7886 | 300926825.979 | 301414813.2675 | 301913272.3863 | 302420108.9693 | 302935323.0164 | 303458914.5277 | 303976222.9408 | 304495625.7201 | 305015028.4993 | 305532336.9124 | 306051739.6917 | 306571142.4709 | 307090545.2501 | 307609948.0293 | 308129350.8085 | 308648753.5877 | 309168156.3669 | 309687559.1462 | 310206961.9254 | 310726364.7046
N4 | Broken Hill | Option 1 | 5097859988.37 | 5117220290.9869 | 5184097635.6324 | 5254876296.3846 | 5302026055.4891 | 5331501877.1373 | 5365979582.1787 | 5397057624.3941 | 5425595998.8652 | 5457995363.638 | 5460280959.5142 | 5462608492.9295 | 5464977963.8838 | 5467389372.3772 | 5469832234.0247 | 5472327517.5961 | 5474864738.7064 | 5477443897.3558 | 5480064993.5442 | 5482654636.5783 | 5485254763.9972 | 5487854891.4161 | 5490444534.4502 | 5493044661.8691 | 5495644789.288 | 5498244916.7068 | 5500845044.1257 | 5503445171.5446 | 5506045298.9635 | 5508645426.3824 | 5511245553.8012 | 5513845681.2201 | 5516445808.639
|  | Option 2 | 4575560873.27 | 4636165564.5156 | 4728471231.6464 | 4819838797.8187 | 4879521590.2302 | 4908737325.3252 | 4936833673.4334 | 4965601447.9623 | 4996493508.4305 | 5031463204.463 | 5037537249.2267 | 5043722744.353 | 5050019689.8419 | 5056428085.6935 | 5062920069.3171 | 5069551365.894 | 5076294112.8335 | 5083148310.1356 | 5090113957.8004 | 5096996017.6932 | 5103905940.1766 | 5110815862.6601 | 5117697922.5529 | 5124607845.0363 | 5131517767.5198 | 5138427690.0032 | 5145337612.4867 | 5152247534.9701 | 5159157457.4536 | 5166067379.9371 | 5172977302.4205 | 5179887224.904 | 5186797147.3874
N5 | South West NSW | Option 1 | 1418427595.46 | 1425333132.6532 | 1446268799.9947 | 1469948259.1294 | 1487141526.8051 | 1496070832.979 | 1506444526.7125 | 1516145948.2089 | 1525369903.3028 | 1544376717.5472 | 1546736519.9898 | 1549139621.5597 | 1551586022.257 | 1554075722.0816 | 1556597896.2518 | 1559174194.3313 | 1561793791.5381 | 1564456687.8723 | 1567162883.3339 | 1569836604.45 | 1572521150.3479 | 1575205696.2458 | 1577879417.3619 | 1580563963.2598 | 1583248509.1577 | 1585933055.0556 | 1588617600.9535 | 1591302146.8514 | 1593986692.7494 | 1596671238.6473 | 1599355784.5452 | 1602040330.4431 | 1604724876.341
|  | Option 2 | 382536056.11 | 385148834.6005 | 391826524.704 | 399135083.8068 | 404725671.9348 | 407486170.8778 | 410596647.8854 | 413541485.4857 | 416364333.7749 | 425232036.6824 | 426186057.5377 | 427157583.3629 | 428146614.1579 | 429153149.9227 | 430172814.4149 | 431214360.1194 | 432273410.7937 | 433349966.4378 | 434444027.0518 | 435524958.9383 | 436610267.0674 | 437695575.1964 | 438776507.083 | 439861815.212 | 440947123.341 | 442032431.4701 | 443117739.5991 | 444203047.7281 | 445288355.8572 | 446373663.9862 | 447458972.1152 | 448544280.2443 | 449629588.3733
|  | Option 3 | 299577968.52 | 301430153.3963 | 306774951.6487 | 312397961.749 | 316595939.3309 | 318684689.403 | 321078470.7037 | 323342248.0055 | 325504702.784 | 331709784.8167 | 332390376.5567 | 333083456.2186 | 333789023.8022 | 334507079.3077 | 335234500.7546 | 335977532.1038 | 336733051.3748 | 337501058.5676 | 338281553.6823 | 339052682.8556 | 339826934.0094 | 340601185.1631 | 341372314.3364 | 342146565.4902 | 342920816.644 | 343695067.7977 | 344469318.9515 | 345243570.1052 | 346017821.259 | 346792072.4128 | 347566323.5665 | 348340574.7203 | 349114825.874
|  | Option 4 | 416523543.37 | 419592161.893 | 426784213.9669 | 435030044.9487 | 441723036.1004 | 444955476.0375 | 448499979.4943 | 451845052.9043 | 455059361.3117 | 467316675.2099 | 468582992.8304 | 469872545.6365 | 471185333.6284 | 472521356.8059 | 473874806.3727 | 475257299.9216 | 476663028.6563 | 478091992.5766 | 479544191.6826 | 480978964.3993 | 482419545.9125 | 483860127.4257 | 485294900.1424 | 486735481.6556 | 488176063.1687 | 489616644.6819 | 491057226.1951 | 492497807.7082 | 493938389.2214 | 495378970.7346 | 496819552.2477 | 498260133.7609 | 499700715.274
|  | Option 5 | 1046609662.37 | 1052952433.5506 | 1071323633.6956 | 1091127653.5852 | 1093303952.6366 | 1100869971.5927 | 1109393448.4619 | 1117383500.5733 | 1124988856.6269 | 1146342846.3104 | 1149004694.691 | 1151715384.3263 | 1154474915.2164 | 1157283287.3611 | 1160128290.4468 | 1163034345.1009 | 1165989241.0097 | 1168992978.1732 | 1172045556.5913 | 1175061504.0685 | 1178089661.8593 | 1181117819.6501 | 1184133767.1273 | 1187161924.9181 | 1190190082.7089 | 1193218240.4997 | 1196246398.2905 | 1199274556.0814 | 1202302713.8722 | 1205330871.663 | 1208359029.4538 | 1211387187.2446 | 1214415345.0355
SWNSW1 | Secondary Transmission Limit - South West NSW | Option 1 | 167000000 | 168033762.58 | 170734660.18 | 174001675.03 | 176856490.5 | 178229713.55 | 179731575.18 | 181125039.64 | 182441642.04 | 183022788.08 | 183614684.67 | 184217441.76 | 184831059.33 | 185455537.4 | 186088160.82 | 186734359.86 | 187391419.39 | 188059339.4 | 188738119.9 | 189408755.04 | 190082105.3 | 190755455.56 | 191426090.69 | 192099440.95 | 192772791.21 | 193446141.47 | 194119491.73 | 194792841.98 | 195466192.24 | 196139542.5 | 196812892.76 | 197486243.02 | 198159593.27
N6 | Wagga Wagga | Option 1 | Refer to Forecasted Transmission flow paths (SNSW-CNSW) Option 3 and 4 in the flow paths
N7 | Tumut | Option 1 | HumeLink
N8 | Cooma-Monaro | Option 1 | 201643435.92 | 203332481.0995 | 206890562.8612 | 211157393.3218 | 214743970.033 | 216428450.6327 | 218250636.543 | 219979845.5148 | 221650742.6675 | 225275368.0382 | 226018272.1716 | 226774807.5736 | 227544974.244 | 228328772.183 | 229122793.5733 | 229933854.0493 | 230758545.7937 | 231596868.8067 | 232448823.0882 | 233290553.9183 | 234135692.5655 | 234980831.2127 | 235822562.0428 | 236667700.69 | 237512839.3373 | 238357977.9845 | 239203116.6317 | 240048255.2789 | 240893393.9262 | 241738532.5734 | 242583671.2206 | 243428809.8678 | 244273948.515
|  | Option 2 | 512954346.52 | 515746313.3228 | 525094845.7586 | 535570829.7798 | 544188611.3109 | 548149756.2428 | 552642984.5469 | 545497432.6261 | 549485986.3414 | 556155550.2711 | 557911201.5019 | 559699066.5167 | 561519145.3156 | 563371437.8985 | 565247890.8195 | 567164610.9705 | 569113544.9056 | 571094692.6247 | 573108054.1279 | 575097255.293 | 577094509.9042 | 579091764.5154 | 581080965.6805 | 583078220.2917 | 585075474.9028 | 587072729.514 | 589069984.1251 | 591067238.7363 | 593064493.3474 | 595061747.9586 | 597059002.5697 | 599056257.1809 | 601053511.7921
N9 | Hunter-Central Coast | Option 1 | 307063934.91 | 308253314.129 | 314822944.1075 | 320875605.7198 | 325062966.3844 | 327057438.6372 | 329488625.3115 | 331801352.6797 | 334010986.64 | 337298442.1695 | 337930835.2032 | 338574831.7788 | 339230431.8962 | 339897635.5556 | 340573541.8714 | 341263952.6146 | 341965966.8997 | 342679584.7267 | 343404806.0956 | 344121324.8081 | 344840744.406 | 345560164.0039 | 346276682.7164 | 346996102.3143 | 347715521.9123 | 348434941.5102 | 349154361.1082 | 349873780.7061 | 350593200.3041 | 351312619.902 | 352032039.4999 | 352751459.0979 | 353470878.6958
|  | Option 1A | 283129029.82 | 284209281.0283 | 290165004.845 | 295750949.6598 | 299736762.1003 | 301631460.1058 | 303919442.1178 | 306085986.5373 | 308148964.049 | 311482912.3829 | 312120640.2511 | 312770069.548 | 313431200.2738 | 314104032.4283 | 314785640.6544 | 315481875.6665 | 316189812.1073 | 316909449.9769 | 317640789.2753 | 318363352.5021 | 319088841.0861 | 319814329.6701 | 320536892.897 | 321262381.481 | 321987870.065 | 322713358.649 | 323438847.233 | 324164335.817 | 324889824.401 | 325615312.985 | 326340801.569 | 327066290.153 | 327791778.737
|  | Option 1AB | 274506774.68 | 275601709.743 | 281315034.7185 | 286692285.0328 | 290389108.8419 | 292116926.8118 | 294229969.8448 | 296255229.2791 | 298207740.2736 | 301068367.887 | 301626733.2061 | 302195343.7604 | 302774199.55 | 303363300.5748 | 303960085.5259 | 304569677.0211 | 305189513.7515 | 305819595.7171 | 306459922.918 | 307092566.1924 | 307727770.7756 | 308362975.3588 | 308995618.6333 | 309630823.2165 | 310266027.7997 | 310901232.3829 | 311536436.9662 | 312171641.5494 | 312806846.1326 | 313442050.7158 | 314077255.2991 | 314712459.8823 | 315347664.4655
|  | Option 1B | 298259423 | 299459028.064 | 305779139.5944 | 311618137.0481 | 315516202.7148 | 317343887.4857 | 319600475.1326 | 321771800.0294 | 323870247.4077 | 326696260.5143 | 327250320.8393 | 327814547.4088 | 328388940.2228 | 328973499.2813 | 329565683.0232 | 330170574.5707 | 330785632.3627 | 331410856.3992 | 332046246.6802 | 332674012.2778 | 333304319.4365 | 333934626.5953 | 334562392.1929 | 335192699.3516 | 335823006.5104 | 336453313.6691 | 337083620.8278 | 337713927.9866 | 338344235.1453 | 338974542.304 | 339604849.4628 | 340235156.6215 | 340865463.7802
|  | Option 2 | 58512971.63 | 59264516.4723 | 60463128.6463 | 61586003.0683 | 62132057.9819 | 62424149.0846 | 62768378.6816 | 63134260.8215 | 63517191.713 | 63564126.0074 | 63573163.0511 | 63582365.9122 | 63591734.5905 | 63601269.0862 | 63610927.9449 | 63620794.0752 | 63630826.0228 | 63641023.7877 | 63651387.37 | 63661626.5892 | 63671907.2628 | 63682187.9364 | 63692427.1557 | 63702707.8293 | 63712988.5029 | 63723269.1765 | 63733549.8501 | 63743830.5237 | 63754111.1973 | 63764391.8709 | 63774672.5445 | 63784953.2181 | 63795233.8916
|  | Option 2A | 106104649.48 | 106707980.5659 | 108923877.3679 | 110857310.8401 | 111741595.0292 | 112127710.4114 | 112683338.6146 | 113276559.8964 | 110568873.6227 | 110596377.2854 | 110605383.6041 | 110614555.1764 | 110623892.0022 | 110633394.0816 | 110643020.1012 | 110652852.6877 | 110662850.5277 | 110673013.6213 | 110683341.9685 | 110693546.3755 | 110703792.0959 | 110714037.8162 | 110724242.2232 | 110734487.9436 | 110744733.664 | 110754979.3844 | 110765225.1048 | 110775470.8252 | 110785716.5455 | 110795962.2659 | 110806207.9863 | 110816453.7067 | 110826699.4271
N10 | Hunter Coast | Option 1 | Refer to Forecasted Transmission flow paths CNSW-SNW Option 1
N11 | Illawarra Coast | Option 1 | Refer to N12 forecasted costs
N12 | Illawarra | Option 1 | 813815319.22 | 817811736.6265 | 832369006.0704 | 848481785.9113 | 860767680.5083 | 866382557.1392 | 872976740.222 | 879280385.8856 | 885371634.17 | 892369728.4993 | 894675154.5803 | 897022882.0572 | 899412910.9302 | 901845241.1991 | 904309297.515 | 906826230.5759 | 909385465.0328 | 911987000.8857 | 914630838.1345 | 917242949.3363 | 919865635.8872 | 922488322.438 | 925100433.6399 | 927723120.1907 | 930345806.7416 | 932968493.2924 | 935591179.8433 | 938213866.3941 | 940836552.945 | 943459239.4958 | 946081926.0467 | 948704612.5975 | 951327299.1483
SA
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
S1 | South East SA | See S1-TBMO transmission limit constraint augmentation and VIC-SESA and SESA-SA sub-regional augmentations
S2 | Riverland | Option 1 | 99500441.64 | 100015326.3701 | 102255314.0525 | 104140918.1788 | 104990385.2527 | 105344504.8246 | 105870682.2941 | 106436138.0283 | 107031077.0638 | 107050696.7222 | 107063575.6081 | 107076690.8038 | 107090042.3093 | 107103630.1247 | 107117395.1724 | 107131455.6074 | 107145752.3523 | 107160285.407 | 107175054.7715 | 107189646.9037 | 107204298.1133 | 107218949.3229 | 107233541.455 | 107248192.6646 | 107262843.8742 | 107277495.0838 | 107292146.2935 | 107306797.5031 | 107321448.7127 | 107336099.9223 | 107350751.1319 | 107365402.3415 | 107380053.5511
S3 | Mid-North SA | Preparatory Activities- See note below
S4 | Yorke Peninsula | Option 1 | 566404537.76 | 570696903.5072 | 581508795.7762 | 594089057.7387 | 604710524.5661 | 609503489.0154 | 614780750.3635 | 619812937.9056 | 624686054.6341 | 628662104.0844 | 631012458.596 | 633405938.8784 | 635842544.9318 | 638322276.756 | 640834352.9083 | 643400336.2742 | 646009445.4109 | 648661680.3185 | 651357040.997 | 654020057.3473 | 656693855.1403 | 659367652.9334 | 662030669.2837 | 664704467.0767 | 667378264.8697 | 670052062.6628 | 672725860.4558 | 675399658.2488 | 678073456.0419 | 680747253.8349 | 683421051.6279 | 686094849.421 | 688768647.214
|  | Option 2 | 155991705.95 | 156381664.364 | 159528033.9236 | 162082678.663 | 163576920.6052 | 164416775.1031 | 165407734.8154 | 166315587.9528 | 167187856.0189 | 167203464.1076 | 167214025.7045 | 167224781.0921 | 167235730.2705 | 167246873.2396 | 167258161.5519 | 167269692.1026 | 167281416.444 | 167293334.5763 | 167305446.4993 | 167317413.0792 | 167329428.1068 | 167341443.1344 | 167353409.7143 | 167365424.7419 | 167377439.7696 | 167389454.7972 | 167401469.8248 | 167413484.8524 | 167425499.88 | 167437514.9076 | 167449529.9352 | 167461544.9628 | 167473559.9905
S5 | Northern SA | See NSA1 group constraint augmentations
S6 | Leigh Creek | Option 1 | 837712569.5 | 839218469.7873 | 851149230.9977 | 862460157.7241 | 870039662.366 | 874810467.6862 | 880547725.0652 | 885630949.4188 | 890208058.2468 | 892091591.0127 | 892399421.3087 | 892712899.867 | 893032026.6876 | 893356801.7706 | 893685813.0502 | 894021884.6578 | 894363604.5276 | 894710972.6598 | 895063989.0543 | 895412769.2521 | 895762961.5154 | 896113153.7787 | 896461933.9765 | 896812126.2398 | 897162318.5031 | 897512510.7665 | 897862703.0298 | 898212895.2931 | 898563087.5565 | 898913279.8198 | 899263472.0831 | 899613664.3464 | 899963856.6098
S7 | Roxby Downs | Option 1 | 541633683.11 | 542220445.1562 | 549702732.8473 | 556080679.0094 | 559451194.7714 | 561978973.5978 | 565178411.3924 | 567991405.3391 | 570504900.075 | 570889913.4188 | 570472792.0162 | 570048017.0098 | 569615588.3998 | 569175506.186 | 568729683.7694 | 568274294.3482 | 567811251.3233 | 567340554.6946 | 566862204.4623 | 566389594.4327 | 565915071.0022 | 565440547.5717 | 564967937.5421 | 564493414.1116 | 564018890.6811 | 563544367.2506 | 563069843.8201 | 562595320.3896 | 562120796.9591 | 561646273.5286 | 561171750.0981 | 560697226.6676 | 560222703.2371
S8 | Eastern Eyre Peninsula | Option 1 | 100000000 | 100496072.7612 | 102452038.7764 | 104197512.9971 | 104989468.221 | 105327833.4761 | 105826243.8583 | 106359700.364 | 106922698.458 | 106925952.3391 | 106927113.8983 | 106928296.7705 | 106929500.9557 | 106930726.4539 | 106931967.9369 | 106933236.0612 | 106934525.4985 | 106935836.2488 | 106937168.3121 | 106938484.3906 | 106939805.7974 | 106941127.2042 | 106942443.2828 | 106943764.6896 | 106945086.0964 | 106946407.5032 | 106947728.91 | 106949050.3168 | 106950371.7236 | 106951693.1304 | 106953014.5372 | 106954335.944 | 106955657.3508
S9 | Western Eyre Peninsula | Option 1 | 862153003.45 | 864007756.3943 | 877129324.2573 | 890072347.5065 | 899533840.5815 | 904941360.3509 | 911352694.644 | 917096095.1333 | 922318178.5586 | 925194177.9455 | 926183275.3287 | 927190521.2877 | 928215915.8225 | 929259458.9332 | 930316613.4758 | 931396453.7382 | 932494442.5764 | 933610579.9904 | 934744865.9803 | 935865540.5383 | 936990752.2402 | 938115963.9422 | 939236638.5002 | 940361850.2021 | 941487061.9041 | 942612273.6061 | 943737485.308 | 944862697.01 | 945987908.7119 | 947113120.4139 | 948238332.1159 | 949363543.8178 | 950488755.5198
|  | Option 2 | 423873320.8 | 425180907.6311 | 431655287.5424 | 438197699.4761 | 443062682.8302 | 445822727.9443 | 449035745.823 | 451927533.6532 | 454573098.2246 | 455108968.7672 | 455652880.5485 | 456206772.3625 | 456770644.2092 | 457344496.0886 | 457925832.9925 | 458519644.9372 | 459123436.9147 | 459737208.9248 | 460360960.9676 | 460977227.9859 | 461595990.0123 | 462214752.0388 | 462831019.0571 | 463449781.0836 | 464068543.11 | 464687305.1365 | 465306067.1629 | 465924829.1894 | 466543591.2159 | 467162353.2423 | 467781115.2688 | 468399877.2952 | 469018639.3217
|  | Option 3 | 1058019572.74 | 1060439617.3493 | 1076390763.5875 | 1082428158.2165 | 1094667925.7616 | 1101576888.4055 | 1109652949.0515 | 1116864367.7635 | 1123407122.9169 | 1124884431.3155 | 1126386558.4864 | 1127916247.6238 | 1129473498.7276 | 1131058311.7979 | 1132663796.343 | 1134303733.3461 | 1135971232.3157 | 1137666293.2517 | 1139388916.1541 | 1141090867.5817 | 1142799709.501 | 1144508551.4202 | 1146210502.8478 | 1147919344.767 | 1149628186.6863 | 1151337028.6055 | 1153045870.5247 | 1154754712.4439 | 1156463554.3632 | 1158172396.2824 | 1159881238.2016 | 1161590080.1209 | 1163298922.0401
S10 | South East SA Coast | See VIC-SESA and SESA-SA sub-regional augmentations
MN1 | Group Constraint - facilitating power out of mid-north SA | S3 Option 1 | n/a | 389000000 | 395956014.6589 | 404038315.4628 | 411052319.0509 | 414293613.609 | 417929064.9711 | 421325534.7685 | 424541304.6973 | 427060839.826 | 428585277.5019 | 430137686.5113 | 431718066.8542 | 433326418.5306 | 434955748.7071 | 436620043.0505 | 438312308.7274 | 440032545.7378 | 441780754.0817 | 443507983.9255 | 445242206.6026 | 446976429.2798 | 448703659.1235 | 450437881.8007 | 452172104.4778 | 453906327.155 | 455640549.8321 | 457374772.5093 | 459108995.1865 | 460843217.8636 | 462577440.5408 | 464311663.2179 | 466045885.8951
|  | S3 Option 1a | n/a | 70000000 | 70889492.2339 | 71774585.4716 | 72424467.9675 | 72861142.5325 | 73363839.6408 | 73796379.9994 | 74175745.4357 | 74340246.3127 | 74367279.0767 | 74394807.8548 | 74422832.647 | 74451353.4531 | 74480246.2698 | 74509759.104 | 74539767.9522 | 74570272.8144 | 74601273.6906 | 74631902.5564 | 74662655.4256 | 74693408.2948 | 74724037.1606 | 74754790.0298 | 74785542.899 | 74816295.7683 | 74847048.6375 | 74877801.5067 | 74908554.376 | 74939307.2452 | 74970060.1144 | 75000812.9837 | 75031565.8529
|  | S3 Option 1b | n/a | 350000000 | 355511059.866 | 361683855.6179 | 366833429.5391 | 369495632.1032 | 372498792.7874 | 375230306.5858 | 377753127.6507 | 379615272.0517 | 380536762.7289 | 381475161.4919 | 382430468.3407 | 383402683.2754 | 384387579.2744 | 385393610.3807 | 386416549.5728 | 387456396.8507 | 388513152.2144 | 389557226.5138 | 390605527.8347 | 391653829.1555 | 392697903.4549 | 393746204.7757 | 394794506.0965 | 395842807.4174 | 396891108.7382 | 397939410.059 | 398987711.3799 | 400036012.7007 | 401084314.0215 | 402132615.3424 | 403180916.6632
|  | S3 Option 2 | 739957582.49 | 743130554.1843 | 756722888 | 771769599.784 | 784275537.2369 | 789986150.8017 | 796582289.3717 | 802776762.367 | 808659214.3016 | 812945262.6041 | 815590629.4164 | 818284535.0693 | 821026979.5627 | 823817962.8968 | 826645350.3613 | 829533411.3766 | 832470011.2324 | 835455149.9289 | 838488827.4659 | 841486100.8725 | 844495508.9892 | 847504917.1059 | 850502190.5125 | 853511598.6293 | 856521006.746 | 859530414.8627 | 862539822.9795 | 865549231.0962 | 868558639.2129 | 871568047.3297 | 874577455.4464 | 877586863.5631 | 880596271.6799
|  | S3 Option 3 | 1434153052.65 | 1438528056.6593 | 1462332903.443 | 1487405452.2763 | 1507791745.9453 | 1518268922.5973 | 1530367579.0275 | 1541356059.2455 | 1551474072.3507 | 1558720735.9124 | 1562253487.0481 | 1565851059.3055 | 1569513452.6846 | 1573240667.1855 | 1577016497.5278 | 1580873354.2722 | 1584795032.1384 | 1588781531.1263 | 1592832851.236 | 1596835555.5043 | 1600854465.0531 | 1604873374.6019 | 1608876078.8703 | 1612894988.4191 | 1616913897.9679 | 1620932807.5167 | 1624951717.0655 | 1628970626.6143 | 1632989536.1631 | 1637008445.7119 | 1641027355.2607 | 1645046264.8096 | 1649065174.3584
|  | S3 Option 4 | 1434203533.62 | 1437377125.2607 | 1460444360.9096 | 1484941724.0972 | 1505296108.1972 | 1515735227.4395 | 1527869346.5409 | 1538817977.4525 | 1548829588.7363 | 1556151505.9303 | 1559761571.2938 | 1563437876.3888 | 1567180421.2152 | 1570989205.7731 | 1574847670.1295 | 1578788934.1503 | 1582796437.9024 | 1586870181.3861 | 1591010164.6011 | 1595100468.0176 | 1599207331.367 | 1603314194.7163 | 1607404498.1328 | 1611511361.4822 | 1615618224.8315 | 1619725088.1809 | 1623831951.5302 | 1627938814.8796 | 1632045678.2289 | 1636152541.5783 | 1640259404.9276 | 1644366268.277 | 1648473131.6263
NSA1 | Group Constraint - facilitating power out of north SA | Option 1 | 268254758.93 | 269325359.3583 | 274389761.0208 | 279267709.3452 | 282794373.4738 | 284590198.6087 | 286719212.8629 | 288702077.8448 | 290565729.4539 | 291613820.2561 | 292120378.4367 | 292636231.2629 | 293161378.7346 | 293695820.8518 | 294237233.9532 | 294790265.3614 | 295352591.4152 | 295924212.1145 | 296505127.4593 | 297079071.82 | 297655339.842 | 298231607.864 | 298805552.2247 | 299381820.2467 | 299958088.2688 | 300534356.2908 | 301110624.3129 | 301686892.3349 | 302263160.3569 | 302839428.379 | 303415696.401 | 303991964.4231 | 304568232.4451
|  | Option 2 | Refer to S8
S1-TBMO | Transmission Limit Constraint - | Option 1 | Preparatory Activities- See note below
TAS
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
T1 | North East Tasmania | Option 1 | 400088757.45 | 402722474.9943 | 410267709.3161 | 418562567.5666 | 425246478.0824 | 428382704.3321 | 431934802.0189 | 435304783.4599 | 438531232.6305 | 440839017.701 | 442169914.8701 | 443525232.1708 | 444904969.603 | 446309127.1668 | 447731599.8292 | 449184597.6561 | 450662015.6145 | 452163853.7044 | 453690111.9259 | 455198055.0487 | 456712103.2044 | 458226151.3601 | 459734094.4829 | 461248142.6387 | 462762190.7944 | 464276238.9501 | 465790287.1058 | 467304335.2615 | 468818383.4172 | 470332431.5729 | 471846479.7286 | 473360527.8843 | 474874576.0401
|  | Option 2 | 269281992.82 | 271051971.6828 | 276718386.2409 | 283022381.3927 | 288378296.6564 | 290720353.6251 | 293343365.9699 | 295845405.7182 | 298260331.8218 | 300517140.3073 | 301735696.0066 | 302976610.5261 | 304239883.8658 | 305525516.0256 | 306827917.3006 | 308158267.1008 | 309510975.7212 | 310886043.1617 | 312283469.4224 | 313664126.568 | 315050373.4186 | 316436620.2692 | 317817277.4148 | 319203524.2654 | 320589771.116 | 321976017.9666 | 323362264.8172 | 324748511.6679 | 326134758.5185 | 327521005.3691 | 328907252.2197 | 330293499.0703 | 331679745.9209
T2 | North West Tasmania | Option 1 (Prior to Project Marinus- Part B) | 303849108.07 | 306078065.5881 | 312480096.5109 | 319222034.1264 | 324412447.1562 | 326743441.5479 | 329419161.432 | 332013752.9721 | 334542231.3656 | 336236091.1411 | 337275319.5909 | 338333616.4527 | 339410981.7264 | 340507415.412 | 341618150.4066 | 342752720.9161 | 343906359.8375 | 345079067.1709 | 346270842.9161 | 347448317.3524 | 348630558.8917 | 349812800.431 | 350990274.8673 | 352172516.4066 | 353354757.9459 | 354536999.4852 | 355719241.0245 | 356901482.5638 | 358083724.1031 | 359265965.6424 | 360448207.1817 | 361630448.721 | 362812690.2603
|  | Option 2 | 258488012.24 | 260336077.2325 | 265388551.9046 | 271200946.2605 | 276133037.502 | 278345985.0831 | 280813713.1642 | 283164585.0915 | 285427475.0258 | 287243194.0907 | 288343194.8693 | 289463379.1485 | 290603746.9281 | 291764298.2083 | 292939987.1139 | 294140905.3951 | 295362007.1769 | 296603292.4592 | 297864761.242 | 299111092.3995 | 300362469.432 | 301613846.4646 | 302860177.622 | 304111554.6546 | 305362931.6871 | 306614308.7197 | 307865685.7522 | 309117062.7848 | 310368439.8173 | 311619816.8499 | 312871193.8825 | 314122570.915 | 315373947.9476
|  | Option 3 | 533716596.52 | 537240141.907 | 548206689.0201 | 549895084.1459 | 559793786.4784 | 564180923.3352 | 569146337.1185 | 573892730.5368 | 578467642.9155 | 581855048.2219 | 584082930.5203 | 586351691.3928 | 588661330.8397 | 591011848.8609 | 593393025.8127 | 595825300.9824 | 598298454.7264 | 600812487.0447 | 603367397.9373 | 605891649.8991 | 608426121.5045 | 610960593.1099 | 613484845.0718 | 616019316.6772 | 618553788.2826 | 621088259.888 | 623622731.4934 | 626157203.0988 | 628691674.7043 | 631226146.3097 | 633760617.9151 | 636295089.5205 | 638829561.1259
T3 | Central Highlands | Option 1 (with Project Marinus) | 200899029.9 | 201074802.43 | 204475521.59 | 207005118.66 | 208505586.04 | 209370127.48 | 210498934.99 | 211555068.49 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54 | 212535778.54
|  | Option 2 (Prior to Project Marinus) | 433747641.34 | 434656874.55 | 441539865.53 | 447336028.52 | 450937936.8 | 453162686.42 | 455892548.71 | 458375646.39 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57 | 460651141.57
|  | Option 2 | 274158646.73 | 275603667.7137 | 280267550.3595 | 285272047.8633 | 289147115.0079 | 291138964.9363 | 293396146.989 | 295485210.5665 | 297449698.5775 | 298785861.4894 | 299403220.771 | 300031907.7458 | 300671922.4138 | 301323264.7751 | 301983102.9064 | 302657100.6541 | 303342426.0951 | 304039079.2294 | 304747060.0569 | 305446545.1144 | 306148862.0953 | 306851179.0762 | 307550664.1338 | 308252981.1146 | 308955298.0955 | 309657615.0764 | 310359932.0572 | 311062249.0381 | 311764566.019 | 312466882.9999 | 313169199.9807 | 313871516.9616 | 314573833.9425
T4 | North Tasmania Coast | Option 1 | 206261557.23 | 207250113.1181 | 211529266.065 | 215675146.7643 | 218677543.3148 | 220105549.7778 | 221797907.5641 | 223405757.3265 | 224944816.7757 | 225930498.2721 | 226424541.5508 | 226927649.8438 | 227439823.151 | 227961061.4726 | 228489098.5548 | 229028466.9049 | 229576900.2693 | 230134398.648 | 230700962.041 | 231260726.6732 | 231822757.5591 | 232384788.4449 | 232944553.0772 | 233506583.963 | 234068614.8488 | 234630645.7346 | 235192676.6205 | 235754707.5063 | 236316738.3921 | 236878769.278 | 237440800.1638 | 238002831.0496 | 238564861.9354
|  | Option 2 | 306999256.12 | 308424671.0711 | 314067497.0531 | 319683617.7493 | 324112519.4624 | 326164424.7618 | 328547442.5595 | 330827449.7516 | 333015702.1934 | 334458155.2141 | 335293478.8441 | 336144129.5131 | 337010107.2212 | 337891411.9684 | 338784211.995 | 339696170.8203 | 340623456.6848 | 341566069.5883 | 342524009.5309 | 343470454.1942 | 344420730.6173 | 345371007.0403 | 346317451.7036 | 347267728.1267 | 348218004.5498 | 349168280.9728 | 350118557.3959 | 351068833.819 | 352019110.242 | 352969386.6651 | 353919663.0882 | 354869939.5112 | 355820215.9343
VIC
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
V2 | Murray River | Option 1 | 911780584.22 | 917606384.6322 | 932461848.4317 | 948753041.1813 | 960995028.5902 | 967443385.4344 | 974685770.2671 | 981434235.0494 | 987824448.9404 | 994541169.1528 | 996361505.2902 | 998215242.0908 | 1000102379.5544 | 1002022917.681 | 1003968506.305 | 1005955845.7578 | 1007976585.8737 | 1010030726.6527 | 1012118268.0947 | 1014180759.0395 | 1016251600.15 | 1018322441.2605 | 1020384932.2052 | 1022455773.3157 | 1024526614.4262 | 1026597455.5367 | 1028668296.6472 | 1030739137.7577 | 1032809978.8682 | 1034880819.9788 | 1036951661.0893 | 1039022502.1998 | 1041093343.3103
V3 | Western Victoria | See V3-EAST secondary transmission limit constraint augmentations
V4 | South West Victoria | Preparatory Activities- See note below
V5 | Gippsland | See SEVIC1 transmission costs
V6 | Central North Vic | Option 1 | 708512452.43 | 712907629.5687 | 725275385.5944 | 739216226.9498 | 750540859.9735 | 756068386.3896 | 762252153.2848 | 768035697.1266 | 773524009.3627 | 778995062.9297 | 781160352.309 | 783365371.7686 | 785610121.3086 | 787894600.9289 | 790208878.1095 | 792572817.8905 | 794976487.7519 | 797419887.6937 | 799903017.7158 | 802356350.1776 | 804819615.1595 | 807282880.1414 | 809736212.6033 | 812199477.5852 | 814662742.5671 | 817126007.549 | 819589272.531 | 822052537.5129 | 824515802.4948 | 826979067.4767 | 829442332.4586 | 831905597.4406 | 834368862.4225
|  | Option 2 | 1109535637.78 | 1119103762.356 | 1138559438.9351 | 1161532266.583 | 1179901684.5623 | 1188712687.8437 | 1198364693.6808 | 1207577906.2212 | 1216500038.1019 | 1225923621.9842 | 1229541448.2463 | 1233225656.6417 | 1236976247.1703 | 1240793219.8322 | 1244659979.094 | 1248609716.0223 | 1252625835.0839 | 1256708336.2788 | 1260857219.6069 | 1264956316.335 | 1269072008.5965 | 1273187700.858 | 1277286797.5861 | 1281402489.8476 | 1285518182.1091 | 1289633874.3706 | 1293749566.632 | 1297865258.8935 | 1301980951.155 | 1306096643.4165 | 1310212335.678 | 1314328027.9394 | 1318443720.2009
|  | Option 3 | 1076547652.47 | 1083019977.9782 | 1100424894.4022 | 1120177068.61 | 1135264939.6981 | 1142916743.3972 | 1151588069.3604 | 1159708826.0175 | 1167428282.0021 | 1173415530.7185 | 1175904153.0033 | 1178438438.0823 | 1181018385.9555 | 1183643996.6229 | 1186303854.386 | 1189020790.6419 | 1191783389.6919 | 1194591651.5362 | 1197445576.1747 | 1200265253.7176 | 1203096346.959 | 1205927440.2004 | 1208747117.7432 | 1211578210.9846 | 1214409304.226 | 1217240397.4674 | 1220071490.7088 | 1222902583.9503 | 1225733677.1917 | 1228564770.4331 | 1231395863.6745 | 1234226956.9159 | 1237058050.1573
V7 | Gippsland Coast | Option 1 | 683642065.32 | 687274431.7386 | 699091025.4306 | 711959377.7071 | 720980072.358 | 725191081.1514 | 730220837.8439 | 735090497.7874 | 739855514.1029 | 742626690.6645 | 744035390.8908 | 745469938.8276 | 746930334.475 | 748416577.833 | 749922206.9739 | 751460145.7531 | 753023932.2428 | 754613566.4431 | 756229048.3539 | 757825144.4819 | 759427702.5374 | 761030260.593 | 762626356.7209 | 764228914.7765 | 765831472.8321 | 767434030.8876 | 769036588.9432 | 770639146.9988 | 772241705.0544 | 773844263.1099 | 775446821.1655 | 777049379.2211 | 778651937.2766
|  | Option 2 | 683642065.32 | 687274431.7386 | 699091025.4306 | 711959377.7071 | 720980072.358 | 725191081.1514 | 730220837.8439 | 735090497.7874 | 739855514.1029 | 742626690.6645 | 744035390.8908 | 745469938.8276 | 746930334.475 | 748416577.833 | 749922206.9739 | 751460145.7531 | 753023932.2428 | 754613566.4431 | 756229048.3539 | 757825144.4819 | 759427702.5374 | 761030260.593 | 762626356.7209 | 764228914.7765 | 765831472.8321 | 767434030.8876 | 769036588.9432 | 770639146.9988 | 772241705.0544 | 773844263.1099 | 775446821.1655 | 777049379.2211 | 778651937.2766
V8 | Portland Coast | Preparatory Activities- See note below
SWV1 | Group Constraint - South West Victoria | Option 1 | Preparatory Activities- See note below
Option 1A
Option 1B
Option 1C
Option 2A
Option 2B
Option 3A
Option 3B
SEVIC1 | Transmission Limit Constraint - Gippsland | Option 1 | 297826370.14 | 296703663.7769 | 300594254.3187 | 304773040.3202 | 307235743.059 | 308090945.7403 | 309515350.975 | 310920498.542 | 312346273.9114 | 312646755.4185 | 312856163.5254 | 313069413.983 | 313286506.7911 | 313507441.9498 | 313731258.8715 | 313959878.7314 | 314192340.9419 | 314428645.5029 | 314668792.4146 | 314906057.5633 | 315144283.2996 | 315382509.036 | 315619774.1847 | 315857999.921 | 316096225.6574 | 316334451.3938 | 316572677.1301 | 316810902.8665 | 317049128.6028 | 317287354.3392 | 317525580.0755 | 317763805.8119 | 318002031.5482
|  | Option 2 | 946000546.8269 | 948379285.4152 | 959855872.5935 | 972385287.4732 | 980273663.7635 | 985054602.191 | 990846009.1504 | 996106299.6132 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069 | 1001016058.3069
V3-East | Secondary Transmission Limit - Western Victoria | Option 1 | 162993305.33 | 164443195.0905 | 167766374.7243 | 171736502.3288 | 175128148.8854 | 176598258.5397 | 178206854.6143 | 179761670.5194 | 181282149.8511 | 183066572.6848 | 183857177.0484 | 184662287.914 | 185481905.2817 | 186316029.1515 | 187161032.8979 | 188024169.7718 | 188901813.1479 | 189793963.026 | 190700619.4062 | 191596395.9099 | 192495799.039 | 193395202.1682 | 194290978.6718 | 195190381.801 | 196089784.9302 | 196989188.0594 | 197888591.1885 | 198787994.3177 | 199687397.4469 | 200586800.576 | 201486203.7052 | 202385606.8344 | 203285009.9636
Notes: AEMO received TNSP cost estimates for actionable projects and projects with preparatory activities from most TNSPs during June 2023. he Mid-north South Australia MN1 preparatory activities were removed from this table in July 2024 to reflect the updated options instead included in the South Australia options bove (as advised by ElectraNet).
Preparatory activities
REZ |  | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Darling Downs REZ Expansion(Stage 1) |  | 28000000 | 27783308.2799 | 28034824.1084 | 28342798.2019 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956
South East SA REZ |  | 34000000 | 34038777.6339 | 34797316.7324 | 35353840.0875 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043
South West Victoria REZ Option 1 |  | 64000000 | 64787970.2113 | 66218095.4211 | 67539462.0643 | 68388713.0716 | 68793750.1457 | 69243369.3162 | 69704525.7704 | 70179250.7902 | 70423854.5746 | 70530541.1554 | 70639185.2882 | 70749786.9729 | 70862346.2095 | 70976373.6102 | 71092847.9507 | 71211279.8432 | 71331669.2876 | 71454016.284 | 71574895.1164 | 71696263.3368 | 71817631.5572 | 71938510.3896 | 72059878.61 | 72181246.8303 | 72302615.0507 | 72423983.2711 | 72545351.4915 | 72666719.7119 | 72788087.9323 | 72909456.1527 | 73030824.3731 | 73152192.5935
South West Victoria REZ Option 1A |  | 725000000 | 729697708.087 | 742015660.4757 | 756241651.7104 | 767998397.7087 | 773686138.1486 | 780015731.9851 | 785949234.9909 | 791596322.797 | 797579400.3446 | 799893385.862 | 802249829.8293 | 804648732.2465 | 807090093.1135 | 809563297.8179 | 812089575.5846 | 814658311.8012 | 817269506.4676 | 819923159.5839 | 822544968.8629 | 825177392.7542 | 827809816.6456 | 830431625.9245 | 833064049.8159 | 835696473.7073 | 838328897.5987 | 840961321.49 | 843593745.3814 | 846226169.2728 | 848858593.1642 | 851491017.0556 | 854123440.9469 | 856755864.8383
South West Victoria REZ Option 1B |  | 1013000000 | 1018732811.9606 | 1036046847.7829 | 1055778305 | 1072268383.9111 | 1080261536.1315 | 1078175009.0763 | 1086429668.6812 | 1094226115.2313 | 1101906615.0519 | 1105180688.8021 | 1108514837.3 | 1111909060.5456 | 1115363358.5389 | 1118862712.593 | 1122437160.0817 | 1126071682.3182 | 1129766279.3023 | 1133520951.0342 | 1137230566.7053 | 1140955201.0633 | 1144679835.4213 | 1148389451.0924 | 1152114085.4504 | 1155838719.8084 | 1159563354.1665 | 1163287988.5245 | 1167012622.8825 | 1170737257.2405 | 1174461891.5985 | 1178186525.9565 | 1181911160.3145 | 1185635794.6726
South West Victoria REZ Option 1C |  | 1372000000 | 1380744730.821 | 1404306396.0524 | 1431534409.6202 | 1454216127.8266 | 1465158801.3188 | 1477327744.7844 | 1488713984.7083 | 1499528741.1873 | 1511316377.7567 | 1515897058.8808 | 1520561789.1997 | 1525310568.7137 | 1530143397.4225 | 1535039263.0276 | 1540040190.1263 | 1545125166.42 | 1550294191.9086 | 1555547266.5921 | 1560737304.3794 | 1565948354.4655 | 1571159404.5516 | 1576349442.3389 | 1581560492.425 | 1586771542.511 | 1591982592.5971 | 1597193642.6832 | 1602404692.7692 | 1607615742.8553 | 1612826792.9414 | 1618037843.0275 | 1623248893.1135 | 1628459943.1996
South West Victoria REZ Option 2A |  | 618000000 | 621792618.5112 | 632381450.9936 | 644572522.8511 | 654641877.5516 | 659483265.7192 | 664899044.1753 | 669973333.8035 | 674797792.4712 | 679959601.4989 | 681955682.2911 | 683988388.4189 | 686057719.8823 | 688163676.6814 | 690297102.4822 | 692476309.9526 | 694692142.7585 | 696944600.9002 | 699233684.3774 | 701495298.8529 | 703766069.6624 | 706036840.4718 | 708298454.9474 | 710569225.7568 | 712839996.5662 | 715110767.3757 | 717381538.1851 | 719652308.9945 | 721923079.804 | 724193850.6134 | 726464621.4229 | 728735392.2323 | 731006163.0417
South West Victoria REZ Option 2B |  | 803000000 | 807836498.45 | 821220911.3363 | 836150144.9242 | 847696390.632 | 853460024.6355 | 859999704.2978 | 866139488.4017 | 871984547.0685 | 876875453.7255 | 878846794.9473 | 880854307.5677 | 882897991.5867 | 884977847.0042 | 887084830.9706 | 889237029.1853 | 891425398.7985 | 893649939.8103 | 895910652.2206 | 898144236.0821 | 900386862.7931 | 902629489.5042 | 904863073.3656 | 907105700.0767 | 909348326.7878 | 911590953.4988 | 913833580.2099 | 916076206.921 | 918318833.632 | 920561460.3431 | 922804087.0542 | 925046713.7653 | 927289340.4763
South West Victoria REZ Option 3A |  | 1076000000 | 1082659353.7656 | 1089847516.8702 | 1111072730.4221 | 1128974900.7559 | 1137555480.7623 | 1147101567.8194 | 1156023468.4644 | 1164486011.4098 | 1173412365.8439 | 1177110680.7302 | 1180876854.6051 | 1184710887.4689 | 1188612779.3213 | 1192565565.4154 | 1196603175.2453 | 1200708644.064 | 1204881971.8714 | 1209123158.6676 | 1213313451.2222 | 1217520708.5239 | 1221727965.8257 | 1225918258.3803 | 1230125515.6821 | 1234332772.9839 | 1238540030.2857 | 1242747287.5875 | 1246954544.8893 | 1251161802.1911 | 1255369059.4928 | 1259576316.7946 | 1263783574.0964 | 1267990831.3982
South West Victoria REZ Option 3B |  | 1325000000 | 1333149471.9042 | 1354977743.4173 | 1379893790.4397 | 1399866877.8393 | 1409810194.5078 | 1420970380.9835 | 1431398070.3572 | 1441283751.6827 | 1450469411.0607 | 1454129521.2617 | 1457856789.448 | 1461651215.6196 | 1465512799.7766 | 1469424752.4225 | 1473420652.5502 | 1477483710.6631 | 1481613926.7614 | 1485811300.8451 | 1489958306.4398 | 1494122101.5307 | 1498285896.6217 | 1502432902.2164 | 1506596697.3074 | 1510760492.3983 | 1514924287.4893 | 1519088082.5803 | 1523251877.6713 | 1527415672.7623 | 1531579467.8533 | 1535743262.9443 | 1539907058.0352 | 1544070853.1262
Progressive Change Scenario | bar: 2031-32 to 2053-54
QLD | bar: 2032-33 to 2053-54
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Q1 | Far North QLD | Option 1 | 1836460949.12 | 1840509947.3547 | 1867338369.8277 | 1895989521.1736 | 1919762563.4121 | 1926160929.7971 | 1929310781.8074 | 1932393484.3186 | 1935548474.405 | 1938777572.0094 | 1942077540.7987 | 1945449424.1393 | 1948893924.985 | 1952411745.737 | 1955989151.0049 | 1959654853.5489 | 1963396916.6911 | 1967215345.7975 | 1971110890.9434 | 1974982211.2073 | 1978880655.273 | 1982795321.8212 | 1986710853.7508 | 1990655480.1374 | 1994616797.143 | 1998593956.7842 | 2002586980.5154 | 2006595957.4282 | 2010620982.6421 | 2014662152.4656 | 2018719564.0128 | 2022793315.1801 | 2026883504.6504
|  | Option 2 | 2780404941.45 | 2787008577.506 | 2829626637.5262 | 2873316623.4515 | 2907958882.2277 | 2915706084.1581 | 2920211849.8212 | 2924836449.3907 | 2929565273.6127 | 2934389585.3877 | 2939303141.6146 | 2944306854.8365 | 2949400725.0534 | 2954584752.2652 | 2959836397.2234 | 2965200738.4252 | 2970655236.6221 | 2976199891.8139 | 2981834704.0007 | 2987401898.4413 | 2992991632.1306 | 2998581365.82 | 3004148560.2605 | 3009738293.9499 | 3015328027.6392 | 3020917761.3285 | 3026507495.0178 | 3032097228.7072 | 3037686962.3965 | 3043276696.0858 | 3048866429.7752 | 3054456163.4645 | 3060045897.1538
Q2 | North Qld Clean Energy Hub | 2021-22: CopperString; 2022-23: Anticipated
|  | Option 1 | 651469275.09 | 652700510.9376 | 662339271.2732 | 671732473.9855 | 678734095.8021 | 680073190.5893 | 680699017.9933 | 681341350.8064 | 681998159.8895 | 682668231.6921 | 683350699.0853 | 684045688.8159 | 684753200.884 | 685473235.2896 | 686202661.4483 | 686947740.5289 | 687705341.947 | 688475465.7025 | 689258111.7956 | 690031366.1355 | 690807751.0598 | 691584135.9841 | 692357390.3241 | 693133775.2484 | 693910160.1727 | 694686545.097 | 695462930.0213 | 696239314.9456 | 697015699.8699 | 697792084.7942 | 698568469.7185 | 699344854.6428 | 700121239.5671
Q3 | Northern Qld | 2021-22: See NQ-CQ subregional augmentations
Q4 | Isaac | 2021-22: See NQ2 group constraint augmentations
Q5 | Barcaldine | Option 1 | 1068420080.45 | 1066891118.0219 | 1080128369.428 | 1080560292.2772 | 1087376309.251 | 1087437112.2408 | 1086829480.9807 | 1086205824.2155 | 1085568112.0878 | 1084917522.8484 | 1084254898.4295 | 1083580115.7643 | 1082893174.8529 | 1082194075.6953 | 1081485857.853 | 1080762442.203 | 1080026868.3067 | 1079279136.1642 | 1078519245.7755 | 1077768474.0715 | 1077014662.8059 | 1076260851.5403 | 1075510079.8363 | 1074756268.5707 | 1074002457.3051 | 1073248646.0395 | 1072494834.7739 | 1071741023.5083 | 1070987212.2427 | 1070233400.9771 | 1069479589.7115 | 1068725778.4459 | 1067971967.1803
Q6 | Fitzroy | 2021-22: See CQ-GG subregional augmentations
Q7 | Wide Bay | 2021-22: See SQ1 group constraint augmentations
Q8 | Darling Downs | 2021-22: Preparatory Activities- See note below
Q9 | Banana | Option 1 | 1078371762.27 | 1072548800.2958 | 1088460048.8349 | 1105428244.3114 | 1117615093.71 | 1119782050.8264 | 1121077881.4268 | 1122407887.9675 | 1123767868.8859 | 1125155311.4233 | 1126568420.1224 | 1128007457.4214 | 1129472423.3204 | 1130963317.8194 | 1132473658.7683 | 1134016410.4673 | 1135585090.7662 | 1137179699.6651 | 1138800237.164 | 1140401328.213 | 1142008901.4119 | 1143616474.6108 | 1145217565.6597 | 1146825138.8586 | 1148432712.0575 | 1150040285.2564 | 1151647858.4553 | 1153255431.6542 | 1154863004.8531 | 1156470578.052 | 1158078151.2509 | 1159685724.4498 | 1161293297.6488
|  | Option 2 | 413993266.52 | 415972385.1915 | 422971745.2715 | 429884999.933 | 434869020.1538 | 435947187.2324 | 436501755.1461 | 437070949.075 | 437652970.9486 | 438246745.3906 | 438851504.0037 | 439467359.1052 | 440094310.695 | 440732358.7731 | 441378729.2174 | 442038970.2722 | 442710307.8152 | 443392741.8466 | 444086272.3663 | 444771480.5197 | 445459462.7953 | 446147445.0708 | 446832653.2242 | 447520635.4998 | 448208617.7753 | 448896600.0508 | 449584582.3263 | 450272564.6019 | 450960546.8774 | 451648529.1529 | 452336511.4285 | 453024493.704 | 453712475.9795
|  | Option 3 | 663241042.44 | 665451267.4768 | 676039252.5965 | 686867674.2085 | 695257486.2025 | 697319801.511 | 698403711.9748 | 699516209.2183 | 700653778.8319 | 701814319.0146 | 702996327.8985 | 704200025.0187 | 705425410.3754 | 706672483.9684 | 707935823.7388 | 709226273.8046 | 710538412.1069 | 711872238.6455 | 713227753.4206 | 714567002.0183 | 715911672.6752 | 717256343.332 | 718595591.9298 | 719940262.5866 | 721284933.2435 | 722629603.9003 | 723974274.5572 | 725318945.214 | 726663615.8709 | 728008286.5277 | 729352957.1846 | 730697627.8414 | 732042298.4983
NQ2 | Group constraint - Facilitating power to Central Queensland | Option 1 | 173333535.69 | 173537087.36 | 176680169.51 | 179174943.14 | 180727275.42 | 180713877.8811 | 180700048.5535 | 180685854.4939 | 180671340.5428 | 180656533.5169 | 180641452.5768 | 180626094.9223 | 180610460.5532 | 180594549.4697 | 180578430.8503 | 180561966.3377 | 180545225.1107 | 180528207.1692 | 180510912.5132 | 180493825.393 | 180476669.0942 | 180459512.7955 | 180442425.6753 | 180425269.3765 | 180408113.0777 | 180390956.779 | 180373800.4802 | 180356644.1814 | 180339487.8826 | 180322331.5839 | 180305175.2851 | 180288018.9863 | 180270862.6875
|  | Option 2 | 1007783813.12 | 1008038253.7148 | 1021051360.2668 | 1032520088.7934 | 1040123938.7591 | 1040913647.7024 | 1040679824.1749 | 1040439833.8453 | 1040194434.8512 | 1039944080.5978 | 1039689095.0668 | 1039429430.9021 | 1039165088.1039 | 1038896066.6721 | 1038623536.2651 | 1038345157.5661 | 1038062100.2335 | 1037774364.2672 | 1037481949.6674 | 1037193044.0428 | 1036902968.7598 | 1036612893.4768 | 1036323987.8522 | 1036033912.5692 | 1035743837.2862 | 1035453762.0032 | 1035163686.7202 | 1034873611.4372 | 1034583536.1542 | 1034293460.8712 | 1034003385.5882 | 1033713310.3052 | 1033423235.0221
SQ1 | Group Constraint - Wide Bay | Option 1 | 536895468.1127 | 538132049.0398 | 545570177.645 | 552673588.8889 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049 | 557503794.049
|  | Option 2 | 583066283.0134 | 585656817.1795 | 594817859.4493 | 605105160.064 | 613599306.4407 | 614819325.4599 | 616125571.7495 | 617466268.6406 | 618837180.8268 | 620235775.3895 | 621660242.4054 | 623110846.4307 | 624587587.4655 | 626090465.5097 | 627612946.3111 | 629168098.3743 | 630749387.4469 | 632356813.5291 | 633990376.6206 | 635604336.9551 | 637224831.542 | 638845326.1288 | 640459286.4633 | 642079781.0502 | 643700275.637 | 645320770.2239 | 646941264.8107 | 648561759.3976 | 650182253.9844 | 651802748.5713 | 653423243.1581 | 655043737.745 | 656664232.3318
|  | Option 3 | 110057013.87 | 110871562.9718 | 110568687.3193 | 112940289.5849 | 113959388.5844 | 113990272.3888 | 114014923.2454 | 114040224.2325 | 114066095.3945 | 114092489.0052 | 114119370.856 | 114146745.9519 | 114174614.2927 | 114202975.8785 | 114231707.398 | 114261055.4737 | 114290896.7944 | 114321231.36 | 114352059.1706 | 114382517.0475 | 114413098.2357 | 114443679.4238 | 114474137.3007 | 114504718.4889 | 114535299.677 | 114565880.8651 | 114596462.0533 | 114627043.2414 | 114657624.4296 | 114688205.6177 | 114718786.8059 | 114749367.994 | 114779949.1821
SWQLD1 | Transmission Limit Constraint - Darling Downs | 2021-22: Option 1; 2022-23: Preparatory Activities- See note below
|  | Option 2 | Non-network projects are not estimated in capital costs
|  | Option 3 | 184026844.16 | 183493336.2729 | 186887794.4916 | 189822632.1016 | 191163843.7508 | 191187408.2812 | 191205285.7448 | 191223634.6982 | 191242397.1955 | 191261538.5924 | 191281034.0538 | 191300887.2301 | 191321098.1212 | 191341666.7273 | 191362503.6195 | 191383787.6553 | 191405429.406 | 191427428.8716 | 191449786.0521 | 191471874.9464 | 191494053.2695 | 191516231.5925 | 191538320.4869 | 191560498.8099 | 191582677.1329 | 191604855.456 | 191627033.779 | 191649212.1021 | 191671390.4251 | 191693568.7482 | 191715747.0712 | 191737925.3943 | 191760103.7173
NSW | bar: 2032-33 to 2053-54
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
N1 | North West NSW | Option 1 | 4683570694.16 | 4703516536.5876 | 4775599569.9091 | 4855161748.7584 | 4914331441.0457 | 4943931629.3408 | 4951953872.5155 | 4960187692.3482 | 4968607078.0332 | 4977196473.3888 | 4985944763.1189 | 4994853571.9266 | 5003922899.8119 | 5013152746.7748 | 5022502983.0459 | 5032053868.1641 | 5041765272.3599 | 5051637195.6333 | 5061669637.9843 | 5071581691.0271 | 5081533873.8393 | 5091486056.6515 | 5101398109.6943 | 5111350292.5065 | 5121302475.3187 | 5131254658.1309 | 5141206840.9431 | 5151159023.7553 | 5161111206.5675 | 5171063389.3797 | 5181015572.1918 | 5190967755.004 | 5200919937.8162
N2 | New England | Option 1 | 370392725.98 | 372722679.4855 | 379824215.2964 | 386767380.232 | 391487462.1087 | 393860481.7591 | 394436385.685 | 395027478.3295 | 395631892.4747 | 396248511.3138 | 396876536.9405 | 397516085.9732 | 398167158.4119 | 398829754.2566 | 399500992.6557 | 400186635.3124 | 400883801.3751 | 401592490.8437 | 402312703.7184 | 403024274.0385 | 403738725.2102 | 404453176.3819 | 405164746.702 | 405879197.8737 | 406593649.0453 | 407308100.217 | 408022551.3887 | 408737002.5603 | 409451453.732 | 410165904.9036 | 410880356.0753 | 411594807.2469 | 412309258.4186
|  | Option 2 | 1004401782 | 1011204959.0609 | 1030510596.3865 | 1051698711.1525 | 1067967373.7034 | 1075596168.6832 | 1078515264.3075 | 1081511347.3945 | 1084574953.3796 | 1087700421.6109 | 1090883707.588 | 1094125402.4821 | 1097425506.2932 | 1100784019.0214 | 1104186338.4373 | 1107661668.9995 | 1111195408.4786 | 1114787556.8748 | 1118438114.188 | 1122044864.8135 | 1125666217.6682 | 1129287570.5229 | 1132894321.1483 | 1136515674.003 | 1140137026.8577 | 1143758379.7124 | 1147379732.5671 | 1151001085.4218 | 1154622438.2765 | 1158243791.1312 | 1161865143.9859 | 1165486496.8406 | 1169107849.6953
|  | Option 3 | 647203680.09 | 651990774.0912 | 664965036.4824 | 679100470.3607 | 690132640.2294 | 695774058.1403 | 697850856.5022 | 699982427.8054 | 702162038.3802 | 704385661.1058 | 706650418.3845 | 708956730.8426 | 711304598.4802 | 713694021.2972 | 716114610.4987 | 718587143.6746 | 721101232.0298 | 723656875.5645 | 726254074.2786 | 728820106.6082 | 731396527.7326 | 733972948.857 | 736538981.1865 | 739115402.3109 | 741691823.4353 | 744268244.5597 | 746844665.6841 | 749421086.8085 | 751997507.9329 | 754573929.0573 | 757150350.1817 | 759726771.3061 | 762303192.4305
N3 | Central-West Orana | 2021-22: Central West Orana REZ transmission link; 2022-23: Anticipated project
|  | Option 1 | 243410039.19 | 242986106.2847 | 247406498.6209 | 251298062.3826 | 253040851.2868 | 253049395.2256 | 253052066.7054 | 253054808.6575 | 253057612.3864 | 253060472.7512 | 253063386.0179 | 253066352.739 | 253069372.9146 | 253072446.5446 | 253075560.2654 | 253078740.8043 | 253081974.7976 | 253085262.2454 | 253088603.1475 | 253091903.9589 | 253095218.1338 | 253098532.3088 | 253101833.1202 | 253105147.2951 | 253108461.4701 | 253111775.6451 | 253115089.82 | 253118403.995 | 253121718.1699 | 253125032.3449 | 253128346.5199 | 253131660.6948 | 253134974.8698
|  | Option 2 | 329782042.82 | 331112953.9979 | 336959977.875 | 342841615.7431 | 346859456.104 | 348882236.8695 | 349384878.4672 | 349900776.5618 | 350428301.4916 | 350966478.5598 | 351514611.2999 | 352072801.5215 | 352641049.2245 | 353219354.409 | 353805202.7047 | 354403622.8521 | 355012100.481 | 355630635.5914 | 356259228.1833 | 356880277.6641 | 357503841.5152 | 358127405.3663 | 358748454.8471 | 359372018.6982 | 359995582.5494 | 360619146.4005 | 361242710.2516 | 361866274.1028 | 362489837.9539 | 363113401.805 | 363736965.6562 | 364360529.5073 | 364984093.3584
|  | Option 3 | 272858295.37 | 274691352.4723 | 280108848.3425 | 285335945.4057 | 288803657.6605 | 290652832.4664 | 291071512.05 | 291501233.7266 | 291940640.0711 | 292388919.2062 | 292845491.0041 | 293310440.2661 | 293783766.9923 | 294265471.1827 | 294753458.4713 | 295251917.59 | 295758754.173 | 296273968.2201 | 296797559.7314 | 297314868.1446 | 297834270.9238 | 298353673.703 | 298870982.1162 | 299390384.8954 | 299909787.6746 | 300429190.4538 | 300948593.233 | 301467996.0122 | 301987398.7914 | 302506801.5707 | 303026204.3499 | 303545607.1291 | 304065009.9083
N4 | Broken Hill | Option 1 | 5097859988.37 | 5117220290.9869 | 5184097635.6324 | 5254876296.3846 | 5302026055.4891 | 5322842024.5999 | 5324937932.0687 | 5327089116.5202 | 5329288782.2496 | 5331532865.0654 | 5333818460.9417 | 5336145994.3569 | 5338515465.3112 | 5340926873.8046 | 5343369735.4521 | 5345865019.0235 | 5348402240.1338 | 5350981398.7832 | 5353602494.9716 | 5356192138.0057 | 5358792265.4246 | 5361392392.8435 | 5363982035.8776 | 5366582163.2965 | 5369182290.7154 | 5371782418.1342 | 5374382545.5531 | 5376982672.972 | 5379582800.3909 | 5382182927.8098 | 5384783055.2286 | 5387383182.6475 | 5389983310.0664
|  | Option 2 | 4575560873.27 | 4636165564.5156 | 4728471231.6464 | 4819838797.8187 | 4879521590.2302 | 4905863199.4103 | 4911433141.1324 | 4917149983.245 | 4922995665.8804 | 4928959388.2988 | 4935033433.0625 | 4941218928.1888 | 4947515873.6778 | 4953924269.5293 | 4960416253.1529 | 4967047549.7298 | 4973790296.6693 | 4980644493.9714 | 4987610141.6362 | 4994492201.529 | 5001402124.0124 | 5008312046.4959 | 5015194106.3887 | 5022104028.8721 | 5029013951.3556 | 5035923873.8391 | 5042833796.3225 | 5049743718.806 | 5056653641.2894 | 5063563563.7729 | 5070473486.2563 | 5077383408.7398 | 5084293331.2232
N5 | South West NSW | Option 1 | 1418427595.46 | 1425333132.6532 | 1446268799.9947 | 1469948259.1294 | 1487141526.8051 | 1499961706.9097 | 1502125662.2986 | 1504346689.3887 | 1506617771.7764 | 1508934713.37 | 1511294515.8125 | 1513697617.3824 | 1516144018.0797 | 1518633717.9044 | 1521155892.0746 | 1523732190.1541 | 1526351787.3609 | 1529014683.6951 | 1531720879.1567 | 1534394600.2728 | 1537079146.1707 | 1539763692.0686 | 1542437413.1847 | 1545121959.0826 | 1547806504.9805 | 1550491050.8784 | 1553175596.7763 | 1555860142.6742 | 1558544688.5721 | 1561229234.47 | 1563913780.368 | 1566598326.2659 | 1569282872.1638
|  | Option 2 | 382536056.11 | 385148834.6005 | 391826524.704 | 399135083.8068 | 404725671.9348 | 410775536.6368 | 411650380.4869 | 412548297.2179 | 413466450.3433 | 414403143.382 | 415357164.2374 | 416328690.0626 | 417317720.8576 | 418324256.6224 | 419343921.1146 | 420385466.8191 | 421444517.4934 | 422521073.1375 | 423615133.7514 | 424696065.638 | 425781373.767 | 426866681.8961 | 427947613.7826 | 429032921.9117 | 430118230.0407 | 431203538.1697 | 432288846.2988 | 433374154.4278 | 434459462.5568 | 435544770.6859 | 436630078.8149 | 437715386.9439 | 438800695.073
|  | Option 3 | 299577968.52 | 301430153.3963 | 306774951.6487 | 312397961.749 | 316595939.3309 | 320834877.868 | 321458985.2946 | 322099552.7323 | 322754556.6966 | 323422786.8955 | 324103378.6355 | 324796458.2974 | 325502025.881 | 326220081.3865 | 326947502.8334 | 327690534.1826 | 328446053.4536 | 329214060.6464 | 329994555.7611 | 330765684.9344 | 331539936.0882 | 332314187.2419 | 333085316.4152 | 333859567.569 | 334633818.7228 | 335408069.8765 | 336182321.0303 | 336956572.184 | 337730823.3378 | 338505074.4916 | 339279325.6453 | 340053576.7991 | 340827827.9528
|  | Option 4 | 416523543.37 | 419592161.893 | 426784213.9669 | 435030044.9487 | 441723036.1004 | 450050317.2824 | 451211539.4401 | 452403387.3831 | 453622096.0354 | 454865413.6431 | 456131731.2636 | 457421284.0697 | 458734072.0616 | 460070095.2391 | 461423544.8059 | 462806038.3548 | 464211767.0894 | 465640731.0097 | 467092930.1158 | 468527702.8325 | 469968284.3457 | 471408865.8588 | 472843638.5756 | 474284220.0887 | 475724801.6019 | 477165383.1151 | 478605964.6282 | 480046546.1414 | 481487127.6546 | 482927709.1677 | 484368290.6809 | 485808872.1941 | 487249453.7072
|  | Option 5 | 1046609662.37 | 1052952433.5506 | 1071323633.6956 | 1091127653.5852 | 1093303952.6366 | 1106833292.1862 | 1109274225.9028 | 1111779536.1076 | 1114341308.6141 | 1116954810.0754 | 1119616658.4561 | 1122327348.0914 | 1125086878.9814 | 1127895251.1261 | 1130740254.2119 | 1133646308.866 | 1136601204.7747 | 1139604941.9382 | 1142657520.3564 | 1145673467.8335 | 1148701625.6244 | 1151729783.4152 | 1154745730.8923 | 1157773888.6831 | 1160802046.474 | 1163830204.2648 | 1166858362.0556 | 1169886519.8464 | 1172914677.6372 | 1175942835.4281 | 1178970993.2189 | 1181999151.0097 | 1185027308.8005
SWNSW1 | Secondary Transmission Limit - South West NSW | Option 1 | 167000000 | 168033762.58 | 170734660.18 | 174001675.03 | 176856490.5 | 177382316.99 | 177925090.34 | 178482178.64 | 179051822.06 | 179632968.1 | 180224864.7 | 180827621.78 | 181441239.36 | 182065717.42 | 182698340.85 | 183344539.88 | 184001599.41 | 184669519.42 | 185348299.93 | 186018935.06 | 186692285.32 | 187365635.58 | 188036270.71 | 188709620.97 | 189382971.23 | 190056321.49 | 190729671.75 | 191403022.01 | 192076372.26 | 192749722.52 | 193423072.78 | 194096423.04 | 194769773.3
N6 | Wagga Wagga | 2021-22: Option 1; 2022-23: Refer to Forecasted Transmission flow paths (SNSW-CNSW) Option 3 and 4 in the flow paths
N7 | Tumut | 2021-22: Option 1; 2022-23: Refer to Forecasted Flow Paths Preparatory Activities for HumeLink forecasted costs
N8 | Cooma-Monaro | Option 1 | 201643435.92 | 203332481.0995 | 206890562.8612 | 211157393.3218 | 214743970.033 | 217299698.1725 | 217980946.4755 | 218680161.8773 | 219395135.4795 | 220124546.308 | 220867450.4414 | 221623985.8434 | 222394152.5138 | 223177950.4528 | 223971971.8431 | 224783032.3191 | 225607724.0635 | 226446047.0765 | 227298001.358 | 228139732.1881 | 228984870.8353 | 229830009.4825 | 230671740.3126 | 231516878.9598 | 232362017.6071 | 233207156.2543 | 234052294.9015 | 234897433.5487 | 235742572.196 | 236587710.8432 | 237432849.4904 | 238277988.1376 | 239123126.7848
|  | Option 2 | 512954346.52 | 515746313.3228 | 525094845.7586 | 535570829.7798 | 544188611.3109 | 549976909.4783 | 551586854.0296 | 553239258.8196 | 554928903.8983 | 556652667.3771 | 558408318.6079 | 560196183.6227 | 562016262.4216 | 563868555.0045 | 565745007.9255 | 567661728.0765 | 569610662.0116 | 571591809.7307 | 573605171.2339 | 575594372.3991 | 577591627.0102 | 579588881.6214 | 581578082.7865 | 583575337.3977 | 585572592.0088 | 587569846.62 | 589567101.2311 | 591564355.8423 | 593561610.4534 | 595558865.0646 | 597556119.6758 | 599553374.2869 | 601550628.8981
N9 | Hunter-Central Coast | Option 1 | 307063934.91 | 308253314.129 | 314822944.1075 | 320875605.7198 | 325062966.3844 | 327405865.1628 | 327985774.0068 | 328580977.2481 | 329189594.5881 | 329810501.5121 | 330442894.5458 | 331086891.1214 | 331742491.2388 | 332409694.8982 | 333085601.214 | 333776011.9572 | 334478026.2423 | 335191644.0693 | 335916865.4382 | 336633384.1506 | 337352803.7486 | 338072223.3465 | 338788742.059 | 339508161.6569 | 340227581.2549 | 340947000.8528 | 341666420.4508 | 342385840.0487 | 343105259.6467 | 343824679.2446 | 344544098.8425 | 345263518.4405 | 345982938.0384
|  | Option 1A | 283129029.82 | 284209281.0283 | 290165004.845 | 295750949.6598 | 299736762.1003 | 302100689.8091 | 302685490.7338 | 303285715.0785 | 303899466.6825 | 304525611.5448 | 305163339.413 | 305812768.71 | 306473899.4357 | 307146731.5903 | 307828339.8164 | 308524574.8284 | 309232511.2693 | 309952149.1389 | 310683488.4373 | 311406051.6641 | 312131540.2481 | 312857028.8321 | 313579592.0589 | 314305080.6429 | 315030569.2269 | 315756057.8109 | 316481546.3949 | 317207034.9789 | 317932523.5629 | 318658012.1469 | 319383500.7309 | 320108989.315 | 320834477.899
|  | Option 1AB | 274506774.68 | 275601709.743 | 281315034.7185 | 286692285.0328 | 290389108.8419 | 292434719.7316 | 292946744.658 | 293472273.5924 | 294009646.4131 | 294557870.179 | 295116235.4981 | 295684846.0524 | 296263701.842 | 296852802.8667 | 297449587.8179 | 298059179.3131 | 298679016.0435 | 299309098.0091 | 299949425.21 | 300582068.4844 | 301217273.0676 | 301852477.6508 | 302485120.9253 | 303120325.5085 | 303755530.0917 | 304390734.6749 | 305025939.2582 | 305661143.8414 | 306296348.4246 | 306931553.0078 | 307566757.5911 | 308201962.1743 | 308837166.7575
|  | Option 1B | 298259423 | 299459028.064 | 305779139.5944 | 311618137.0481 | 315516202.7148 | 317546057.248 | 318054134.4645 | 318575611.5732 | 319108841.2519 | 319652838.2149 | 320206898.54 | 320771125.1095 | 321345517.9235 | 321930076.982 | 322522260.7239 | 323127152.2714 | 323742210.0634 | 324367434.0998 | 325002824.3808 | 325630589.9784 | 326260897.1372 | 326891204.2959 | 327518969.8935 | 328149277.0523 | 328779584.211 | 329409891.3697 | 330040198.5285 | 330670505.6872 | 331300812.8459 | 331931120.0047 | 332561427.1634 | 333191734.3222 | 333822041.4809
|  | Option 2 | 58512971.63 | 59264516.4723 | 60463128.6463 | 61586003.0683 | 62132057.9819 | 62167612.5084 | 62175899.5388 | 62184405.1392 | 62193102.4072 | 62201975.3346 | 62211012.3783 | 62220215.2393 | 62229583.9177 | 62239118.4134 | 62248777.272 | 62258643.4023 | 62268675.3499 | 62278873.1149 | 62289236.6971 | 62299475.9164 | 62309756.59 | 62320037.2636 | 62330276.4829 | 62340557.1564 | 62350837.83 | 62361118.5036 | 62371399.1772 | 62381679.8508 | 62391960.5244 | 62402241.198 | 62412521.8716 | 62422802.5452 | 62433083.2188
|  | Option 2A | 106104649.48 | 106707980.5659 | 108923877.3679 | 110857310.8401 | 111741595.0292 | 111773159.0131 | 111781417.8684 | 111789894.5507 | 111798562.2489 | 111807405.0092 | 111816411.3279 | 111825582.9002 | 111834919.726 | 111844421.8054 | 111854047.825 | 111863880.4115 | 111873878.2515 | 111884041.3451 | 111894369.6923 | 111904574.0993 | 111914819.8197 | 111925065.5401 | 111935269.9471 | 111945515.6674 | 111955761.3878 | 111966007.1082 | 111976252.8286 | 111986498.549 | 111996744.2694 | 112006989.9898 | 112017235.7101 | 112027481.4305 | 112037727.1509
N10 | Hunter Coast | 2021-22: Option 1; 2022-23: Refer to Forecasted Transmission flow paths CNSW-SNW Option 1
N11 | Illawarra Coast | 2021-22: Option 1; 2022-23: Refer to N12 forecasted costs
N12 | Illawarra | Option 1 | 813815319.22 | 817811736.6265 | 832369006.0704 | 848481785.9113 | 860767680.5083 | 865922379.5144 | 868036471.4127 | 870206319.8907 | 872425070.2908 | 874688623.1311 | 876994049.2121 | 879341776.689 | 881731805.562 | 884164135.8309 | 886628192.1468 | 889145125.2077 | 891704359.6646 | 894305895.5174 | 896949732.7663 | 899561843.9681 | 902184530.519 | 904807217.0698 | 907419328.2717 | 910042014.8225 | 912664701.3734 | 915287387.9242 | 917910074.4751 | 920532761.0259 | 923155447.5767 | 925778134.1276 | 928400820.6784 | 931023507.2293 | 933646193.7801
SA | bar: 2032-33 to 2053-54
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
S1 | South East SA | 2021-22: See S1-TBMO transmission limit constraint augmentation and VIC-SESA and SESA-SA sub-regional augmentations
S2 | Riverland | Option 1 | 99500441.64 | 100015326.3701 | 102255314.0525 | 104140918.1788 | 104990385.2527 | 105006911.1628 | 105018721.1874 | 105030842.7032 | 105043237.3665 | 105055882.3674 | 105068761.2532 | 105081876.4489 | 105095227.9544 | 105108815.7698 | 105122580.8175 | 105136641.2526 | 105150937.9974 | 105165471.0521 | 105180240.4166 | 105194832.5488 | 105209483.7584 | 105224134.968 | 105238727.1002 | 105253378.3098 | 105268029.5194 | 105282680.729 | 105297331.9386 | 105311983.1482 | 105326634.3578 | 105341285.5674 | 105355936.777 | 105370587.9866 | 105385239.1962
S3 | Mid-North SA | 2021-22: Preparatory Activities- See note below
S4 | Yorke Peninsula | Option 1 | 566404537.76 | 570696903.5072 | 581508795.7762 | 594089057.7387 | 604710524.5661 | 607895080.7776 | 610050372.4273 | 612262507.1503 | 614524496.8339 | 616832162.0664 | 619182516.578 | 621575996.8605 | 624012602.9138 | 626492334.738 | 629004410.8903 | 631570394.2562 | 634179503.3929 | 636831738.3005 | 639527098.979 | 642190115.3293 | 644863913.1224 | 647537710.9154 | 650200727.2657 | 652874525.0587 | 655548322.8518 | 658222120.6448 | 660895918.4378 | 663569716.2309 | 666243514.0239 | 668917311.8169 | 671591109.61 | 674264907.403 | 676938705.196
|  | Option 2 | 155991705.95 | 156381664.364 | 159528033.9236 | 162082678.663 | 163576920.6052 | 163589852.1385 | 163599537.2171 | 163609477.6926 | 163619642.2094 | 163630011.9695 | 163640573.5663 | 163651328.9539 | 163662278.1323 | 163673421.1015 | 163684709.4137 | 163696239.9644 | 163707964.3059 | 163719882.4381 | 163731994.3611 | 163743960.941 | 163755975.9686 | 163767990.9963 | 163779957.5762 | 163791972.6038 | 163803987.6314 | 163816002.659 | 163828017.6866 | 163840032.7142 | 163852047.7419 | 163864062.7695 | 163876077.7971 | 163888092.8247 | 163900107.8523
S5 | Northern SA | 2021-22: See NSA1 group constraint augmentations
S6 | Leigh Creek | Option 1 | 837712569.5 | 839218469.7873 | 851149230.9977 | 862460157.7241 | 870039662.366 | 871286903.0261 | 871569185.5825 | 871858912.9629 | 872155169.9552 | 872457409.1646 | 872765239.4606 | 873078718.0189 | 873397844.8395 | 873722619.9224 | 874051631.2021 | 874387702.8096 | 874729422.6795 | 875076790.8117 | 875429807.2061 | 875778587.4039 | 876128779.6672 | 876478971.9306 | 876827752.1283 | 877177944.3916 | 877528136.655 | 877878328.9183 | 878228521.1816 | 878578713.445 | 878928905.7083 | 879279097.9716 | 879629290.235 | 879979482.4983 | 880329674.7616
S7 | Roxby Downs | Option 1 | 541633683.11 | 542220445.1562 | 549702732.8473 | 556080679.0094 | 559451194.7714 | 559570986.2403 | 559188482.9827 | 558795891.666 | 558394452.5306 | 557984907.2668 | 557567785.8642 | 557143010.8578 | 556710582.2478 | 556270500.034 | 555824677.6174 | 555369288.1962 | 554906245.1713 | 554435548.5426 | 553957198.3103 | 553484588.2807 | 553010064.8502 | 552535541.4197 | 552062931.3901 | 551588407.9596 | 551113884.5291 | 550639361.0986 | 550164837.6681 | 549690314.2376 | 549215790.8071 | 548741267.3766 | 548266743.9461 | 547792220.5156 | 547317697.0851
S8 | Eastern Eyre Peninsula | Option 1 | 100000000 | 100496072.7612 | 102452038.7764 | 104197512.9971 | 104989468.221 | 104992023.3415 | 104993088.497 | 104994181.7469 | 104995299.6377 | 104996440.1018 | 104997601.661 | 104998784.5332 | 104999988.7184 | 105001214.2166 | 105002455.6996 | 105003723.8239 | 105005013.2612 | 105006324.0115 | 105007656.0748 | 105008972.1533 | 105010293.5601 | 105011614.9669 | 105012931.0455 | 105014252.4523 | 105015573.8591 | 105016895.2659 | 105018216.6727 | 105019538.0795 | 105020859.4863 | 105022180.8931 | 105023502.2998 | 105024823.7066 | 105026145.1134
S9 | Western Eyre Peninsula | Option 1 | 862153003.45 | 864007756.3943 | 877129324.2573 | 890072347.5065 | 899533840.5815 | 901596031.1103 | 902503040.3828 | 903433970.8736 | 904385881.7619 | 905357014.2596 | 906346111.6428 | 907353357.6018 | 908378752.1367 | 909422295.2473 | 910479449.7899 | 911559290.0523 | 912657278.8905 | 913773416.3045 | 914907702.2944 | 916028376.8524 | 917153588.5543 | 918278800.2563 | 919399474.8143 | 920524686.5163 | 921649898.2182 | 922775109.9202 | 923900321.6221 | 925025533.3241 | 926150745.026 | 927275956.728 | 928401168.43 | 929526380.1319 | 930651591.8339
|  | Option 2 | 423873320.8 | 425180907.6311 | 431655287.5424 | 438197699.4761 | 443062682.8302 | 443547029.4984 | 444045800.4361 | 444557725.8157 | 445081188.4808 | 445615221.2488 | 446159133.0301 | 446713024.8441 | 447276896.6908 | 447850748.5702 | 448432085.4741 | 449025897.4188 | 449629689.3963 | 450243461.4064 | 450867213.4492 | 451483480.4675 | 452102242.4939 | 452721004.5204 | 453337271.5387 | 453956033.5652 | 454574795.5916 | 455193557.6181 | 455812319.6445 | 456431081.671 | 457049843.6975 | 457668605.7239 | 458287367.7504 | 458906129.7768 | 459524891.8033
|  | Option 3 | 1058019572.74 | 1060439617.3493 | 1076390763.5875 | 1082428158.2165 | 1094667925.7616 | 1096003759.9865 | 1097381221.1967 | 1098795011.1763 | 1100240663.7983 | 1101715507.9771 | 1103217635.148 | 1104747324.2854 | 1106304575.3892 | 1107889388.4595 | 1109494873.0045 | 1111134810.0077 | 1112802308.9772 | 1114497369.9132 | 1116219992.8157 | 1117921944.2433 | 1119630786.1625 | 1121339628.0818 | 1123041579.5094 | 1124750421.4286 | 1126459263.3478 | 1128168105.2671 | 1129876947.1863 | 1131585789.1055 | 1133294631.0247 | 1135003472.944 | 1136712314.8632 | 1138421156.7824 | 1140129998.7017
S10 | South East SA Coast | 2021-22: See VIC-SESA and SESA-SA sub-regional augmentations
MN1 | Group Constraint - facilitating power out of mid-north SA | S3 Option 1 | n/a | 389000000 | 395956014.6589 | 404038315.4628 | 411052319.0509 | 413062687.6815 | 414460607.7708 | 415895396.227 | 417362520.5404 | 418859269.9972 | 420383707.6731 | 421936116.6825 | 423516497.0254 | 425124848.7018 | 426754178.8783 | 428418473.2217 | 430110738.8986 | 431830975.909 | 433579184.2529 | 435306414.0966 | 437040636.7738 | 438774859.4509 | 440502089.2947 | 442236311.9719 | 443970534.649 | 445704757.3262 | 447438980.0033 | 449173202.6805 | 450907425.3576 | 452641648.0348 | 454375870.7119 | 456110093.3891 | 457844316.0662
|  | S3 Option 1a | n/a | 70000000 | 70889492.2339 | 71774585.4716 | 72424467.9675 | 72530341.4172 | 72555130.6575 | 72580573.6734 | 72606590.1015 | 72633131.8691 | 72660164.6332 | 72687693.4113 | 72715718.2035 | 72744239.0096 | 72773131.8263 | 72802644.6604 | 72832653.5086 | 72863158.3709 | 72894159.2471 | 72924788.1128 | 72955540.9821 | 72986293.8513 | 73016922.717 | 73047675.5863 | 73078428.4555 | 73109181.3247 | 73139934.194 | 73170687.0632 | 73201439.9324 | 73232192.8017 | 73262945.6709 | 73293698.5402 | 73324451.4094
|  | S3 Option 1b | n/a | 350000000 | 355511059.866 | 361683855.6179 | 366833429.5391 | 368251828.7395 | 369096842.1771 | 369964141.7733 | 370850987.7312 | 371755741.4745 | 372677232.1516 | 373615630.9146 | 374570937.7635 | 375543152.6981 | 376528048.6971 | 377534079.8034 | 378557018.9955 | 379596866.2734 | 380653621.6372 | 381697695.9365 | 382745997.2574 | 383794298.5782 | 384838372.8776 | 385886674.1984 | 386934975.5193 | 387983276.8401 | 389031578.1609 | 390079879.4818 | 391128180.8026 | 392176482.1234 | 393224783.4443 | 394273084.7651 | 395321386.0859
|  | S3 Option 2 | 739957582.49 | 743130554.1843 | 756722888 | 771769599.784 | 784275537.2369 | 787714979.7566 | 790140799.7593 | 792630597.5878 | 795176508.2273 | 797773827.3603 | 800419194.1725 | 803113099.8254 | 805855544.3189 | 808646527.653 | 811473915.1175 | 814361976.1327 | 817298575.9886 | 820283714.685 | 823317392.222 | 826314665.6286 | 829324073.7454 | 832333481.8621 | 835330755.2687 | 838340163.3854 | 841349571.5022 | 844358979.6189 | 847368387.7356 | 850377795.8524 | 853387203.9691 | 856396612.0858 | 859406020.2026 | 862415428.3193 | 865424836.436
|  | S3 Option 3 | 1434153052.65 | 1438528056.6593 | 1462332903.443 | 1487405452.2763 | 1507791745.9453 | 1513301535.4818 | 1516541093.1631 | 1519866090.0779 | 1523266022.499 | 1526734608.6333 | 1530267359.769 | 1533864932.0264 | 1537527325.4055 | 1541254539.9064 | 1545030370.2486 | 1548887226.9931 | 1552808904.8592 | 1556795403.8472 | 1560846723.9568 | 1564849428.2252 | 1568868337.774 | 1572887247.3228 | 1576889951.5912 | 1580908861.14 | 1584927770.6888 | 1588946680.2376 | 1592965589.7864 | 1596984499.3352 | 1601003408.884 | 1605022318.4328 | 1609041227.9816 | 1613060137.5304 | 1617079047.0792
|  | S3 Option 4 | 1434203533.62 | 1437377125.2607 | 1460444360.9096 | 1484941724.0972 | 1505296108.1972 | 1510846007.9717 | 1514156463.307 | 1517554227.7424 | 1521028567.6765 | 1524573063.7469 | 1528183129.1105 | 1531859434.2055 | 1535601979.0319 | 1539410763.5897 | 1543269227.9462 | 1547210491.9669 | 1551217995.7191 | 1555291739.2027 | 1559431722.4178 | 1563522025.8343 | 1567628889.1837 | 1571735752.533 | 1575826055.9495 | 1579932919.2988 | 1584039782.6482 | 1588146645.9975 | 1592253509.3469 | 1596360372.6962 | 1600467236.0456 | 1604574099.3949 | 1608680962.7443 | 1612787826.0936 | 1616894689.443
NSA1 | Group Constraint - facilitating power out of north SA | Option 1 | 268254758.93 | 269325359.3583 | 274389761.0208 | 279267709.3452 | 282794373.4738 | 283603289.2232 | 284067806.6481 | 284544575.1199 | 285032088.5403 | 285529446.1526 | 286036004.3333 | 286551857.1595 | 287077004.6312 | 287611446.7484 | 288152859.8498 | 288705891.258 | 289268217.3118 | 289839838.0111 | 290420753.3559 | 290994697.7165 | 291570965.7386 | 292147233.7606 | 292721178.1213 | 293297446.1433 | 293873714.1654 | 294449982.1874 | 295026250.2094 | 295602518.2315 | 296178786.2535 | 296755054.2756 | 297331322.2976 | 297907590.3196 | 298483858.3417
|  | Option 2 | Refer to S8
S1-TBMO | Transmission Limit Constraint - | 2021-22: Option 1; 2022-23: Part of Preparatory activities
TAS | bar: 2032-33 to 2053-54
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
T1 | North East Tasmania | Option 1 | 400088757.45 | 402722474.9943 | 410267709.3161 | 418562567.5666 | 425246478.0824 | 427083933.9191 | 428304376.0034 | 429557005.6697 | 430837865.9348 | 432144590.1907 | 433475487.3598 | 434830804.6605 | 436210542.0927 | 437614699.6565 | 439037172.3189 | 440490170.1457 | 441967588.1041 | 443469426.1941 | 444995684.4156 | 446503627.5384 | 448017675.6941 | 449531723.8498 | 451039666.9726 | 452553715.1283 | 454067763.2841 | 455581811.4398 | 457095859.5955 | 458609907.7512 | 460123955.9069 | 461638004.0626 | 463152052.2183 | 464666100.374 | 466180148.5297
|  | Option 2 | 269281992.82 | 271051971.6828 | 276718386.2409 | 283022381.3927 | 288378296.6564 | 290159610.2383 | 291277034.3854 | 292423929.1854 | 293596671.6044 | 294793094.8113 | 296011650.5107 | 297252565.0302 | 298515838.3698 | 299801470.5297 | 301103871.8047 | 302434221.6049 | 303786930.2252 | 305161997.6658 | 306559423.9265 | 307940081.072 | 309326327.9226 | 310712574.7733 | 312093231.9188 | 313479478.7695 | 314865725.6201 | 316251972.4707 | 317638219.3213 | 319024466.1719 | 320410713.0225 | 321796959.8732 | 323183206.7238 | 324569453.5744 | 325955700.425
T2 | North West Tasmania | Option 1(Prior to Project Marinus) | 303849108.07 | 306078065.5881 | 312480096.5109 | 319222034.1264 | 324412447.1562 | 325786898.7025 | 326739878.5396 | 327717991.935 | 328718149.1359 | 329738502.2078 | 330777730.6576 | 331836027.5194 | 332913392.7931 | 334009826.4788 | 335120561.4733 | 336255131.9828 | 337408770.9042 | 338581478.2376 | 339773253.9828 | 340950728.4191 | 342132969.9584 | 343315211.4977 | 344492685.934 | 345674927.4733 | 346857169.0126 | 348039410.5519 | 349221652.0912 | 350403893.6305 | 351586135.1698 | 352768376.7091 | 353950618.2484 | 355132859.7877 | 356315101.327
|  | Option 2 | 258488012.24 | 260336077.2325 | 265388551.9046 | 271200946.2605 | 276133037.502 | 277592124.3346 | 278600832.7905 | 279636144.6558 | 280694789.3814 | 281774810.9631 | 282874811.7418 | 283994996.0209 | 285135363.8006 | 286295915.0808 | 287471603.9863 | 288672522.2676 | 289893624.0494 | 291134909.3317 | 292396378.1145 | 293642709.2719 | 294894086.3045 | 296145463.337 | 297391794.4944 | 298643171.527 | 299894548.5596 | 301145925.5921 | 302397302.6247 | 303648679.6572 | 304900056.6898 | 306151433.7223 | 307402810.7549 | 308654187.7875 | 309905564.82
|  | Option 3 | 533716596.52 | 537240141.907 | 548206689.0201 | 549895084.1459 | 559793786.4784 | 562472235.8521 | 564515219.546 | 566612084.4262 | 568756206.3787 | 570943623.9123 | 573171506.2106 | 575440267.0832 | 577749906.53 | 580100424.5512 | 582481601.503 | 584913876.6727 | 587387030.4167 | 589901062.735 | 592455973.6276 | 594980225.5894 | 597514697.1948 | 600049168.8002 | 602573420.7621 | 605107892.3675 | 607642363.9729 | 610176835.5783 | 612711307.1837 | 615245778.7892 | 617780250.3946 | 620314722 | 622849193.6054 | 625383665.2108 | 627918136.8162
T3 | Central Highlands | Option 1(with Project Marinus) | 200899029.9 | 201074802.43 | 204475521.59 | 207005118.66 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04 | 208505586.04
|  | Option 2(Prior to Project Marinus) | 433747641.34 | 434656874.55 | 441539865.53 | 447336028.52 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8 | 450937936.8
|  | Option 2 | 274158646.73 | 275603667.7137 | 280267550.3595 | 285272047.8633 | 289147115.0079 | 290165348.8296 | 290731471.6397 | 291312525.2102 | 291906674.0228 | 292512820.2727 | 293130179.5543 | 293758866.5291 | 294398881.1971 | 295050223.5584 | 295710061.6897 | 296384059.4374 | 297069384.8784 | 297766038.0127 | 298474018.8402 | 299173503.8977 | 299875820.8786 | 300578137.8595 | 301277622.9171 | 301979939.8979 | 302682256.8788 | 303384573.8597 | 304086890.8405 | 304789207.8214 | 305491524.8023 | 306193841.7832 | 306896158.764 | 307598475.7449 | 308300792.7258
T4 | North Tasmania Coast | Option 1 | 206261557.23 | 207250113.1181 | 211529266.065 | 215675146.7643 | 218677543.3148 | 219449121.3454 | 219902162.5179 | 220367152.0863 | 220842621.1158 | 221327691.1106 | 221821734.3893 | 222324842.6823 | 222837015.9895 | 223358254.311 | 223886291.3933 | 224425659.7434 | 224974093.1078 | 225531591.4865 | 226098154.8795 | 226657919.5117 | 227219950.3975 | 227781981.2834 | 228341745.9156 | 228903776.8015 | 229465807.6873 | 230027838.5731 | 230589869.4589 | 231151900.3448 | 231713931.2306 | 232275962.1164 | 232837993.0023 | 233400023.8881 | 233962054.7739
|  | Option 2 | 306999256.12 | 308424671.0711 | 314067497.0531 | 319683617.7493 | 324112519.4624 | 325263941.8861 | 326029939.5074 | 326816139.3734 | 327620057.857 | 328440209.5959 | 329275533.2259 | 330126183.8949 | 330992161.603 | 331873466.3502 | 332766266.3767 | 333678225.2021 | 334605511.0665 | 335548123.9701 | 336506063.9127 | 337452508.576 | 338402784.999 | 339353061.4221 | 340299506.0854 | 341249782.5085 | 342200058.9315 | 343150335.3546 | 344100611.7777 | 345050888.2007 | 346001164.6238 | 346951441.0469 | 347901717.4699 | 348851993.893 | 349802270.3161
VIC | bar: 2032-33 to 2053-54
REZ / Constraint ID | REZ Name | Option | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
V2 | Murray River | Option 1 | 911780584.22 | 917606384.6322 | 932461848.4317 | 948753041.1813 | 960995028.5902 | 965802434.3734 | 967471695.4335 | 969184981.1469 | 970936879.1964 | 972724152.7966 | 974544488.934 | 976398225.7346 | 978285363.1982 | 980205901.3248 | 982151489.9488 | 984138829.4016 | 986159569.5175 | 988213710.2965 | 990301251.7385 | 992363742.6833 | 994434583.7938 | 996505424.9043 | 998567915.849 | 1000638756.9595 | 1002709598.07 | 1004780439.1805 | 1006851280.291 | 1008922121.4015 | 1010992962.512 | 1013063803.6225 | 1015134644.733 | 1017205485.8436 | 1019276326.9541
V3 | Western Victoria | 2021-22: See V3-EAST secondary transmission limit constraint augmentations
V4 | South West Victoria | 2021-22: Preparatory Activities- See note below
V5 | Gippsland | 2021-22: See SEVIC1 transmission costs
V6 | Central North Vic | Option 1 | 708512452.43 | 712907629.5687 | 725275385.5944 | 739216226.9498 | 750540859.9735 | 754626971.7297 | 756612557.3343 | 758650510.2621 | 760734392.5668 | 762860354.0169 | 765025643.3962 | 767230662.8558 | 769475412.3958 | 771759892.0161 | 774074169.1967 | 776438108.9777 | 778841778.8391 | 781285178.7809 | 783768308.803 | 786221641.2648 | 788684906.2467 | 791148171.2286 | 793601503.6905 | 796064768.6724 | 798528033.6543 | 800991298.6362 | 803454563.6182 | 805917828.6001 | 808381093.582 | 810844358.5639 | 813307623.5458 | 815770888.5278 | 818234153.5097
|  | Option 2 | 1109535637.78 | 1119103762.356 | 1138559438.9351 | 1161532266.583 | 1179901684.5623 | 1186978191.549 | 1190295763.6757 | 1193700832.6612 | 1197182641.6458 | 1200734757.7865 | 1204352584.0486 | 1208036792.4439 | 1211787382.9725 | 1215604355.6344 | 1219471114.8962 | 1223420851.8245 | 1227436970.8861 | 1231519472.081 | 1235668355.4091 | 1239767452.1372 | 1243883144.3987 | 1247998836.6602 | 1252097933.3884 | 1256213625.6498 | 1260329317.9113 | 1264445010.1728 | 1268560702.4343 | 1272676394.6957 | 1276792086.9572 | 1280907779.2187 | 1285023471.4802 | 1289139163.7416 | 1293254856.0031
|  | Option 3 | 1076547652.47 | 1083019977.9782 | 1100424894.4022 | 1120177068.61 | 1135264939.6981 | 1139765410.8633 | 1142047494.9664 | 1144389766.2226 | 1146784825.3269 | 1149228246.9841 | 1151716869.2689 | 1154251154.3479 | 1156831102.2211 | 1159456712.8885 | 1162116570.6516 | 1164833506.9075 | 1167596105.9576 | 1170404367.8018 | 1173258292.4404 | 1176077969.9832 | 1178909063.2246 | 1181740156.466 | 1184559834.0089 | 1187390927.2503 | 1190222020.4917 | 1193053113.7331 | 1195884206.9745 | 1198715300.2159 | 1201546393.4573 | 1204377486.6987 | 1207208579.9401 | 1210039673.1815 | 1212870766.4229
V7 | Gippsland Coast | Option 1 | 683642065.32 | 687274431.7386 | 699091025.4306 | 711959377.7071 | 720980072.358 | 723153503.8392 | 724445291.7968 | 725771149.1034 | 727126887.2944 | 728510001.4694 | 729918701.6957 | 731353249.6325 | 732813645.2799 | 734299888.6379 | 735805517.7789 | 737343456.558 | 738907243.0477 | 740496877.248 | 742112359.1588 | 743708455.2868 | 745311013.3423 | 746913571.3979 | 748509667.5258 | 750112225.5814 | 751714783.637 | 753317341.6925 | 754919899.7481 | 756522457.8037 | 758125015.8593 | 759727573.9148 | 761330131.9704 | 762932690.026 | 764535248.0815
|  | Option 2 | 683642065.32 | 687274431.7386 | 699091025.4306 | 711959377.7071 | 720980072.358 | 723153503.8392 | 724445291.7968 | 725771149.1034 | 727126887.2944 | 728510001.4694 | 729918701.6957 | 731353249.6325 | 732813645.2799 | 734299888.6379 | 735805517.7789 | 737343456.558 | 738907243.0477 | 740496877.248 | 742112359.1588 | 743708455.2868 | 745311013.3423 | 746913571.3979 | 748509667.5258 | 750112225.5814 | 751714783.637 | 753317341.6925 | 754919899.7481 | 756522457.8037 | 758125015.8593 | 759727573.9148 | 761330131.9704 | 762932690.026 | 764535248.0815
V8 | Portland Coast | 2021-22: Preparatory Activities- See note below
SWV1 | Group Constraint - South West Victoria | 2021-22: Option 1; 2022-23: Preparatory Activities- See note below
Option 1A
Option 1B
Option 1C
Option 2A
Option 2B
Option 3A
Option 3B
SEVIC1 | Transmission Limit Constraint - Gippsland | Option 1 | 297826370.14 | 296703663.7769 | 300594254.3187 | 304773040.3202 | 307235743.059 | 307483259.421 | 307675288.1244 | 307872381.336 | 308073916.4511 | 308279521.1011 | 308488929.208 | 308702179.6656 | 308919272.4737 | 309140207.6324 | 309364024.5541 | 309592644.4139 | 309825106.6244 | 310061411.1855 | 310301558.0971 | 310538823.2458 | 310777048.9822 | 311015274.7185 | 311252539.8673 | 311490765.6036 | 311728991.34 | 311967217.0763 | 312205442.8127 | 312443668.549 | 312681894.2854 | 312920120.0217 | 313158345.7581 | 313396571.4944 | 313634797.2308
|  | Option 2 | 946000546.8269 | 948379285.4152 | 959855872.5935 | 972385287.4732 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635 | 980273663.7635
V3-East | Secondary Transmission Limit - Western Victoria | Option 1 | 162993305.33 | 164443195.0905 | 167766374.7243 | 171736502.3288 | 175128148.8854 | 176499439.4407 | 177224429.1925 | 177968539.6642 | 178729420.1595 | 179505664.8542 | 180296269.2177 | 181101380.0833 | 181920997.4511 | 182755121.3209 | 183600125.0672 | 184463261.9412 | 185340905.3172 | 186233055.1954 | 187139711.5756 | 188035488.0792 | 188934891.2084 | 189834294.3376 | 190730070.8412 | 191629473.9704 | 192528877.0996 | 193428280.2287 | 194327683.3579 | 195227086.4871 | 196126489.6162 | 197025892.7454 | 197925295.8746 | 198824699.0038 | 199724102.1329
Notes: AEMO received TNSP cost estimates for actionable projects and projects with preparatory activities from most TNSPs during June 2023. he Mid-north South Australia MN1 preparatory activities were removed from this table in July 2024 to reflect the updated options instead included in the South Australia options bove (as advised by ElectraNet). | bar: 2032-33 to 2052-53
Preparatory activities | bar: 2031-32 to 2052-53
REZ |  |  | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Darling Downs REZ Expansion(Stage 1) |  |  | 28000000 | 27783308.2799 | 28034824.1084 | 28342798.2019 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956 | 28506666.2956
South East SA REZ |  |  | 34000000 | 34038777.6339 | 34797316.7324 | 35353840.0875 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043 | 35691226.2043
South West Victoria REZ Option 1 |  |  | 64000000 | 64385474.3472 | 65452227.0554 | 66642103.705 | 67562352.429 | 67854547.2503 | 67998625.6523 | 68146503.9521 | 68297714.9799 | 68451979.3666 | 68609097.4714 | 68769098.4773 | 68931982.3842 | 69097749.192 | 69265678.1757 | 69437210.7855 | 69611626.2964 | 69788924.7083 | 69969106.0212 | 70147125.1584 | 70325865.0208 | 70504604.8832 | 70682624.0203 | 70861363.8827 | 71040103.7451 | 71218843.6075 | 71397583.4699 | 71576323.3323 | 71755063.1947 | 71933803.0571 | 72112542.9195 | 72291282.782 | 72470022.6444
South West Victoria REZ Option 1A |  |  | 725000000 | 729697708.087 | 742015660.4757 | 756241651.7104 | 767998397.7087 | 772450197.8505 | 774572138.8574 | 776750043.384 | 778977031.5052 | 781248988.2694 | 783562973.7868 | 785919417.7541 | 788318320.1712 | 790759681.0382 | 793232885.7426 | 795759163.5094 | 798327899.726 | 800939094.3924 | 803592747.5087 | 806214556.7876 | 808846980.679 | 811479404.5704 | 814101213.8493 | 816733637.7407 | 819366061.6321 | 821998485.5234 | 824630909.4148 | 827263333.3062 | 829895757.1976 | 832528181.089 | 835160604.9803 | 837793028.8717 | 840425452.7631
South West Victoria REZ Option 1B |  |  | 1013000000 | 1018732811.9606 | 1036046847.7829 | 1055778305 | 1072268383.9111 | 1078435625.9013 | 1081437974.6241 | 1084519506.4174 | 1087670486.8434 | 1090885093.8907 | 1094159167.6409 | 1097493316.1388 | 1100887539.3844 | 1104341837.3777 | 1107841191.4318 | 1111415638.9206 | 1115050161.157 | 1118744758.1412 | 1122499429.8731 | 1126209045.5441 | 1129933679.9022 | 1133658314.2602 | 1137367929.9313 | 1141092564.2893 | 1144817198.6473 | 1148541833.0053 | 1152266467.3633 | 1155991101.7213 | 1159715736.0793 | 1163440370.4374 | 1167165004.7954 | 1170889639.1534 | 1174614273.5114
South West Victoria REZ Option 1C |  |  | 1372000000 | 1380744730.821 | 1404306396.0524 | 1431534409.6202 | 1454216127.8266 | 1462985360.9044 | 1467185877.699 | 1471497177.9652 | 1475905642.0129 | 1480403124.5738 | 1484983805.6978 | 1489648536.0168 | 1494397315.5307 | 1499230144.2396 | 1504126009.8446 | 1509126936.9434 | 1514211913.237 | 1519380938.7256 | 1524634013.4092 | 1529824051.1965 | 1535035101.2826 | 1540246151.3686 | 1545436189.156 | 1550647239.242 | 1555858289.3281 | 1561069339.4142 | 1566280389.5003 | 1571491439.5863 | 1576702489.6724 | 1581913539.7585 | 1587124589.8445 | 1592335639.9306 | 1597546690.0167
South West Victoria REZ Option 2A |  |  | 618000000 | 621792618.5112 | 632381450.9936 | 644572522.8511 | 654641877.5516 | 658480837.5932 | 660311257.6846 | 662189952.9414 | 664110988.3273 | 666070814.4096 | 668066895.2017 | 670099601.3296 | 672168932.793 | 674274889.5921 | 676408315.3929 | 678587522.8632 | 680803355.6692 | 683055813.8108 | 685344897.2881 | 687606511.7636 | 689877282.573 | 692148053.3825 | 694409667.858 | 696680438.6675 | 698951209.4769 | 701221980.2863 | 703492751.0958 | 705763521.9052 | 708034292.7146 | 710305063.5241 | 712575834.3335 | 714846605.143 | 717117375.9524
South West Victoria REZ Option 2B |  |  | 803000000 | 807836498.45 | 821220911.3363 | 836150144.9242 | 847696390.632 | 851362522.5305 | 853170256.2309 | 855025666.7736 | 856922892.6389 | 858858428.615 | 860829769.8369 | 862837282.4573 | 864880966.4762 | 866960821.8937 | 869067805.8602 | 871220004.0748 | 873408373.6881 | 875632914.6998 | 877893627.1102 | 880127210.9716 | 882369837.6827 | 884612464.3938 | 886846048.2552 | 889088674.9662 | 891331301.6773 | 893573928.3884 | 895816555.0995 | 898059181.8105 | 900301808.5216 | 902544435.2327 | 904787061.9437 | 907029688.6548 | 909272315.3659
South West Victoria REZ Option 3A |  |  | 1076000000 | 1082659353.7656 | 1089847516.8702 | 1111072730.4221 | 1128974900.7559 | 1135430536.4926 | 1138821917.1574 | 1142302741.3624 | 1145862012.969 | 1149493155.7521 | 1153191470.6384 | 1156957644.5134 | 1160791677.3771 | 1164693569.2296 | 1168646355.3236 | 1172683965.1535 | 1176789433.9722 | 1180962761.7796 | 1185203948.5758 | 1189394241.1304 | 1193601498.4322 | 1197808755.734 | 1201999048.2886 | 1206206305.5903 | 1210413562.8921 | 1214620820.1939 | 1218828077.4957 | 1223035334.7975 | 1227242592.0993 | 1231449849.4011 | 1235657106.7029 | 1239864364.0046 | 1244071621.3064
South West Victoria REZ Option 3B |  |  | 1325000000 | 1333131423.1834 | 1355834017.098 | 1381971832.9736 | 1403560659.7991 | 1411791439.8235 | 1415715884.1943 | 1419743831.1446 | 1423862555.8797 | 1428064448.3701 | 1432344071.4277 | 1436702219.6791 | 1441138893.1241 | 1445654091.7629 | 1450228184.297 | 1454900433.3232 | 1459651207.5432 | 1464480506.9569 | 1469388331.5642 | 1474237262.2763 | 1479105824.2869 | 1483974386.2974 | 1488823317.0095 | 1493691879.02 | 1498560441.0306 | 1503429003.0411 | 1508297565.0516 | 1513166127.0621 | 1518034689.0727 | 1522903251.0832 | 1527771813.0937 | 1532640375.1042 | 1537508937.1148

## Non-REZ Assumptions
Go to Assumptions Summary
Non-REZ Connection Assumptions
Within the capacity outlook model, VRE can be connected into REZs or into other areas within 10 km of an existing transmission line. This is done to consider options that avoid the need to expand the transmission network. These areas are not part of the standard group of REZs due to them being located on/near sensitive environmental/community/cultural land, having lower quality resources or other detrimental factors.
Candidates for connection of VRE outside REZs
Region | Approximate location of connections | Resource Limit (MW) | Resource limit violation penalty factor ($M/MW) | Land area (km2)1 | Land use limits in MW
[5 empty] | Wind | Solar
New South Wales Non-REZ | Within 10 km of the 500 kV network between Mt Piper and west of Bayswater | 0 | 1 | 3357 | 699.375 | 1678.5
Victoria Non-REZ | Within 10 km of the 500 kV network between Latrobe Valley and Cranbourne/South Morang | 0 | 1 | 1398 | 291.25 | 699
Connection Costs for Wind and Solar outside REZs
Non-REZ name | Region | Network voltage (kV) | Connection capacity (MVA) | Feeder length (km) | Total cost ($M) | $/kW | System strength connection costs ($/kW)2
New South Wales Non-REZ | NSW | 500 | 600 | 20 | 138 | 230 | 137
Victoria Non-REZ | VIC | 500 | 600 | 20 | 126 | 210 | 137
Notes:
1. A land use limit of 5% for onshore wind and 1% for solar is applied for all scenarios.
2. Where no costs are shown, these have been allocated to REZ expansion costs instead

## Build limits - PHES
Go to Assumptions Summary
Initial Build limits - Pumped Hydro Energy Storage (PHES)
Potential in each NEM sub-region to build pumped hydro energy storage.
Sub-regional limits are considered to reflect the sub-regional configuration of the capacity outlook models.
Limits are based on the Entura report, available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Planning_and_Forecasting/Inputs-Assumptions-Methodologies/2019/Report-Pumped-Hydro-Cost-Modelling.pdf
Limits have been adjusted to reflect the latest PHES development announcements. AEMO has also combined 6 and 12-hour PHES options from Entura into a single 8-hour PHES option.
Name | ISP Sub-region | Region | Pumped Hydro Energy Storage (PHES) limits (MW)
Name |  |  | 8hrs storage | 24hrs storage | 48hrs storage | BOTN - Cethana | Name
Northern New South Wales | NNSW | NSW | 1275 | 500 | 500 | 0
Central New South Wales | CNSW | NSW | 1750 | 235 | 83 | 0
South New South Wales | SNSW | NSW | 2500 | 583 | 167 | 0
Sydney, Newcastle, Wollongong | SNW | NSW | 0 | 0 | 0 | 0
Northern Queensland | NQ | QLD | 1250 | 5278 | 111 | 0
Central Queensland | CQ | QLD | 1000 | 0 | 89 | 0
Gladstone Grid | GG | QLD | 0 | 0 | 0 | 0
South Queensland | SQ | QLD | 1750 | 0 | 300 | 0
Central South Australia | CSA | SA | 698 | 200 | 0 | 0
South East South Australia | SESA | SA | 0 | 0 | 0 | 0
Tasmania | TAS | TAS | 1625 | 1200 | 371 | 750
Victoria | VIC | VIC | 2700 | 700 | 400 | 0
Notes:
1. NSW PHES limits are based on 24 energy projects shortlisted for potential development as part of the NSW Government Pumped Hydro Roadmap. Total value excludes the contribution of the proposed Snowy 2.0 project. NSW Pumped Hydro Roadmap, available at: https://energy.nsw.gov.au/renewables/clean-energy-initiatives/hydro-energy-and-storage#-pumped-hydro-roadmap-
2. PHES limits in NNSW and CNSW have been further adjusted to provide sufficient capacity to reflect five projects that have been awarded funding under the NSW Pumped Hydro Recoverable Grants Program. More information available at: https://www.nsw.gov.au/media-releases/pumped-hydro
3. Tasmanian PHES limits have been informed by underlying analysis of the detailed project information within the Entura report, provided by contributors to the Entura report (but not published). This data avoids misinterpretation of projects that may not be mutually exclusive, and is aligned reasonably with Tasmanian PHES Generation Information submissions.
4. The South Queensland limits do not include Borumba Dam (2GW, 24hrs storage), which will be modelled as a specific project.
5. Where applicable, PHES limits have been adjusted above Entura estimates to ensure proposed projects in Generation Information submissions can be accommodated.

## Build limits
Go to Assumptions Summary
Initial Build limits (MW)
Potential in each NEM region to build different thermal and storage capacities; potential in each zone to build new renewable energy capacity
The new renewable energy capacity in each REZ zone will be moderated by transmission expansion choices in each scenario, loss factor impacts, etc
REZ ID | REZ Name | Region | NTNDP zone | ISP Sub-region | Wind generation total limits (MW) |  |  |  | Solar PV plus Solar thermal Limits (MW) | REZ resource limit violation penalty factor ($M/MW) | REZ Transmission Network limit (Note 1) |  |  | Indicative transmission expansion cost ($M/MW)2 (Note 13) | Indicative transmission expansion cost ($M/MW) (Note 10) |  | Distance to nearest load centre (km) - Green Energy Exports scenario | Indicative transmission expansion cost - Green Energy Export scenario ($M/MW) (Note 13) | Land use limits in MW |  | Land use limits in MW Green Energy Exports scenario |  | Land area (km2)9
[5 empty] | High | Medium | Offshore -fixed | Offshore -floating | Solar |  | Peak demand | Summer Typical | Winter Reference |  | Tranche 2 | Tranche 3 |  |  | Wind | Solar | Wind | Solar
Q1 | Far North QLD | QLD | NQ | NQ | 570 | 1710 |  |  | 1100 | 0.28871 | 750 | 750 | 750 | 1.42 |  |  | 370 | 0.66477 | 6764.1667 | 16234 | 33820.836 | 81170 | 32468
Q2 | North Qld Clean Energy Hub | QLD | NQ | NQ | 4700 | 13900 |  |  | 8000 | 0.28871 | 700 | 700 | 700 | 0.43 |  |  | 292 | 0.52463 | 27529.7917 | 66071.5 | 137648.9693 | 330357.5 | 132143
Q3 | Northern Qld | QLD | NQ | NQ | 0 | 0 |  |  | 3400 | 0.28871 | Modelled as part of NQ-CQ sub-regional limit |  |  | - |  |  | 49 | 0.088037 | 2087.7083 | 5010.5 | 10438.5425 | 25052.5 | 10021
Q4 | Isaac | QLD | NQ | CQ | 1000 | 2800 |  |  | 6900 | 0.28871 | See Group Constraint NQ2 |  |  | - |  |  | 160 | 0.28747 | 12925.4167 | 31021 | 64627.0885 | 155105 | 62042
Q5 | Barcaldine | QLD | CQ | CQ | 1000 | 2900 |  |  | 8000 | 0.28871 | 85 | 85 | 85 | 0.79 |  |  | 415 | 0.74562 | 5320.8333 | 12770 | 26604.1688 | 63850 | 25540
Q6 | Fitzroy | QLD | CQ | CQ | 900 | 2600 |  |  | 7533 | 0.28871 | Modelled as part of CQ-SQ sub-regional limit (Note 11) |  |  | 0 |  |  | 181 | 0.3252 | 4921.4583 | 11811.5 | 24607.2936 | 59057.5 | 23623
Q7 | Wide Bay | QLD | SQ | SQ | 300 | 800 |  |  | 2200 | 0.28871 | See Grouip Constraint SQ1 |  |  | 0 |  |  | 66 | 0.11858 | 2907.7083 | 6978.5 | 14538.5428 | 34892.5 | 13957
Q8 | Darling Downs | QLD | SWQ | SQ | 1400 | 4200 |  |  | 6992 | 0.28871 | See Transmission Limit SWQLD1 |  |  | 0 |  |  | 147 | 0.26411 | 9618.9583 | 23085.5 | 48094.7955 | 115427.5 | 46171
Q9 | Banana | QLD | CQ | SQ | 900 | 2500 |  |  | 6100 | 0.28871 | 150 | 150 | 150 | 0 (Included in connection costs) |  |  | 238 | 0.42761 | 11423.5417 | 27416.5 | 57117.7129 | 137082.5 | 54833
N1 | North West NSW | NSW | NNS | NNSW | 0 | 0 |  |  | 6385 | 0.28871 | 171 | 171 | 171 | 2.82 |  |  | 205 (Note 8) | 0.36832 | 4755 | 11412 | 23775.0019 | 57060 | 22824
N2 | New England | NSW | NNS | NNSW | 1800 | 5600 |  |  | 2985 | 0.28871 | 577 | 577 | 577 | 0.37 |  |  | 298 | 0.53541 | 4601.6667 | 11044 | 23008.3352 | 55220 | 22088
N3 | Central-West Orana | NSW | NCEN | CNSW | 800 | 2200 |  |  | 6850 | 0.28871 | 900 (Note 7) | 900 (Note 7) | 900 (Note 7) | 0 | 0.16 (apply from 5,400 MW) | 0.55 (apply from 6,900 MW) | 143 | 0.25692 | 4519.375 | 10846.5 | 22596.8768 | 54232.5 | 21693
N4 | Broken Hill | NSW | CAN | SNSW | 1300 | 3800 |  |  | 8000 | 0.28871 | 250 | 250 | 250 | 2.61 |  |  | 1032 | 1.8542 | 6312.9167 | 15151 | 31564.5859 | 75755 | 30302
N5 | South West NSW | NSW | SWNSW | SNSW | 1000 | 2900 |  |  | 2256 | 0.28871 | 215 (also see SNSW1 limit below) | 215 (also see SNSW1 limit below) | 215 (also see SNSW1 limit below) | 0.57 | 0.21 (apply from 4,315 MW) |  | 532 | 0.95583 | 5615.4167 | 13477 | 28077.0856 | 67385 | 26954
N6 | Wagga Wagga | NSW | SWNSW | SNSW | 300 | 700 |  |  | 1028 | 0.28871 | 1100 | 1100 | 1100 | - (Note 2) |  |  | 265 | 0.47612 | 2106.4583 | 5055.5 | 10532.2925 | 25277.5 | 10111
N7 | Tumut | NSW | SWNSW | SNSW | 0 | 0 |  |  | 0 | 0.28871 | 0 | 0 | 0 | N/A (Note 3) |  |  | 260 | 0.46713 | 2819.375 | 6766.5 | 14096.8761 | 33832.5 | 13533
N8 | Cooma-Monaro | NSW | CAN | SNSW | 100 | 200 |  |  | 0 | 0.28871 | 350 | 350 | 350 | 1.02 |  |  | 260 | 0.46713 | 828.3333 | 1988 | 4141.667 | 9940 | 3976
N9 | Hunter-Central Coast | NSW | NCEN | CNSW | 400 | 1000 |  |  | 516 | 0.28871 | 400 | 400 | 400 | 0.12 |  |  | 26 | 0.046713 | 1524.375 | 3658.5 | 7621.8756 | 18292.5 | 7317
N10 | Hunter Coast | NSW | NCEN | SNW | 0 | 0 | - | 7420 | 0 | 0.28871 | 5650 | 5650 | 5650 | 0.46 (Note 12) |  |  | 26 | 0.046713 | 0 | 0 | 0 | 0 | 0
N11 | Illawarra Coast | NSW | NCEN | SNW | 0 | 0 | 148 | 5696 (Note 14) | 0 | 0 | 1000 | 1000 | 1000 | 0.41 |  |  | 24 | 0.04312 | 0 | 0 | 0 | 0 | 0
N12 | Illawarra | NSW | NCEN | SNW | 0 | 0 |  |  | 0 | 0.29 | 1000 | 1000 | 1000 | 0.41 |  |  | 24 | 0.04312 | 71.4583 | 171.5 | 357.2917 | 857.5 | 343
V1 | Ovens Murray | VIC | NVIC | VIC | 0 | 0 |  |  | 1000 | 0.28871 | 350 | 350 | 350 | 0 |  |  | 189 | 0.33957 | 3083.75 | 7401 | 15418.7512 | 37005 | 14802
V2 | Murray River | VIC | CVIC | VIC | 0 | 0 |  |  | 4700 | 0.28871 | 440 | 440 | 640 | 1.14 |  |  | 297 | 0.53361 | 5142.5 | 12342 | 25712.5021 | 61710 | 24684
V3 | Western Victoria | VIC | CVIC | VIC | 700 | 1900 |  |  | 400 | 0.28871 | See Transmission Limit V3-EAST and V3-WEST |  |  | 0 |  |  | 191 | 0.34316 | 4521.875 | 10852.5 | 22609.3768 | 54262.5 | 21705
V4 | South West Victoria | VIC | MEL | VIC | 860.5 | 2581.5 |  |  | 0 | 0.28871 | See Transmission Limit SWV1 |  |  | 0 |  |  | 89 | 0.1599 | 3027.0833 | 7265 | 15135.4179 | 36325 | 14530
V5 | Gippsland | VIC | LV | VIC | 500 | 1500 |  |  | 500 | 0.28871 | See Transmission Limit SEVIC1 |  |  | 0 |  |  | 183 | 0.32879 | 1030.625 | 2473.5 | 5153.1254 | 12367.5 | 4947
V6 | Central North Vic | VIC | NVIC | VIC | 400 | 1200 |  |  | 1700 | 0.28871 | 650 | 650 | 1300 | 2.22 |  |  | 131 | 0.23536 | 1253.75 | 3009 | 6268.7505 | 15045 | 6018
V7 | Gippsland Coast | VIC | LV | VIC | 0 | 0 | 54996 | 5000 | 0 | - | 0 | 0 | 0 | - | Included in the connection cost |  | 222 | 0.39886 | 0 | 0 | 0 | 0 | 0
V8 | Southern Ocean (Note 15) | VIC | MEL | VIC | 0 | 0 | 780 | 3330 | 0 | - | See Transmission Limit SWV1 |  |  | 0 |  |  | 242 | 0.43479 | 0 | 0 | 0 | 0 | 0
S1 | South East SA | SA | SESA | SESA | 800 | 2400 |  |  | 100 | 0.28871 | Modelled as part of SESA-CSA subregional limit |  |  | 0 |  |  | 230 | 0.41323 | 5528.9583 | 13269.5 | 27644.7939 | 66347.5 | 26539
S2 | Riverland | SA | NSA | CSA | 400 | 1000 |  |  | 4000 | 0.28871 | 130 | 130 | 130 | 0.14 |  |  | 165 | 0.29645 | 844.7917 | 2027.5 | 4223.9587 | 10137.5 | 4055
S3 | Mid-North SA | SA | ADE | CSA | 1200 | 3400 |  |  | 1300 | 0.28871 | See Group Constraint MN1 |  |  | 0 |  |  | 116 | 0.20841 | 6243.3333 | 14984 | 31216.6692 | 74920 | 29968
S4 | Yorke Peninsula | SA | NSA | CSA | 400 | 1000 |  |  | 0 | 0.28871 | 100 | 100 | 100 | 1.26 |  |  | 81 | 0.14553 | 1669.7917 | 4007.5 | 8348.959 | 20037.5 | 8015
S5 | Northern SA | SA | NSA | CSA | 0 | 0 |  |  | 2900 | 0.28871 | See Group Constraint NSA1 |  |  | 0 |  |  | 55 | 0.098817 | 1858.75 | 4461 | 9293.7507 | 22305 | 8922
S6 | Leigh Creek | SA | NSA | CSA | 600 | 1800 |  |  | 6500 | 0.28871 | 0 | 0 | 0 | 1.26 |  |  | 279 | 0.50127 | 3485.2083 | 8364.5 | 17426.0431 | 41822.5 | 16729
S7 | Roxby Downs | SA | NSA | CSA | 0 | 0 |  |  | 3400 | 0.28871 | 500 | 500 | 500 | 0.57 |  |  | 288 | 0.51744 | 4905.2083 | 11772.5 | 24526.0436 | 58862.5 | 23545
S8 | Eastern Eyre Peninsula | SA | NSA | CSA | 600 | 1700 |  |  | 5000 | 0.28871 | 300 (Note 6) | 300 (Note 6) | 300 (Note 6) | 0.33 |  |  | 46 | 0.082647 | 3475.2083 | 8340.5 | 17376.0431 | 41702.5 | 16681
S9 | Western Eyre Peninsula | SA | NSA | CSA | 400 | 1100 |  |  | 4000 | 0.28871 | - | - | - | 0.91 |  |  | 180 | 0.3234 | 2215 | 5316 | 11075.0009 | 26580 | 10632
S10 | South East SA Coast | SA | SESA | SESA | 0 | 0 | 20428 | 7032 | 0 | 0 | Modelled as part of SESA-CSA subregional limit |  |  | 0 |  |  | 325 | 0.58392 | 0 | 0 | 0 | 0 | 0
T1 | North East Tasmania | TAS | TAS | TAS | 400 | 1000 |  |  | 300 | 0.28871 | 400 | 400 | 400 | 0.5 |  |  | 62 | 0.11139 | 3132.0833 | 7517 | 15660.4179 | 37585 | 15034
T2 | North West Tasmania | TAS | TAS | TAS | 1300 | 3700 |  |  | 150 | 0.28871 | 277 | 277 | 112 | 0.38 | 0.035 |  | 124 | 0.22279 | 3125 | 7500 | 15625.0013 | 37500 | 15000
T3 | Central Highlands | TAS | TAS | TAS | 900 | 2500 |  |  | 150 | 0.28871 | 527 | 527 | 668 | 0.63 | 0.32 (after MarinusLink) |  | 111 | 0.19943 | 2318.3333 | 5564 | 11591.6676 | 27820 | 11128
T4 | North Tasmania Coast | TAS | TAS | TAS | 0 | 0 | 14400 | 26150 | 0 | 0 | Included in T2 limit for Option 1 and in Group Constraint NET1 for Option 2 |  |  | 0.15 |  |  | 112 | 0.20123 | 0 | 0 | 0 | 0 | 0
Notes
1. Intraregional transmission augmentations may be selected by the model if economic to access larger new renewable resource locations.
2. Network upgrades modelled with SNSW-CNSW cutset options 3 and 4
3. Available wind and solar resource capacity is less than the existing transmission capacity.
4. [Note removed.]
5. Transmission limited total build in this REZ will increase with expected coal power station closures.
6. This capacity assumes the completed Eyre Peninsula Reinforcement Project.
7. Build limit does not initially include the capacity gained by the development of the Central-West Orana REZ Pilot project supported by NSW Government.
8. For REZs in NNSW, distance to Armidale used, for REZs in CNSW distance to Bayswater used, and REZs in SNSW distance to Bannaby used. This is to allow for the NSW sub-regional modelling
9. A land use limit of 5% for onshore wind and 1% for solar is applied for all scenarios but Green Energy Exports scenario. The limit for the Green Energy Exports scenario is 25% and 5% for onshore wind and solar respectively. AEMO assumed an indicative land usage of 0.24 km2/MW for wind and 0.02km2/MW for solar.
10. Where expansion cost vary for larger VRE build, additional cost estimates are modelled when VRE exceeds a threshold to capture changes in costs for staged upgrades.
11. A REZ network limit of 3,000 MW has also been modelled for the Green Energy Exports scenario for Q6 to reflect changes in power flow direction associated with significant Hydrogen demand in the CQ sub-region
12. Expansion cost based on CNSW to SNW Option 1
13. Indicative expansion costs will also take into account the forecasted REZ augmentation costs, as shown on 'Forecasted REZ Cost' tabs
14. Values shown are as per modelled. If updated to the recently declared area as of the 15 th June 2024, values would change to 0 MW fixed capacity, and 4,452 MW floating capacity.
15. V8 'Portland' renamed to 'Southern Ocean' to align with governments' references and naming.
REZ transmission modifiers due to committed and anticipated network augmentations
REZ ID | REZ | Project EnergyConnect | Western Renewables Link | Central-West Orana REZ Transmission Link | The Victorian Government RDP: Mortlake turn in Project (Note 2) | The Victorian Government RDP: The network augmentation project (Note 2) | CopperString 2032
[5 empty] | Mortlake turn in Project† | The network augmentation project†
N3 | Central-West Orana |  |  | 3,000 MW
N5 | South West NSW | 800 MW
V2 | Murray River | 400 MW |  |  |  | 112 MW
V3 | Western Victoria |  | 1,460 MW |  |  | -
SWV1 | South West Victoria |  |  |  | 1,100 MW (Note 1) | 81 MW (Note 2)
V6 | Central North Victoria |  |  |  |  | 12 MW (Note 2)
S2 | Riverland | 800 MW
Q2 | North Qld Clean Energy Hub | [5 empty] | 1500
Notes
1. The Mortlake turn in project, South West REZ and the network augmentation project forms part of the Victorian Government’s REZ Development Plan stage 1. On 14 October 2022, by Ministerial Order, the Victorian Government has directed AEMO Victorian Planner to enter into a contract with AusNet services to supply the Mortlake Tun in Project and the network augmentation project. The turn-in project, when combined with Cressy Terminal Station (constructed as part of the Golden Plains Wind Farm committed generation project), is expected to allow up to 1,500 MW of additional generation output under optimal network conditions and, on average, 1,100 MW of additional generation output during peak summer periods following its commissioning.
2. See AEMO’s 2023 Victorian Annual Planning Report for more details at https://aemo.com.au/-/media/files/electricity/nem/planning_and_forecasting/vapr/2023/2023-victorian-annual-planning-report.pdf
REZ Group Constraints Summary
Term | Description | Group Constraint ID | Transmission-limited total build |  |  | Indicative transmission expansion cost ($M/MW) | Indicative transmission expansion cost ($M/MW)
|  |  | Summer Peak | Summer Typical | Winter Reference
-CQ-NQ | North Queensland to Central Queensland flow | NQ2 | 2500 | 2500 | 2750 | 0.43 | 0.72 (Apply from 2,900 MW)
Q4 | Isaac
Q5 | Barcaldine
-0.5 x SQ-CQ | Central Queensland - South Queensland | SQ1(Before Queensland SuperGrid) | 1400 | 1400 | 1400 | 0.49
Q7 | Wide Bay
Q7 | Wide Bay | SQ1 (After Queensland SuperGrid) | 5700 | 5700 | 5700 | -
0.42 x Q8 | Darling Downs
-0.82 x CQ-SQ | CQ-SQ sub-regional flow
0.75 x BPH | Borumba Pumped Hydro
0.51 x Q8_Coal | Existing South West Queensland coal and gas generation (Tarong, Tarong North, Kogan Creek, Darling Downs, Braemar)
-VIC-SA | Heywood Interconnector | SWV1 | 1850 | 1850 | 1850 | 0.63
V4 | South West Victoria
V8 | Southern Ocean
S3 | Mid-North SA | MN1 | 2,000 | 2,000 | 2000 (Note 3) | 0.32417 | 0.29 Apply after 1,200 MW
0.5 x S4 (Note 1) | Yorke Peninsula
S5 | Northern SA
S6 | Leigh Creek
S7 | Roxby Downs
S8 | Eastern Eyre Peninsula
S9 | Western Eyre Peninsula
-CSA Export Electrolyser load | H2 Electrolyser load in CSA area
S3 | Mid-North SA | MN1 North | 800 | 800 | 800 | 1.434 | 1.7925
-0.5 x S4 (Note 1) | Yorke Peninsula
-S5 | Northern SA
-S6 | Leigh Creek
-S7 | Roxby Downs
-S8 | Eastern Eyre Peninsula
-S9 | Western Eyre Peninsula
CSA Export Electrolyser load | H2 Electrolyser load in CSA area
0.5 x S5 | Northern SA | NSA1 | 1125 | 1125 | 1125 | 0.22
S8 | Eastern Eyre Peninsula
S9 | Western Eyre Peninsula
-CSA Export Electrolyser load | H2 Electrolyser load in CSA area
- 0.5 x S5 | Northern SA | NSA1 North | 350 | 350 | 350 | 0.22 (Note 2)
- S8 | Eastern Eyre Peninsula
- S9 | Western Eyre Peninsula
CSA Export Electrolyser load | H2 Electrolyser load in CSA area
T1 | North East Tasmania | NET1 | 1600 | 1600 | 1600 | 0.34
T4 | North Tasmania Coast
Notes
1. Only 50% of the renewable energy developed in the Yorke Peninsula contributes to this transmission constraint.
2. Increase in capacity to NSA1 also allows for increase in capacity for NSA1 North
REZ Transmission Limit Constraint Summary
Term | Description | Constraint ID | Transmission-limited total build |  |  | Indicative transmission expansion cost ($M/MW) | Indicative transmission expansion cost ($M/MW)
|  |  | Summer Peak | Summer Typical | Winter Reference |  | Tranche 2
V5 | Gippsland | SEVIC1 | 6000 | 6000 | 6000 | 0.1485
V7 | Gippsland Coast
TAS-VIC | Basslink and Marinuslink
Existing gen | Existing coal and gas in SE VIC (Note 1)
Q8 | Darling Downs | SWQLD1 | 5300 | 5300 | 5300 | 0.06 | 0.12 (apply from 6,160 MW)
1.5 x NSW-QLD | NSW to Queensland Interconnector
-0.3 x CQ-SQ | CQ-SQ sub-regional flow
0.6 x Existing gen | Existing coal and gas in Q8 (Note 2)
1.5 x MM | Millmerran coal units
0.5 x BPH | Borumba Pumped Hydro
0.3 x SESA-CSA | SESA-CSA sub-regional flow | S1-TBMO | 350 | 350 | 350 | 0.28
S1 TB | Tailem Bend (Note 3)
Notes
1. Loy Yang A, Loy Yang B, Yallourn, Jeeralang, Bairnsdale, Valley Power
2.Tarong, Tarong North, Kogan Creek, Darling Downs, Braemar
3. Tailem Bend Solar stages 1 and 2; Tailem Bend battery
REZ Secondary Transmission Limit Summary
Term | Description | Constraint ID | Transmission-limited total build |  |  | Indicative transmission expansion cost ($M/MW) | Indicative transmission expansion cost ($M/MW)
|  |  | Summer Peak | Summer Typical | Winter Reference |  | Tranche 2
Limondale SF | Existing BESS and solar generation in South West New South Wales area (Note 1) | SWNSW1 | 940 | 940 | 940 | 0.28
Limondale 2 SF
Sunraysia SF
Coleambally SF
Finley SF
Darlington Pt SF
Hillston SF
Darlington Point BESS
Riverina BESS 1 & 2
Elaine WF | Existing wind generation in Western Victoria East of Ballarat | V3-EAST | 600 | 600 | 800 | 0.27
Mt Mercer WF
Moorabool WF
Yoloak South WF
Yendon
Ararat WF | Existing wind generation in Western Victoria West of Ballarat | V3-WEST | 780 | 780 | 980 | -
Bulgana WF
Challicum Hills WF
Crowlands WF
Kiata WF
Murra Warra WF stages 1 & 2
Waubra
V3 New | New VRE forecast for the Western Victorian REZ
Notes
1. Limodale 1, Limondale 2 and Sunraysia SFs are mapped as being in the N5 REZ only, following the update to the REZ geographical boundary

## Power System Constraints
Go to Assumptions Summary
Power System Constraints - Synchronous Generating Units
These are constraints which reflect the operational limits which need to be observed in the model. For discussion on these power system security constraints please see the 2023 IASR.
Synchronous unit commitment requirement All scenarios except for the Green Energy Exports scenario
Year | Coal unit commitment requirements1 |  |  |  | Gas unit commitment requirements1
| QLD | NSW | VIC | TAS2 | SA
2022-23 | 11 | 7 | 5 | - | 2
2023-24 | 11 | 7 | 5 | - | 2
2024-25 | 11 | 7 | 5 | - | 1
2025-26 | 8 | 5 | 3 | - | 1
2026-27 | 6 | 3 | 2 | - | 0
2027-28 | 4 | 2 | 2 | - | 0
2028-29 | 3 | 2 | 1 | - | 0
2029-30 | 2 | 1 | 1 | - | 0
2030-31 | 1 | 1 | 0 | - | 0
2031-32 | 1 | 0 | 0 | - | 0
2032-33 | 1 | 0 | 0 | - | 0
≥2033-34 | 0 | 0 | 0 | - | 0
Synchronous unit commitment requirement for the Green Energy Exports scenario
Year | Coal unit commitment requirements1 |  |  |  | Gas unit commitment requirements1
| QLD | NSW | VIC | TAS2 | SA
2022-23 | 11 | 7 | 5 | - | 2
2023-24 | 11 | 7 | 5 | - | 2
2024-25 | 11 | 7 | 5 | - | 1
2025-26 | 5 | 3 | 2 | - | 1
2026-27 | 2 | 1 | 1 | - | 0
2027-28 | 1 | 0 | 0 | - | 0
2028-29 | 0 | 0 | 0 | - | 0
2029-30 | 0 | 0 | 0 | - | 0
2030-31 | 0 | 0 | 0 | - | 0
2031-32 | 0 | 0 | 0 | - | 0
2032-33 | 0 | 0 | 0 | - | 0
≥2033-34 | 0 | 0 | 0 | - | 0
Notes:
1 . Numbers shown are high-level planning assumptions only, not operational advice. Comprehensive studies with detailed models will be required closer to these time periods as the power system evolves.
2. Tasmania does not have any unit commitment constraints applied
3. When assessing system strength and inertia shortfalls, the requirement to always keep minimum units online is relaxed in market modelling in order to determine timing and size of potential shortfalls.
4. Future AEMO reports such as the System Strength and Inertia reports may test interim numbers of machines as part of their detailed studies and assessments.

## Storage properties
Go to Assumptions Summary
Battery properties
Property | Battery storage (1hr storage) | Battery storage (2hrs storage) | Battery storage (4hrs storage) | Battery storage (8hrs storage) | Virtual Power Plants (aggregated ESS)4 | Units
Maximum power1 | 1 | 1 | 1 | 1 | 1 | MW
Energy capacity2 | 1 | 2 | 4 | 8 | 2.2 | MWh
Round trip efficiency (aggregated)3 | not applicable | not applicable | not applicable | not applicable | 85 | %
Charge efficiency (utility) | 91.6515 | 91.6515 | 92.1954 | 91.1043 | not applicable | %
Discharge efficiency (utility) | 91.6515 | 91.6515 | 92.1954 | 91.1043 | not applicable | %
Round trip efficiency (utility) | 84 | 84 | 85 | 83 | not applicable | %
Annual degradation (utility) | 1.8 | 1.8 | 1.8 | 1.8 |  | %
Allowable max state of charge | 100 | 100 | 100 | 100 | 85 | %
Allowable min state of charge | 0 | 0 | 0 | 0 | 0 | %
Notes:
1. Large-scale battery storage operating parameters are sourced from Aurecon 2022 Costs and Technical Parameter Review.
2. Capacities for large-scale batteries are before any degradation.
3. VPP values have been sourced from CSIRO Small-scale solar PV and battery projections 2022 (p60).
4. The VPP forecasts already account for degradation of capacity of 1.6% per year.
Pumped hydro properties
Property | Existing and committed projects |  |  |  |  | New entrant assumptions |  |  | Units
| Snowy 2.01 | Lower Tumut2 | Wivenhoe | Shoalhaven | Kidston3 | Cethana4 | Borumba4 | New Entrant PHES4
Installed capacity3 | 2040 |  | 570 | 240 | 250 (generation) 325 (pump) | 750 | 1998 |  | MW
Storage capacity | 168 |  | 10 | 63.5 | 6 | 20 | 24 |  | hours
Pumping efficiency | 76 | 78 | 70 | 70 | 80 | 76 | 76 | 76 | %
Notes:
1. Snowy 2.0 pumping efficiency has been sourced from Snowy Hydro Limited's report on NEM outlook and Snowy 2.0 . Source: https://www.snowyhydro.com.au/wp-content/uploads/2018/01/MJA_ReportFinal_Jan2018.pdf (p50). It was confirmed with Snowy Hydro for the 2023 IASR.
2. Lower Tumut pumping efficiency is based on discussions with the participant.
3. Information based on Kidston Pumped Storage Hydro Project Financial Close Report August 2021.
4. Pumping efficiency for new entrant generators is based on information provided by Hydro Tasmania.

## Coal and Biomass price
Go to Assumptions Summary
Coal price ($/GJ, real 2023 dollars)
Export exposed: Weighting of 2021 Woodmac prices and 2022 Oxford Economics Australia Newcastle Export thermal prices converted to domestic quality
| Non export exposed: Woodmac 2021 prices used Biomass is based on an AEMO assumption. | [5 empty] | Consultant's scenario mapping
[8 empty] | Progressive Change | Step Change | Green Energy Exports
| Modelling Scenario | [5 empty] | Fuel Cost Scenario | High price | Central | Low price
Progressive Change
| Generator | Coal Price Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Progressive Change | Bayswater | High Price | 2.0055 | 2.0391 | 1.9893 | 1.9476 | 3.846 | 3.8256 | 3.8098 | 3.8047 | 3.7803 | 3.7544 | 3.7272 | 3.6993 | 3.6711 | 3.6419 | 3.612 | 3.5809 | 3.5489 | 3.5672 | 3.558 | 3.521 | 3.4833 | 3.4451 | 3.4358 | 3.4358 | 3.4358 | 3.4358 | 3.4358 | 3.4358 | 3.4358 | 3.4358 | 3.4358 | 3.4358
Progressive Change | Eraring | High Price | 11.2679 | 4.3839 | 5.2906 | 4.2375 | 4.1575 | 4.1355 | 4.1184 | 4.0951 | 4.0693 | 4.0418 | 4.0129 | 3.9827 | 3.9511 | 3.9182 | 3.8841 | 3.8489 | 3.8127 | 3.7755 | 3.7374 | 3.6986 | 3.659 | 3.6189 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091
Progressive Change | Mt Piper | High Price | 4.0486 | 4.1342 | 5.2906 | 4.2375 | 4.1575 | 4.1355 | 4.1184 | 4.0951 | 4.0693 | 4.0418 | 4.0129 | 3.9827 | 3.9511 | 3.9182 | 3.8841 | 3.8489 | 3.8127 | 3.7755 | 3.7374 | 3.6986 | 3.659 | 3.6189 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091 | 3.6091
Progressive Change | Vales Point B | High Price | 10.0588 | 3.8886 | 4.7617 | 3.8518 | 3.7666 | 3.7315 | 3.7157 | 3.6928 | 3.6728 | 3.6525 | 3.6299 | 3.6061 | 3.5878 | 3.5699 | 3.5552 | 3.5375 | 3.5188 | 3.5084 | 3.485 | 3.4488 | 3.4119 | 3.3744 | 3.3653 | 3.3653 | 3.3653 | 3.3653 | 3.3653 | 3.3653 | 3.3653 | 3.3653 | 3.3653 | 3.3653
Progressive Change | Callide B | High Price | 2.3084 | 2.3197 | 2.3264 | 2.3272 | 2.3279 | 2.3287 | 2.3294 | 2.3302 | 2.3309 | 2.3317 | 2.3324 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328
Progressive Change | Callide C | High Price | 2.3084 | 2.3197 | 2.3264 | 2.3272 | 2.3279 | 2.3287 | 2.3294 | 2.3302 | 2.3309 | 2.3317 | 2.3324 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328
Progressive Change | Gladstone | High Price | 9.0353 | 3.814 | 4.5017 | 3.703 | 3.6423 | 3.6256 | 3.6126 | 3.595 | 3.5754 | 3.5546 | 3.5327 | 3.5097 | 3.4857 | 3.4608 | 3.4349 | 3.4082 | 3.3807 | 3.3525 | 3.3237 | 3.2942 | 3.2642 | 3.2338 | 3.2029 | 3.1723 | 3.1421 | 3.1123 | 3.1073 | 3.1073 | 3.1073 | 3.1073 | 3.1073 | 3.1073
Progressive Change | Kogan Creek | High Price | 1.566 | 1.5702 | 1.5775 | 1.5863 | 1.5951 | 1.6092 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188
Progressive Change | Millmerran | High Price | 1.4327 | 1.4316 | 1.4408 | 1.4524 | 1.4643 | 1.4801 | 1.4794 | 1.4704 | 1.4717 | 1.4723 | 1.4727 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726
Progressive Change | Stanwell | High Price | 7.4587 | 3.4906 | 4.0132 | 3.4062 | 3.3601 | 3.3474 | 3.3376 | 3.3242 | 3.3092 | 3.2934 | 3.2768 | 3.2593 | 3.2411 | 3.2221 | 3.2025 | 3.1822 | 3.1613 | 3.1399 | 3.118 | 3.0956 | 3.0728 | 3.0496 | 3.0454 | 3.0454 | 3.0454 | 3.0454 | 3.0454 | 3.0454 | 3.0454 | 3.0454 | 3.0454 | 3.0454
Progressive Change | Tarong | High Price | 3.0141 | 3.0269 | 3.0366 | 3.0367 | 3.0367 | 3.0413 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441
Progressive Change | Tarong North | High Price | 3.0141 | 3.0269 | 3.0366 | 3.0367 | 3.0367 | 3.0413 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441
Progressive Change | Loy Yang A | High Price | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934
Progressive Change | Loy Yang B | High Price | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934
Progressive Change | Yallourn W | High Price | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182
Step Change
| Generator | Coal Price Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Step Change | Bayswater | Central | 1.9824 | 2.0062 | 1.9561 | 1.9145 | 3.6295 | 3.6097 | 3.5906 | 3.5858 | 3.5121 | 3.3269 | 3.1309 | 2.9601 | 2.8703 | 2.8159 | 2.7335 | 2.6516 | 2.5702 | 2.5482 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537
Step Change | Eraring | Central | 9.6928 | 4.3821 | 4.16 | 4.0067 | 3.9649 | 3.9433 | 3.9224 | 3.8984 | 3.8197 | 3.6197 | 3.4078 | 3.2218 | 3.1227 | 3.0608 | 2.967 | 2.8738 | 2.7811 | 2.6891 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433
Step Change | Mt Piper | Central | 3.7259 | 3.6285 | 4.16 | 4.0067 | 3.9649 | 3.9433 | 3.9224 | 3.8984 | 3.8197 | 3.6197 | 3.4078 | 3.2218 | 3.1227 | 3.0608 | 2.967 | 2.8738 | 2.7811 | 2.6891 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433
Step Change | Vales Point B | Central | 8.9865 | 4.1193 | 3.9721 | 3.8718 | 3.8685 | 3.875 | 3.8709 | 3.8609 | 3.7963 | 3.6099 | 3.4104 | 3.2357 | 3.1473 | 3.1082 | 3.0487 | 2.9893 | 2.9298 | 2.8703 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406
Step Change | Callide B | Central | 2.3084 | 2.3197 | 2.3264 | 2.3272 | 2.3279 | 2.3287 | 2.3294 | 2.3302 | 2.3309 | 2.3317 | 2.3324 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328
Step Change | Callide C | Central | 2.3084 | 2.3197 | 2.3264 | 2.3272 | 2.3279 | 2.3287 | 2.3294 | 2.3302 | 2.3309 | 2.3317 | 2.3324 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328
Step Change | Gladstone | Central | 7.8406 | 3.8127 | 3.6442 | 3.5279 | 3.4962 | 3.4798 | 3.464 | 3.4457 | 3.3861 | 3.2344 | 3.1698 | 3.1488 | 3.1278 | 3.0839 | 3.0172 | 2.9505 | 2.8837 | 2.817 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836
Step Change | Kogan Creek | Central | 1.566 | 1.5702 | 1.5775 | 1.5863 | 1.5951 | 1.6092 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188
Step Change | Millmerran | Central | 1.4327 | 1.4316 | 1.4408 | 1.4524 | 1.4643 | 1.4801 | 1.4794 | 1.4704 | 1.4717 | 1.4723 | 1.4727 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726
Step Change | Stanwell | Central | 6.5508 | 3.4896 | 3.3615 | 3.2732 | 3.2491 | 3.2366 | 3.2246 | 3.2107 | 3.1654 | 3.0501 | 2.9295 | 2.8287 | 2.7444 | 2.6757 | 2.6203 | 2.5755 | 2.5395 | 2.5108 | 2.4875 | 2.4661 | 2.4456 | 2.4262 | 2.4077 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057
Step Change | Tarong | Central | 3.0141 | 3.0269 | 3.0366 | 3.0367 | 3.0367 | 3.0413 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441
Step Change | Tarong North | Central | 3.0141 | 3.0269 | 3.0366 | 3.0367 | 3.0367 | 3.0413 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441
Step Change | Loy Yang A | Central | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934
Step Change | Loy Yang B | Central | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934
Step Change | Yallourn W | Central | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182
Green Energy Exports
| Generator | Coal Price Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Green Energy Exports | Bayswater | Low price | 1.9824 | 2.0062 | 1.9561 | 1.9145 | 3.0484 | 3.0074 | 2.9855 | 2.9817 | 2.9628 | 2.9444 | 2.9237 | 2.8964 | 2.8703 | 2.8159 | 2.7335 | 2.6516 | 2.5702 | 2.5482 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537 | 2.537
Green Energy Exports | Eraring | Low price | 9.5273 | 4.4702 | 4.096 | 3.4804 | 3.3301 | 3.2853 | 3.2614 | 3.2415 | 3.2222 | 3.2035 | 3.1823 | 3.1525 | 3.1227 | 3.0608 | 2.967 | 2.8738 | 2.7811 | 2.6891 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433
Green Energy Exports | Mt Piper | Low price | 3.7259 | 3.6285 | 4.096 | 3.4804 | 3.3301 | 3.2853 | 3.2614 | 3.2415 | 3.2222 | 3.2035 | 3.1823 | 3.1525 | 3.1227 | 3.0608 | 2.967 | 2.8738 | 2.7811 | 2.6891 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433 | 2.6433
Green Energy Exports | Vales Point B | Low price | 8.8331 | 4.2021 | 3.911 | 3.3632 | 3.2491 | 3.2284 | 3.2186 | 3.2104 | 3.2025 | 3.1949 | 3.1848 | 3.166 | 3.1473 | 3.1082 | 3.0487 | 2.9893 | 2.9298 | 2.8703 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406 | 2.8406
Green Energy Exports | Callide B | Low price | 2.3084 | 2.3197 | 2.3264 | 2.3272 | 2.3279 | 2.3287 | 2.3294 | 2.3302 | 2.3309 | 2.3317 | 2.3324 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328
Green Energy Exports | Callide C | Low price | 2.3084 | 2.3197 | 2.3264 | 2.3272 | 2.3279 | 2.3287 | 2.3294 | 2.3302 | 2.3309 | 2.3317 | 2.3324 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328 | 2.3328
Green Energy Exports | Gladstone | Low price | 7.6869 | 3.8512 | 3.5675 | 3.1005 | 3.0973 | 3.1306 | 3.1668 | 3.2037 | 3.2119 | 3.1908 | 3.1698 | 3.1488 | 3.1278 | 3.0839 | 3.0172 | 2.9505 | 2.8837 | 2.817 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836 | 2.7836
Green Energy Exports | Kogan Creek | Low price | 1.566 | 1.5702 | 1.5775 | 1.5863 | 1.5951 | 1.6092 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188 | 1.6188
Green Energy Exports | Millmerran | Low price | 1.4327 | 1.4316 | 1.4408 | 1.4524 | 1.4643 | 1.4801 | 1.4794 | 1.4704 | 1.4717 | 1.4723 | 1.4727 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726 | 1.4726
Green Energy Exports | Stanwell | Low price | 6.4249 | 3.5099 | 3.2942 | 2.9394 | 2.753 | 2.6569 | 2.6093 | 2.5772 | 2.5541 | 2.5387 | 2.527 | 2.5155 | 2.5042 | 2.493 | 2.4819 | 2.471 | 2.4602 | 2.4495 | 2.4393 | 2.4296 | 2.4205 | 2.412 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057 | 2.4057
Green Energy Exports | Tarong | Low price | 3.0141 | 3.0269 | 3.0366 | 3.0367 | 3.0367 | 3.0413 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441
Green Energy Exports | Tarong North | Low price | 3.0141 | 3.0269 | 3.0366 | 3.0367 | 3.0367 | 3.0413 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441 | 3.0441
Green Energy Exports | Loy Yang A | Low price | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934
Green Energy Exports | Loy Yang B | Low price | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934 | 0.75934
Green Energy Exports | Yallourn W | Low price | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182 | 0.75182
All scenarios (No updates)
| Biomass price | Price Scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
| Biomass | Central | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
| Biomass | Low Price | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425
| Biomass | High Price | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425 | 0.62425

## Gas, Liquid fuel, H2 price
Go to Assumptions Summary
Gas price ($/GJ, real July 2023 dollars)
Gas prices based on price forecasts delivered by ACIL Allen in July 2023 |  |  |  |  | Consultant's scenario mapping
In response to stakeholder feedback, these price forecasts were updated following the 2023 Draft IASR to consider the Federal Government's gas price cap and Mandatory Code of Conduct. | [7 empty] | Progressive Change | Step Change | Green Energy Exports
[5 empty] | Gas price scenario |  |  | Progressive Change | Step Change | Green Energy Exports
[5 empty] | Liquid fuel price scenario |  |  | Medium | Medium | Medium
Gas powered generation fuel costs |  |  |  |  | Hydrogen price scenario |  |  | - | - | Hydrogen Export
Step Change
| Gas price scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Bairnsdale | Step Change | 18.7347 | 18.3805 | 17.2354 | 14.6931 | 12.5995 | 11.8894 | 11.4698 | 11.4153 | 11.3839 | 11.4007 | 11.5499 | 11.7322 | 11.915 | 12.0593 | 12.1252 | 12.2664 | 12.4388 | 12.6484 | 12.9023 | 13.054 | 13.0706 | 13.1028 | 13.3147 | 13.5877 | 13.7432 | 13.7603 | 13.8445 | 13.8866 | 13.8814 | 13.979 | 14.0772 | 14.1761
Barcaldine Power Station | Step Change | 17.7314 | 17.0173 | 15.3714 | 13.6355 | 12.319 | 11.794 | 11.7755 | 11.7718 | 11.7745 | 11.7832 | 11.9136 | 12.0368 | 12.0458 | 12.0541 | 12.0604 | 12.1783 | 12.2914 | 12.3066 | 12.4539 | 12.6126 | 12.6422 | 12.6464 | 12.6464 | 12.6464 | 12.6464 | 12.6574 | 12.6726 | 12.6799 | 12.686 | 12.6921 | 12.6983 | 12.7044
Barker Inlet Power Station | Step Change | 17.3458 | 16.9218 | 15.8534 | 13.9157 | 12.2737 | 11.7315 | 11.4235 | 11.2722 | 11.2361 | 11.2396 | 11.307 | 11.408 | 11.5601 | 11.6421 | 11.6214 | 11.7495 | 11.9226 | 12.1735 | 12.4938 | 12.7047 | 12.6952 | 12.6343 | 12.8051 | 13.0591 | 13.1943 | 13.1905 | 13.2295 | 13.301 | 13.4176 | 13.635 | 13.8559 | 14.0804
Bell Bay Three | Step Change | 19.4671 | 19.1692 | 18.0771 | 15.2923 | 13.0571 | 12.5893 | 12.3016 | 12.2415 | 12.2287 | 12.1875 | 12.2352 | 12.3454 | 12.538 | 12.6423 | 12.6004 | 12.7101 | 12.8698 | 13.1824 | 13.5879 | 13.8959 | 14.0255 | 14.0639 | 14.2758 | 14.5488 | 14.6926 | 14.6865 | 14.7482 | 14.7654 | 14.7395 | 14.8225 | 14.9061 | 14.99
Bolivar Power Station | Step Change | 19.0157 | 18.5597 | 17.1792 | 14.6885 | 12.7862 | 12.2565 | 11.9485 | 11.7972 | 11.7611 | 11.7646 | 11.832 | 11.933 | 12.0851 | 12.1671 | 12.1464 | 12.2745 | 12.4476 | 12.6985 | 13.0188 | 13.2297 | 13.214 | 13.1468 | 13.3176 | 13.5716 | 13.7068 | 13.703 | 13.742 | 13.7385 | 13.7074 | 13.7776 | 13.8483 | 13.9192
Braemar | Step Change | 17.7582 | 16.9488 | 15.2868 | 13.6586 | 12.3842 | 11.888 | 11.8911 | 11.8924 | 11.893 | 11.8924 | 12.0168 | 12.1418 | 12.1418 | 12.1424 | 12.143 | 12.2668 | 12.3899 | 12.3905 | 12.5174 | 12.6418 | 12.6411 | 12.6418 | 12.6399 | 12.6405 | 12.6418 | 12.6411 | 12.6437 | 12.6463 | 12.6478 | 12.6493 | 12.6508 | 12.6523
Braemar 2 Power Station | Step Change | 17.7582 | 16.9488 | 15.2868 | 13.6586 | 12.3842 | 11.888 | 11.8911 | 11.8924 | 11.893 | 11.8924 | 12.0168 | 12.1418 | 12.1418 | 12.1424 | 12.143 | 12.2668 | 12.3899 | 12.3905 | 12.5174 | 12.6418 | 12.6411 | 12.6418 | 12.6399 | 12.6405 | 12.6418 | 12.6411 | 12.6437 | 12.6463 | 12.6478 | 12.6493 | 12.6508 | 12.6523
Colongra | Step Change | 19.5667 | 19.17 | 17.8359 | 15.333 | 13.4376 | 12.7218 | 12.2503 | 12.1365 | 12.1427 | 12.2276 | 12.3693 | 12.532 | 12.6962 | 12.8198 | 12.8684 | 12.989 | 13.1325 | 13.3192 | 13.5582 | 13.7228 | 13.6845 | 13.5885 | 13.7075 | 13.8894 | 13.975 | 13.9673 | 14.0423 | 14.0836 | 14.0877 | 14.196 | 14.3051 | 14.4151
Condamine A | Step Change | 13.261 | 13.0717 | 12.6843 | 11.6914 | 10.3968 | 9.8968 | 9.8968 | 9.8968 | 9.8968 | 9.8968 | 10.0218 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.2718 | 10.3968 | 10.3968 | 10.5218 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468
Darling Downs | Step Change | 13.261 | 13.0717 | 12.6843 | 11.6914 | 10.3968 | 9.8968 | 9.8968 | 9.8968 | 9.8968 | 9.8968 | 10.0218 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.2718 | 10.3968 | 10.3968 | 10.5218 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468
Dry Creek GT | Step Change | 19.0157 | 18.5597 | 17.1792 | 14.6885 | 12.7862 | 12.2565 | 11.9485 | 11.7972 | 11.7611 | 11.7646 | 11.832 | 11.933 | 12.0851 | 12.1671 | 12.1464 | 12.2745 | 12.4476 | 12.6985 | 13.0188 | 13.2297 | 13.214 | 13.1468 | 13.3176 | 13.5716 | 13.7068 | 13.703 | 13.742 | 13.7385 | 13.7074 | 13.7776 | 13.8483 | 13.9192
Hallett GT | Step Change | 17.3458 | 16.9218 | 15.8534 | 13.9157 | 12.2737 | 11.7315 | 11.4235 | 11.2722 | 11.2361 | 11.2396 | 11.307 | 11.408 | 11.5601 | 11.6421 | 11.6214 | 11.7495 | 11.9226 | 12.1735 | 12.4938 | 12.7047 | 12.6952 | 12.6343 | 12.8051 | 13.0591 | 13.1943 | 13.1905 | 13.2295 | 13.2298 | 13.2025 | 13.2728 | 13.3435 | 13.4145
Jeeralang A | Step Change | 16.8629 | 16.5505 | 15.6838 | 13.6966 | 11.9935 | 11.4998 | 11.212 | 11.1519 | 11.1391 | 11.0979 | 11.1456 | 11.2559 | 11.4485 | 11.5527 | 11.5108 | 11.6206 | 11.7802 | 12.0928 | 12.4983 | 12.8063 | 12.9489 | 13.0003 | 13.2122 | 13.4852 | 13.6407 | 13.6578 | 13.742 | 13.7848 | 13.7804 | 13.878 | 13.9763 | 14.0752
Jeeralang B | Step Change | 16.8629 | 16.5505 | 15.6838 | 13.6966 | 11.9935 | 11.4998 | 11.212 | 11.1519 | 11.1391 | 11.0979 | 11.1456 | 11.2559 | 11.4485 | 11.5527 | 11.5108 | 11.6206 | 11.7802 | 12.0928 | 12.4983 | 12.8063 | 12.9489 | 13.0003 | 13.2122 | 13.4852 | 13.6407 | 13.6578 | 13.742 | 13.8682 | 14.0328 | 14.3038 | 14.58 | 14.8615
Kurri Kurri | Step Change | 19.5667 | 19.17 | 17.8359 | 15.333 | 13.4376 | 12.7218 | 12.2503 | 12.1365 | 12.1427 | 12.2276 | 12.3693 | 12.532 | 12.6962 | 12.8198 | 12.8684 | 12.989 | 13.1325 | 13.3192 | 13.5582 | 13.7228 | 13.6845 | 13.5885 | 13.7075 | 13.8894 | 13.975 | 13.9673 | 14.0423 | 14.0622 | 14.0231 | 14.0877 | 14.1526 | 14.2178
Ladbroke Grove | Step Change | 17.858 | 17.5483 | 16.6777 | 14.3695 | 12.2737 | 11.7315 | 11.4235 | 11.2722 | 11.2361 | 11.2396 | 11.307 | 11.408 | 11.5601 | 11.6421 | 11.6214 | 11.7495 | 11.9226 | 12.1735 | 12.4938 | 12.7047 | 12.6952 | 12.6343 | 12.8051 | 13.0591 | 13.1943 | 13.1905 | 13.2295 | 13.2298 | 13.2025 | 13.2728 | 13.3435 | 13.4145
Laverton North | Step Change | 18.9294 | 18.6315 | 17.5394 | 14.7546 | 12.506 | 12.0248 | 11.737 | 11.6769 | 11.6641 | 11.6229 | 11.6706 | 11.7809 | 11.9735 | 12.0777 | 12.0358 | 12.1456 | 12.3052 | 12.6178 | 13.0233 | 13.3313 | 13.4677 | 13.5128 | 13.7247 | 13.9977 | 14.1532 | 14.1703 | 14.2545 | 14.2935 | 14.2853 | 14.3828 | 14.4809 | 14.5797
Mintaro GT | Step Change | 19.0157 | 18.5597 | 17.1792 | 14.6885 | 12.7862 | 12.2565 | 11.9485 | 11.7972 | 11.7611 | 11.7646 | 11.832 | 11.933 | 12.0851 | 12.1671 | 12.1464 | 12.2745 | 12.4476 | 12.6985 | 13.0188 | 13.2297 | 13.214 | 13.1468 | 13.3176 | 13.5716 | 13.7068 | 13.703 | 13.742 | 13.8096 | 13.9222 | 14.1391 | 14.3594 | 14.5831
Mortlake | Step Change | 17.3926 | 17.1186 | 16.2833 | 14.1998 | 12.4228 | 11.9427 | 11.6479 | 11.5131 | 11.4219 | 11.3497 | 11.3701 | 11.4744 | 11.6649 | 11.7671 | 11.7231 | 11.8308 | 11.9884 | 12.299 | 13.0595 | 13.3818 | 13.179 | 13.2256 | 13.4515 | 13.7385 | 13.8883 | 13.9153 | 14.2912 | 14.665 | 14.776 | 14.9975 | 15.2223 | 15.4506
Newport | Step Change | 16.8629 | 16.5505 | 15.6838 | 13.6966 | 11.9935 | 11.4998 | 11.212 | 11.1519 | 11.1391 | 11.0979 | 11.1456 | 11.2559 | 11.4485 | 11.5527 | 11.5108 | 11.6206 | 11.7802 | 12.0928 | 12.4983 | 12.8063 | 12.9489 | 13.0003 | 13.2122 | 13.4852 | 13.6407 | 13.6578 | 13.742 | 13.7848 | 13.7804 | 13.878 | 13.9763 | 14.0752
Oakey Power Station | Step Change | 17.7314 | 17.0173 | 15.3714 | 13.6682 | 12.3968 | 11.8968 | 11.8968 | 11.8968 | 11.8968 | 11.8968 | 12.0218 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.2718 | 12.3968 | 12.3968 | 12.5218 | 12.6468 | 12.6468 | 12.6468 | 12.6468 | 12.6468 | 12.6468 | 12.6468 | 12.6468 | 12.6468 | 12.6468 | 12.6468 | 12.6468 | 12.6468
Osborne | Step Change | 14.6741 | 14.3012 | 13.7322 | 12.3292 | 10.7362 | 10.1565 | 9.8485 | 9.6972 | 9.6611 | 9.6646 | 9.732 | 9.833 | 9.9851 | 10.0671 | 10.0464 | 10.1745 | 10.3476 | 10.5985 | 10.9188 | 11.1297 | 11.139 | 11.0968 | 11.2676 | 11.5216 | 11.6568 | 11.653 | 11.692 | 11.7036 | 11.6877 | 11.7582 | 11.8292 | 11.9006
Pelican Point | Step Change | 14.6741 | 14.3012 | 13.7322 | 12.3292 | 10.7362 | 10.1565 | 9.8485 | 9.6972 | 9.6611 | 9.6646 | 9.732 | 9.833 | 9.9851 | 10.0671 | 10.0464 | 10.1745 | 10.3476 | 10.5985 | 10.9188 | 11.1297 | 11.139 | 11.0968 | 11.2676 | 11.5216 | 11.6568 | 11.653 | 11.692 | 11.7036 | 11.6877 | 11.7582 | 11.8292 | 11.9006
Quarantine | Step Change | 17.3458 | 16.9218 | 15.8534 | 14.1657 | 12.7862 | 12.2565 | 11.9485 | 11.7972 | 11.7611 | 11.7646 | 11.832 | 11.933 | 12.0851 | 12.1671 | 12.1464 | 12.2745 | 12.4476 | 12.6985 | 13.0188 | 13.2297 | 13.214 | 13.1468 | 13.3176 | 13.5716 | 13.7068 | 13.703 | 13.742 | 13.7385 | 13.7074 | 13.7776 | 13.8483 | 13.9192
Roma | Step Change | 16.0253 | 15.5175 | 14.3457 | 13.0392 | 11.8968 | 11.3968 | 11.3968 | 11.3968 | 11.3968 | 11.3968 | 11.5218 | 11.6468 | 11.6468 | 11.6468 | 11.6468 | 11.7718 | 11.8968 | 11.8968 | 12.0218 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.1468 | 12.1468
Smithfield Energy Facility | Step Change | 19.1347 | 18.739 | 17.4071 | 14.9062 | 13.0024 | 12.2782 | 11.8088 | 11.6972 | 11.7054 | 11.7925 | 11.9363 | 12.1011 | 12.2674 | 12.393 | 12.4438 | 12.5665 | 12.7121 | 12.9008 | 13.1418 | 13.3085 | 13.2771 | 13.1879 | 13.3089 | 13.4928 | 13.5841 | 13.586 | 13.6703 | 13.7005 | 13.6702 | 13.7411 | 13.8123 | 13.8839
Somerton | Step Change | 16.8629 | 16.5505 | 15.6838 | 13.6966 | 11.9935 | 11.4998 | 11.212 | 11.1519 | 11.1391 | 11.0979 | 11.1456 | 11.2559 | 11.4485 | 11.5527 | 11.5108 | 11.6206 | 11.7802 | 12.0928 | 12.4983 | 12.8063 | 12.9489 | 13.0003 | 13.2122 | 13.4852 | 13.6407 | 13.6578 | 13.742 | 13.7848 | 13.7804 | 13.878 | 13.9763 | 14.0752
Swanbank E GT | Step Change | 13.6519 | 13.3183 | 12.6173 | 11.4249 | 10.1238 | 9.6816 | 9.6902 | 9.6687 | 9.6635 | 9.6595 | 9.7937 | 9.9227 | 9.9187 | 9.8881 | 9.8268 | 9.9172 | 10.0422 | 10.0422 | 10.1753 | 10.3003 | 10.2922 | 10.3228 | 10.3868 | 10.574 | 10.9024 | 11.0952 | 11.114 | 11.1868 | 11.3321 | 11.4793 | 11.6284 | 11.7794
Tallawarra | Step Change | 14.8321 | 14.4807 | 13.9431 | 12.5491 | 10.9524 | 10.1782 | 9.7088 | 9.5972 | 9.6054 | 9.6925 | 9.8363 | 10.0011 | 10.1674 | 10.293 | 10.3438 | 10.4665 | 10.6121 | 10.8008 | 11.0418 | 11.2085 | 11.2021 | 11.1379 | 11.2589 | 11.4428 | 11.5341 | 11.536 | 11.6203 | 11.6656 | 11.6506 | 11.7217 | 11.7933 | 11.8653
Tallawarra B | Step Change | 17.4799 | 17.1012 | 16.0748 | 14.1343 | 12.4899 | 11.7532 | 11.2838 | 11.1722 | 11.1804 | 11.2675 | 11.4113 | 11.5761 | 11.7424 | 11.868 | 11.9188 | 12.0415 | 12.1871 | 12.3758 | 12.6168 | 12.7835 | 12.7583 | 12.6754 | 12.7964 | 12.9803 | 13.0716 | 13.0735 | 13.1578 | 13.1918 | 13.1653 | 13.2362 | 13.3075 | 13.3792
Tamar Valley Combined Cycle | Step Change | 14.8659 | 14.5305 | 14.0242 | 12.5774 | 11.0071 | 10.4893 | 10.2016 | 10.1415 | 10.1287 | 10.0875 | 10.1352 | 10.2454 | 10.438 | 10.5423 | 10.5004 | 10.6101 | 10.7698 | 11.0824 | 11.4879 | 11.7959 | 11.9505 | 12.0139 | 12.2258 | 12.4988 | 12.6426 | 12.6365 | 12.6982 | 12.7305 | 12.7199 | 12.8033 | 12.8872 | 12.9717
Tamar Valley Peaking | Step Change | 14.8659 | 14.5305 | 14.0242 | 12.5774 | 11.0071 | 10.4893 | 10.2016 | 10.1415 | 10.1287 | 10.0875 | 10.1352 | 10.2454 | 10.438 | 10.5423 | 10.5004 | 10.6101 | 10.7698 | 11.0824 | 11.4879 | 11.7959 | 11.9505 | 12.0139 | 12.2258 | 12.4988 | 12.6426 | 12.6365 | 12.6982 | 12.7305 | 12.7199 | 12.8033 | 12.8872 | 12.9717
Torrens Island A | Step Change | 17.3458 | 16.9218 | 15.8534 | 14.1657 | 12.7862 | 12.2565 | 11.9485 | 11.7972 | 11.7611 | 11.7646 | 11.832 | 11.933 | 12.0851 | 12.1671 | 12.1464 | 12.2745 | 12.4476 | 12.6985 | 13.0188 | 13.2297 | 13.214 | 13.1468 | 13.3176 | 13.5716 | 13.7068 | 13.703 | 13.742 | 13.7385 | 13.7074 | 13.7776 | 13.8483 | 13.9192
Torrens Island B | Step Change | 17.3458 | 16.9218 | 15.8534 | 14.1657 | 12.7862 | 12.2565 | 11.9485 | 11.7972 | 11.7611 | 11.7646 | 11.832 | 11.933 | 12.0851 | 12.1671 | 12.1464 | 12.2745 | 12.4476 | 12.6985 | 13.0188 | 13.2297 | 13.214 | 13.1468 | 13.3176 | 13.5716 | 13.7068 | 13.703 | 13.742 | 13.8096 | 13.9222 | 14.1391 | 14.3594 | 14.5831
Townsville Power Station | Step Change | 13.261 | 13.0717 | 12.6843 | 11.6588 | 10.319 | 9.794 | 9.7755 | 9.7718 | 9.7745 | 9.7832 | 9.9136 | 10.0368 | 10.0458 | 10.0541 | 10.0604 | 10.1783 | 10.2914 | 10.3066 | 10.4539 | 10.6126 | 10.6422 | 10.6464 | 10.6464 | 10.6464 | 10.6464 | 10.6574 | 10.6726 | 10.6799 | 10.686 | 10.6921 | 10.6983 | 10.7044
Uranquinty | Step Change | 17.4605 | 17.0508 | 16.0819 | 14.1144 | 12.37 | 11.6958 | 11.284 | 11.2137 | 11.2289 | 11.2604 | 11.3598 | 11.5072 | 11.713 | 11.8347 | 11.8313 | 11.9561 | 12.1257 | 12.3834 | 12.7196 | 12.9411 | 12.9364 | 12.8789 | 13.0497 | 13.3135 | 13.4663 | 13.4843 | 13.5703 | 13.6949 | 13.8549 | 14.1199 | 14.39 | 14.6652
Valley Power | Step Change | 18.9294 | 18.6315 | 17.5394 | 14.7546 | 12.506 | 12.0248 | 11.737 | 11.6769 | 11.6641 | 11.6229 | 11.6706 | 11.7809 | 11.9735 | 12.0777 | 12.0358 | 12.1456 | 12.3052 | 12.6178 | 13.0233 | 13.3313 | 13.4677 | 13.5128 | 13.7247 | 13.9977 | 14.1532 | 14.1703 | 14.2545 | 14.3768 | 14.5372 | 14.8075 | 15.0828 | 15.3633
Yarwun Cogen | Step Change | 13.3721 | 13.1828 | 12.7953 | 11.3025 | 10.0078 | 10.0078 | 10.0078 | 10.0078 | 10.0078 | 10.1328 | 10.2578 | 10.2578 | 10.2578 | 10.2578 | 10.3828 | 10.5078 | 10.5078 | 10.6328 | 10.7578 | 10.7578 | 10.7578 | 10.7578 | 10.7578 | 10.7578 | 10.7578 | 10.7578 | 10.7847 | 10.8387 | 10.8928 | 10.9473 | 11.002 | 11.0571
New generating stations
NSW new CCGT | Step Change | 14.8321 | 14.4807 | 13.9431 | 12.5491 | 10.9524 | 10.1782 | 9.7088 | 9.5972 | 9.6054 | 9.6925 | 9.8363 | 10.0011 | 10.1674 | 10.293 | 10.3438 | 10.4665 | 10.6121 | 10.8008 | 11.0418 | 11.2085 | 11.2021 | 11.1379 | 11.2589 | 11.4428 | 11.5341 | 11.536 | 11.6203 | 11.6656 | 11.6506 | 11.7217 | 11.7933 | 11.8653
NSW new OCGT | Step Change | 19.4227 | 19.0263 | 17.693 | 15.1907 | 13.2925 | 12.5739 | 12.1031 | 11.9901 | 11.9969 | 12.0826 | 12.2249 | 12.3884 | 12.5533 | 12.6775 | 12.7269 | 12.8482 | 12.9924 | 13.1797 | 13.4194 | 13.5847 | 13.5487 | 13.455 | 13.5746 | 13.7572 | 13.8447 | 13.8402 | 13.9183 | 13.9416 | 13.9055 | 13.9722 | 14.0392 | 14.1065
QLD new CCGT | Step Change | 13.6519 | 13.3183 | 12.6173 | 11.4249 | 10.365 | 10.1656 | 10.1747 | 10.1521 | 10.1466 | 10.1425 | 10.2834 | 10.4188 | 10.4146 | 10.3825 | 10.3181 | 10.4131 | 10.5443 | 10.5443 | 10.6841 | 10.8153 | 10.6782 | 10.5809 | 10.6465 | 10.8384 | 11.175 | 11.3725 | 11.3918 | 11.382 | 11.4454 | 11.5941 | 11.7447 | 11.8972
QLD new OCGT | Step Change | 17.7492 | 16.9716 | 15.315 | 13.6509 | 12.659 | 12.4495 | 12.4452 | 12.4448 | 12.4462 | 12.4488 | 12.5815 | 12.7121 | 12.7153 | 12.7186 | 12.7212 | 12.8491 | 12.9749 | 12.9807 | 13.1211 | 13.2636 | 13.1155 | 12.9594 | 12.9581 | 12.9585 | 12.9594 | 12.9627 | 12.9696 | 12.879 | 12.7871 | 12.7902 | 12.7933 | 12.7964
SA new CCGT | Step Change | 14.6741 | 14.3012 | 13.7322 | 12.3292 | 10.7362 | 10.1565 | 9.8485 | 9.6972 | 9.6611 | 9.6646 | 9.732 | 9.833 | 9.9851 | 10.0671 | 10.0464 | 10.1745 | 10.3476 | 10.5985 | 10.9188 | 11.1297 | 11.139 | 11.0968 | 11.2676 | 11.5216 | 11.6568 | 11.653 | 11.692 | 11.7752 | 11.9043 | 12.1233 | 12.3463 | 12.5735
SA new OCGT | Step Change | 18.4368 | 18.054 | 16.9285 | 14.529 | 12.53 | 11.994 | 11.686 | 11.5347 | 11.4986 | 11.5021 | 11.5695 | 11.6705 | 11.8226 | 11.9046 | 11.8839 | 12.012 | 12.1851 | 12.436 | 12.7563 | 12.9672 | 12.9546 | 12.8906 | 13.0614 | 13.3153 | 13.4506 | 13.4467 | 13.4857 | 13.4841 | 13.4549 | 13.5252 | 13.5959 | 13.6669
TAS new CCGT | Step Change | 14.8659 | 14.5305 | 14.0242 | 12.5774 | 11.0071 | 10.4893 | 10.2016 | 10.1415 | 10.1287 | 10.0875 | 10.1352 | 10.2454 | 10.438 | 10.5423 | 10.5004 | 10.6101 | 10.7698 | 11.0824 | 11.4879 | 11.7959 | 11.9505 | 12.0139 | 12.2258 | 12.4988 | 12.6426 | 12.6365 | 12.6982 | 12.7305 | 12.7199 | 12.8033 | 12.8872 | 12.9717
TAS new OCGT | Step Change | 19.4671 | 19.1692 | 18.0771 | 15.2923 | 13.0571 | 12.5893 | 12.3016 | 12.2415 | 12.2287 | 12.1875 | 12.2352 | 12.3454 | 12.538 | 12.6423 | 12.6004 | 12.7101 | 12.8698 | 13.1824 | 13.5879 | 13.8959 | 14.0255 | 14.0639 | 14.2758 | 14.5488 | 14.6926 | 14.6865 | 14.7482 | 14.8435 | 14.9754 | 15.2197 | 15.468 | 15.7204
VIC new CCGT | Step Change | 15.8962 | 15.591 | 14.6116 | 12.2256 | 10.1997 | 9.6623 | 9.3745 | 9.3144 | 9.3016 | 9.2604 | 9.3081 | 9.4184 | 9.611 | 9.7152 | 9.6733 | 9.7831 | 9.9427 | 10.2553 | 10.6608 | 10.9688 | 11.1333 | 11.2065 | 11.4184 | 11.6914 | 11.847 | 11.864 | 11.9483 | 12.0044 | 12.0135 | 12.1115 | 12.2103 | 12.31
VIC new OCGT | Step Change | 17.8962 | 17.591 | 16.6116 | 14.2256 | 12.2497 | 11.7623 | 11.4745 | 11.4144 | 11.4016 | 11.3604 | 11.4081 | 11.5184 | 11.711 | 11.8152 | 11.7733 | 11.8831 | 12.0427 | 12.3553 | 12.7608 | 13.0688 | 13.2083 | 13.2565 | 13.4684 | 13.7414 | 13.897 | 13.914 | 13.9983 | 14.0392 | 14.0329 | 14.1304 | 14.2286 | 14.3274
Progressive Change
Generator | Gas price scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Bairnsdale | Progressive Change | 18.7663 | 18.3614 | 16.7669 | 14.3004 | 12.9476 | 12.6879 | 12.4427 | 12.409 | 12.5536 | 12.6387 | 12.838 | 13.3323 | 13.8041 | 14.0473 | 14.0916 | 14.2276 | 14.3644 | 14.3713 | 14.5446 | 14.8088 | 15.0538 | 15.3693 | 15.5757 | 15.7377 | 15.8661 | 16.102 | 16.6424 | 16.9871 | 17.1637 | 17.4699 | 17.7815 | 18.0987
Barcaldine Power Station | Progressive Change | 17.7867 | 17.076 | 15.821 | 14.2827 | 13.2563 | 13.1801 | 13.1244 | 13.0851 | 13.0919 | 13.0992 | 13.1811 | 13.4309 | 13.6042 | 13.6446 | 13.6623 | 13.8066 | 13.9577 | 13.9851 | 14.1214 | 14.2464 | 14.2464 | 14.2504 | 14.2657 | 14.2845 | 14.2921 | 14.2921 | 14.2997 | 14.3127 | 14.3233 | 14.3339 | 14.3445 | 14.3551
Barker Inlet Power Station | Progressive Change | 17.3633 | 16.9965 | 15.7322 | 13.7641 | 12.65 | 12.5153 | 12.4628 | 12.4504 | 12.4667 | 12.3537 | 12.4046 | 12.8909 | 13.372 | 13.6417 | 13.7036 | 13.8637 | 14.0165 | 14.0002 | 14.1507 | 14.3674 | 14.5499 | 14.8179 | 14.9967 | 15.103 | 15.1457 | 15.138 | 15.7405 | 16.3669 | 16.5407 | 16.8394 | 17.1434 | 17.453
Bell Bay Three | Progressive Change | 19.2541 | 18.9861 | 17.5613 | 14.8497 | 13.2493 | 13.1019 | 13.0827 | 13.1557 | 13.2297 | 13.1217 | 13.112 | 13.5824 | 14.1327 | 14.4886 | 14.6474 | 14.9388 | 15.1868 | 15.2301 | 15.4454 | 15.7478 | 15.9863 | 16.2675 | 16.4757 | 16.6212 | 16.7264 | 16.9514 | 17.4647 | 17.7782 | 17.9292 | 18.2146 | 18.5046 | 18.7991
Bolivar Power Station | Progressive Change | 19.0534 | 18.5829 | 16.8616 | 14.4022 | 13.1625 | 13.0403 | 12.9878 | 12.9754 | 12.9917 | 12.8787 | 12.9296 | 13.4159 | 13.897 | 14.1667 | 14.2286 | 14.3887 | 14.5415 | 14.519 | 14.6632 | 14.8799 | 15.0624 | 15.3304 | 15.5092 | 15.6155 | 15.6582 | 15.6505 | 16.253 | 16.8754 | 17.0449 | 17.3428 | 17.6459 | 17.9543
Braemar | Progressive Change | 17.8274 | 17.0495 | 15.7949 | 14.3526 | 13.3732 | 13.3229 | 13.2717 | 13.2263 | 13.2291 | 13.2367 | 13.3212 | 13.5615 | 13.7178 | 13.7449 | 13.7462 | 13.8712 | 13.9937 | 13.9924 | 14.1187 | 14.2443 | 14.2462 | 14.2481 | 14.2462 | 14.243 | 14.2411 | 14.2405 | 14.2424 | 14.2439 | 14.2432 | 14.2424 | 14.2416 | 14.2409
Braemar 2 Power Station | Progressive Change | 17.8274 | 17.0495 | 15.7949 | 14.3526 | 13.3732 | 13.3229 | 13.2717 | 13.2263 | 13.2291 | 13.2367 | 13.3212 | 13.5615 | 13.7178 | 13.7449 | 13.7462 | 13.8712 | 13.9937 | 13.9924 | 14.1187 | 14.2443 | 14.2462 | 14.2481 | 14.2462 | 14.243 | 14.2411 | 14.2405 | 14.2424 | 14.2439 | 14.2432 | 14.2424 | 14.2416 | 14.2409
Colongra | Progressive Change | 19.6453 | 19.2159 | 17.408 | 14.9394 | 13.7928 | 13.5515 | 13.3042 | 13.2632 | 13.3993 | 13.4875 | 13.691 | 14.1832 | 14.653 | 14.894 | 14.9362 | 15.0701 | 15.2111 | 15.1304 | 15.1937 | 15.3909 | 15.5205 | 15.6984 | 15.8489 | 16.0374 | 16.1771 | 16.3968 | 16.9589 | 17.3508 | 17.5466 | 17.8751 | 18.2098 | 18.5508
Condamine A | Progressive Change | 13.9673 | 13.7677 | 13.4582 | 12.3739 | 11.3857 | 11.3355 | 11.2849 | 11.2389 | 11.2385 | 11.2423 | 11.325 | 11.5659 | 11.7216 | 11.7468 | 11.7468 | 11.8718 | 11.9968 | 11.9968 | 12.1218 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468
Darling Downs | Progressive Change | 13.9673 | 13.7677 | 13.4582 | 12.3739 | 11.3857 | 11.3355 | 11.2849 | 11.2389 | 11.2385 | 11.2423 | 11.325 | 11.5659 | 11.7216 | 11.7468 | 11.7468 | 11.8718 | 11.9968 | 11.9968 | 12.1218 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468 | 12.2468
Dry Creek GT | Progressive Change | 19.0534 | 18.5829 | 16.8616 | 14.4022 | 13.1625 | 13.0403 | 12.9878 | 12.9754 | 12.9917 | 12.8787 | 12.9296 | 13.4159 | 13.897 | 14.1667 | 14.2286 | 14.3887 | 14.5415 | 14.519 | 14.6632 | 14.8799 | 15.0624 | 15.3304 | 15.5092 | 15.6155 | 15.6582 | 15.6505 | 16.253 | 16.8754 | 17.0449 | 17.3428 | 17.6459 | 17.9543
Hallett GT | Progressive Change | 17.3633 | 16.9965 | 15.7322 | 13.7641 | 12.65 | 12.5153 | 12.4628 | 12.4504 | 12.4667 | 12.3537 | 12.4046 | 12.8909 | 13.372 | 13.6417 | 13.7036 | 13.8637 | 14.0165 | 14.0002 | 14.1507 | 14.3674 | 14.5499 | 14.8179 | 14.9967 | 15.103 | 15.1457 | 15.138 | 15.7405 | 16.3669 | 16.5407 | 16.8394 | 17.1434 | 17.453
Jeeralang A | Progressive Change | 16.6278 | 16.4263 | 15.3979 | 13.4141 | 12.1856 | 12.0123 | 11.9931 | 12.0661 | 12.1401 | 12.0321 | 12.0224 | 12.4928 | 13.0431 | 13.399 | 13.5578 | 13.8492 | 14.0972 | 14.1535 | 14.3818 | 14.6842 | 14.9226 | 15.2039 | 15.412 | 15.5448 | 15.644 | 15.8814 | 16.3863 | 16.691 | 16.8445 | 17.1247 | 17.4095 | 17.6991
Jeeralang B | Progressive Change | 16.6278 | 16.4263 | 15.3979 | 13.4141 | 12.1856 | 12.0123 | 11.9931 | 12.0661 | 12.1401 | 12.0321 | 12.0224 | 12.4928 | 13.0431 | 13.399 | 13.5578 | 13.8492 | 14.0972 | 14.1535 | 14.3818 | 14.6842 | 14.9226 | 15.2039 | 15.412 | 15.5448 | 15.644 | 15.8814 | 16.3863 | 16.691 | 16.8445 | 17.1247 | 17.4095 | 17.6991
Kurri Kurri | Progressive Change | 19.6453 | 19.2159 | 17.408 | 14.9394 | 13.7928 | 13.5515 | 13.3042 | 13.2632 | 13.3993 | 13.4875 | 13.691 | 14.1832 | 14.653 | 14.894 | 14.9362 | 15.0701 | 15.2111 | 15.1304 | 15.1937 | 15.3909 | 15.5205 | 15.6984 | 15.8489 | 16.0374 | 16.1771 | 16.3968 | 16.9589 | 17.3508 | 17.5466 | 17.8751 | 18.2098 | 18.5508
Ladbroke Grove | Progressive Change | 17.6416 | 17.4376 | 16.4001 | 14.13 | 12.65 | 12.5153 | 12.4628 | 12.4504 | 12.4667 | 12.3537 | 12.4046 | 12.8909 | 13.372 | 13.6417 | 13.7036 | 13.8637 | 14.0165 | 14.0002 | 14.1507 | 14.3674 | 14.5499 | 14.8179 | 14.9967 | 15.103 | 15.1457 | 15.138 | 15.7405 | 16.3669 | 16.5407 | 16.8394 | 17.1434 | 17.453
Laverton North | Progressive Change | 18.7164 | 18.4484 | 17.0236 | 14.312 | 12.6981 | 12.5373 | 12.5181 | 12.5911 | 12.6651 | 12.5571 | 12.5474 | 13.0178 | 13.5681 | 13.924 | 14.0828 | 14.3742 | 14.6222 | 14.6722 | 14.8943 | 15.1967 | 15.4351 | 15.7164 | 15.9245 | 16.0573 | 16.1565 | 16.3939 | 16.8988 | 17.1995 | 17.3488 | 17.6284 | 17.9124 | 18.201
Mintaro GT | Progressive Change | 19.0534 | 18.5829 | 16.8616 | 14.4022 | 13.1625 | 13.0403 | 12.9878 | 12.9754 | 12.9917 | 12.8787 | 12.9296 | 13.4159 | 13.897 | 14.1667 | 14.2286 | 14.3887 | 14.5415 | 14.519 | 14.6632 | 14.8799 | 15.0624 | 15.3304 | 15.5092 | 15.6155 | 15.6582 | 15.6505 | 16.253 | 16.8754 | 17.0449 | 17.3428 | 17.6459 | 17.9543
Mortlake | Progressive Change | 17.2221 | 17.0308 | 16.0057 | 13.92 | 12.6216 | 12.4724 | 12.451 | 12.5015 | 12.5427 | 12.3468 | 12.2677 | 12.7277 | 13.2595 | 13.6134 | 13.7701 | 14.0594 | 14.3054 | 14.3573 | 14.5811 | 14.8815 | 15.1822 | 15.5756 | 15.8293 | 15.9257 | 16.0032 | 16.2805 | 16.8942 | 17.2924 | 17.4782 | 17.7959 | 18.1195 | 18.4489
Newport | Progressive Change | 16.6278 | 16.4263 | 15.3979 | 13.4141 | 12.1856 | 12.0123 | 11.9931 | 12.0661 | 12.1401 | 12.0321 | 12.0224 | 12.4928 | 13.0431 | 13.399 | 13.5578 | 13.8492 | 14.0972 | 14.1535 | 14.3818 | 14.6842 | 14.9226 | 15.2039 | 15.412 | 15.5448 | 15.644 | 15.8814 | 16.3863 | 16.691 | 16.8445 | 17.1247 | 17.4095 | 17.6991
Oakey Power Station | Progressive Change | 17.7867 | 17.076 | 15.821 | 14.3381 | 13.3857 | 13.3355 | 13.2849 | 13.2389 | 13.2385 | 13.2423 | 13.325 | 13.5659 | 13.7216 | 13.7468 | 13.7468 | 13.8718 | 13.9968 | 13.9968 | 14.1218 | 14.2468 | 14.2468 | 14.2468 | 14.2468 | 14.2468 | 14.2468 | 14.2468 | 14.2468 | 14.2468 | 14.2468 | 14.2468 | 14.2468 | 14.2468
Osborne | Progressive Change | 14.6591 | 14.4583 | 13.925 | 12.393 | 11.1125 | 10.9403 | 10.8878 | 10.8754 | 10.8917 | 10.7787 | 10.8296 | 11.3159 | 11.797 | 12.0667 | 12.1286 | 12.2887 | 12.4415 | 12.444 | 12.6132 | 12.8299 | 13.0124 | 13.2804 | 13.4592 | 13.5655 | 13.6082 | 13.6005 | 14.203 | 14.8415 | 15.0286 | 15.3298 | 15.6372 | 15.9506
Pelican Point | Progressive Change | 14.6591 | 14.4583 | 13.925 | 12.393 | 11.1125 | 10.9403 | 10.8878 | 10.8754 | 10.8917 | 10.7787 | 10.8296 | 11.3159 | 11.797 | 12.0667 | 12.1286 | 12.2887 | 12.4415 | 12.444 | 12.6132 | 12.8299 | 13.0124 | 13.2804 | 13.4592 | 13.5655 | 13.6082 | 13.6005 | 14.203 | 14.8415 | 15.0286 | 15.3298 | 15.6372 | 15.9506
Quarantine | Progressive Change | 17.3633 | 16.9965 | 15.7322 | 13.7641 | 12.65 | 12.5153 | 12.4628 | 12.4504 | 12.4667 | 12.3537 | 12.4046 | 12.8909 | 13.372 | 13.6417 | 13.7036 | 13.8637 | 14.0165 | 14.0002 | 14.1507 | 14.3674 | 14.5499 | 14.8179 | 14.9967 | 15.103 | 15.1457 | 15.138 | 15.7405 | 16.3669 | 16.5407 | 16.8394 | 17.1434 | 17.453
Roma | Progressive Change | 16.3017 | 15.7928 | 14.8932 | 13.701 | 12.8857 | 12.8355 | 12.7849 | 12.7389 | 12.7385 | 12.7423 | 12.825 | 13.0659 | 13.2216 | 13.2468 | 13.2468 | 13.3718 | 13.4968 | 13.4968 | 13.6218 | 13.7468 | 13.7468 | 13.7468 | 13.7468 | 13.7468 | 13.7468 | 13.7468 | 13.7468 | 13.7468 | 13.7468 | 13.7468 | 13.7468 | 13.7468
Smithfield Energy Facility | Progressive Change | 19.2133 | 18.7849 | 16.9792 | 14.5127 | 13.3576 | 13.1079 | 12.8627 | 12.8238 | 12.9621 | 13.0524 | 13.258 | 13.7523 | 14.2241 | 14.4673 | 14.5116 | 14.6476 | 14.7906 | 14.7169 | 14.7873 | 14.9865 | 15.1181 | 15.2978 | 15.4503 | 15.6407 | 15.7863 | 16.0155 | 16.5869 | 16.9898 | 17.196 | 17.5326 | 17.8759 | 18.2259
Somerton | Progressive Change | 16.6278 | 16.4263 | 15.3979 | 13.4141 | 12.1856 | 12.0123 | 11.9931 | 12.0661 | 12.1401 | 12.0321 | 12.0224 | 12.4928 | 13.0431 | 13.399 | 13.5578 | 13.8492 | 14.0972 | 14.1535 | 14.3818 | 14.6842 | 14.9226 | 15.2039 | 15.412 | 15.5448 | 15.644 | 15.8814 | 16.3863 | 16.691 | 16.8445 | 17.1247 | 17.4095 | 17.6991
Swanbank E GT | Progressive Change | 14.3387 | 14.0296 | 13.5188 | 12.312 | 11.2865 | 11.2499 | 11.1999 | 11.1343 | 11.1339 | 11.1378 | 11.2204 | 11.4613 | 11.617 | 11.6422 | 11.6422 | 11.7672 | 11.8922 | 11.8922 | 12.0172 | 12.1422 | 12.1422 | 12.1463 | 12.1615 | 12.1802 | 12.1872 | 12.1858 | 12.1922 | 12.2041 | 12.2139 | 12.2237 | 12.2335 | 12.2433
Tallawarra | Progressive Change | 14.7482 | 14.6156 | 14.122 | 12.5923 | 11.3076 | 11.0079 | 10.7627 | 10.7238 | 10.8621 | 10.9524 | 11.158 | 11.6523 | 12.1241 | 12.3673 | 12.4116 | 12.5476 | 12.6906 | 12.6419 | 12.7373 | 12.9365 | 13.0681 | 13.2478 | 13.4003 | 13.5907 | 13.7363 | 13.9655 | 14.5369 | 14.9562 | 15.1806 | 15.5215 | 15.8701 | 16.2265
Tallawarra B | Progressive Change | 17.496 | 17.1813 | 15.8803 | 13.9087 | 12.8451 | 12.5829 | 12.3377 | 12.2988 | 12.4371 | 12.5274 | 12.733 | 13.2273 | 13.6991 | 13.9423 | 13.9866 | 14.1226 | 14.2656 | 14.1982 | 14.2748 | 14.474 | 14.6056 | 14.7853 | 14.9378 | 15.1282 | 15.2738 | 15.503 | 16.0744 | 16.4824 | 16.6956 | 17.0365 | 17.3851 | 17.7415
Tamar Valley Combined Cycle | Progressive Change | 14.5954 | 14.5006 | 14.1062 | 12.5509 | 11.1993 | 11.0019 | 10.9827 | 11.0557 | 11.1297 | 11.0217 | 11.012 | 11.4824 | 12.0327 | 12.3886 | 12.5474 | 12.8388 | 13.0868 | 13.1551 | 13.3954 | 13.6978 | 13.9363 | 14.2175 | 14.4257 | 14.5712 | 14.6764 | 14.9014 | 15.4147 | 15.7441 | 15.9122 | 16.2004 | 16.4938 | 16.7925
Tamar Valley Peaking | Progressive Change | 14.5954 | 14.5006 | 14.1062 | 12.5509 | 11.1993 | 11.0019 | 10.9827 | 11.0557 | 11.1297 | 11.0217 | 11.012 | 11.4824 | 12.0327 | 12.3886 | 12.5474 | 12.8388 | 13.0868 | 13.1551 | 13.3954 | 13.6978 | 13.9363 | 14.2175 | 14.4257 | 14.5712 | 14.6764 | 14.9014 | 15.4147 | 15.7441 | 15.9122 | 16.2004 | 16.4938 | 16.7925
Torrens Island A | Progressive Change | 17.3633 | 16.9965 | 15.7322 | 13.7641 | 12.65 | 12.5153 | 12.4628 | 12.4504 | 12.4667 | 12.3537 | 12.4046 | 12.8909 | 13.372 | 13.6417 | 13.7036 | 13.8637 | 14.0165 | 14.0002 | 14.1507 | 14.3674 | 14.5499 | 14.8179 | 14.9967 | 15.103 | 15.1457 | 15.138 | 15.7405 | 16.3669 | 16.5407 | 16.8394 | 17.1434 | 17.453
Torrens Island B | Progressive Change | 17.3633 | 16.9965 | 15.7322 | 13.7641 | 12.65 | 12.5153 | 12.4628 | 12.4504 | 12.4667 | 12.3537 | 12.4046 | 12.8909 | 13.372 | 13.6417 | 13.7036 | 13.8637 | 14.0165 | 14.0002 | 14.1507 | 14.3674 | 14.5499 | 14.8179 | 14.9967 | 15.103 | 15.1457 | 15.138 | 15.7405 | 16.3669 | 16.5407 | 16.8394 | 17.1434 | 17.453
Townsville Power Station | Progressive Change | 13.9673 | 13.7677 | 13.4582 | 12.3185 | 11.2563 | 11.1801 | 11.1244 | 11.0851 | 11.0919 | 11.0992 | 11.1811 | 11.4309 | 11.6042 | 11.6446 | 11.6623 | 11.8066 | 11.9577 | 11.9851 | 12.1214 | 12.2464 | 12.2464 | 12.2504 | 12.2657 | 12.2845 | 12.2921 | 12.2921 | 12.2997 | 12.3127 | 12.3233 | 12.3339 | 12.3445 | 12.3551
Uranquinty | Progressive Change | 17.4101 | 17.0888 | 15.877 | 13.8719 | 12.6713 | 12.4643 | 12.2949 | 12.273 | 12.3969 | 12.4271 | 12.573 | 13.0643 | 13.582 | 13.8685 | 13.9372 | 14.1074 | 14.267 | 14.2477 | 14.3952 | 14.6119 | 14.7944 | 15.0774 | 15.2634 | 15.4095 | 15.5316 | 15.7689 | 16.3151 | 16.6731 | 16.8512 | 17.1564 | 17.4673 | 17.7837
Valley Power | Progressive Change | 18.7164 | 18.4484 | 17.0236 | 14.312 | 12.6981 | 12.5373 | 12.5181 | 12.5911 | 12.6651 | 12.5571 | 12.5474 | 13.0178 | 13.5681 | 13.924 | 14.0828 | 14.3742 | 14.6222 | 14.6722 | 14.8943 | 15.1967 | 15.4351 | 15.7164 | 15.9245 | 16.0573 | 16.1565 | 16.3939 | 16.8988 | 17.1995 | 17.3488 | 17.6284 | 17.9124 | 18.201
Yarwun Cogen | Progressive Change | 14.0783 | 13.8787 | 13.5692 | 12.4849 | 11.498 | 11.4478 | 11.3982 | 11.3546 | 11.3543 | 11.3556 | 11.436 | 11.6769 | 11.8326 | 11.8578 | 11.8578 | 11.9828 | 12.1078 | 12.1078 | 12.2328 | 12.3578 | 12.3578 | 12.3578 | 12.3578 | 12.3578 | 12.3578 | 12.3578 | 12.3578 | 12.3887 | 12.4507 | 12.5129 | 12.5755 | 12.6384
New generating stations
NSW new CCGT | Progressive Change | 14.7482 | 14.6156 | 14.122 | 12.5923 | 11.3076 | 11.0079 | 10.7627 | 10.7238 | 10.8621 | 10.9524 | 11.158 | 11.6523 | 12.1241 | 12.3673 | 12.4116 | 12.5476 | 12.6906 | 12.6419 | 12.7373 | 12.9365 | 13.0681 | 13.2478 | 13.4003 | 13.5907 | 13.7363 | 13.9655 | 14.5369 | 14.8103 | 15.0347 | 15.5215 | 15.8701 | 16.2265
NSW new OCGT | Progressive Change | 19.5013 | 19.0722 | 17.2651 | 14.7972 | 13.6477 | 13.4036 | 13.1571 | 13.1168 | 13.2536 | 13.3424 | 13.5467 | 14.0395 | 14.51 | 14.7518 | 14.7947 | 14.9293 | 15.0709 | 14.9926 | 15.0583 | 15.2561 | 15.3864 | 15.5649 | 15.7161 | 15.9052 | 16.0468 | 16.2697 | 16.8349 | 17.0856 | 17.2848 | 17.761 | 18.0985 | 18.4425
QLD new CCGT | Progressive Change | 14.3387 | 14.0296 | 13.5188 | 12.312 | 11.5682 | 11.8124 | 11.7599 | 11.691 | 11.6906 | 11.6946 | 11.7814 | 12.0344 | 12.1979 | 12.2243 | 12.2243 | 12.3556 | 12.4868 | 12.3382 | 12.3176 | 12.4458 | 12.4458 | 12.4499 | 12.4655 | 12.4848 | 12.4918 | 12.4904 | 12.497 | 12.4133 | 12.3317 | 12.3459 | 12.3558 | 12.3658
QLD new OCGT | Progressive Change | 17.8138 | 17.0583 | 15.8036 | 14.3293 | 13.6671 | 13.9391 | 13.8837 | 13.8382 | 13.8425 | 13.8504 | 13.9382 | 14.1939 | 14.3639 | 14.397 | 14.4041 | 14.5421 | 14.6808 | 14.5145 | 14.4725 | 14.6011 | 14.6024 | 14.6051 | 14.609 | 14.6133 | 14.6146 | 14.6142 | 14.618 | 14.5151 | 14.4112 | 14.4156 | 14.4187 | 14.4217
SA new CCGT | Progressive Change | 14.6591 | 14.4583 | 13.925 | 12.393 | 11.1125 | 10.9403 | 10.8878 | 10.8754 | 10.8917 | 10.7787 | 10.8296 | 11.3159 | 11.797 | 12.0667 | 12.1286 | 12.2887 | 12.4415 | 12.444 | 12.6132 | 12.8299 | 13.0124 | 13.2804 | 13.4592 | 13.5655 | 13.6082 | 13.6005 | 14.203 | 14.7123 | 14.8993 | 15.3298 | 15.6372 | 15.9506
SA new OCGT | Progressive Change | 18.2547 | 17.8632 | 16.4082 | 14.1441 | 12.9062 | 12.7778 | 12.7253 | 12.7129 | 12.7292 | 12.6162 | 12.6671 | 13.1534 | 13.6345 | 13.9042 | 13.9661 | 14.1262 | 14.279 | 14.2596 | 14.4069 | 14.6237 | 14.8062 | 15.0742 | 15.253 | 15.3593 | 15.4019 | 15.3942 | 15.9967 | 16.6212 | 16.7928 | 17.0911 | 17.3947 | 17.7036
TAS new CCGT | Progressive Change | 14.5954 | 14.5006 | 14.1062 | 12.5509 | 11.1993 | 11.0019 | 10.9827 | 11.0557 | 11.1297 | 11.0217 | 11.012 | 11.4824 | 12.0327 | 12.3886 | 12.5474 | 12.8388 | 13.0868 | 13.1551 | 13.3954 | 13.6978 | 13.9363 | 14.2175 | 14.4257 | 14.5712 | 14.6764 | 14.9014 | 15.4147 | 15.6192 | 15.7873 | 16.2004 | 16.4938 | 16.7925
TAS new OCGT | Progressive Change | 19.2541 | 18.9861 | 17.5613 | 14.8497 | 13.2493 | 13.1019 | 13.0827 | 13.1557 | 13.2297 | 13.1217 | 13.112 | 13.5824 | 14.1327 | 14.4886 | 14.6474 | 14.9388 | 15.1868 | 15.2301 | 15.4454 | 15.7478 | 15.9863 | 16.2675 | 16.4757 | 16.6212 | 16.7264 | 16.9514 | 17.4647 | 17.6523 | 17.8033 | 18.2146 | 18.5046 | 18.7991
VIC new CCGT | Progressive Change | 15.6721 | 15.4373 | 14.2107 | 11.863 | 10.3919 | 10.1748 | 10.1556 | 10.2286 | 10.3026 | 10.1946 | 10.1849 | 10.6553 | 11.2056 | 11.5615 | 11.7203 | 12.0117 | 12.2597 | 12.3379 | 12.588 | 12.8904 | 13.1289 | 13.4101 | 13.6183 | 13.7511 | 13.8502 | 14.0876 | 14.5926 | 15.0043 | 15.3638 | 15.847 | 16.3454 | 16.8595
VIC new OCGT | Progressive Change | 17.6721 | 17.4373 | 16.2107 | 13.863 | 12.4419 | 12.2748 | 12.2556 | 12.3286 | 12.4026 | 12.2946 | 12.2849 | 12.7553 | 13.3056 | 13.6615 | 13.8203 | 14.1117 | 14.3597 | 14.4129 | 14.638 | 14.9404 | 15.1789 | 15.4601 | 15.6683 | 15.8011 | 15.9002 | 16.1376 | 16.6426 | 17.0375 | 17.3775 | 17.8542 | 18.3439 | 18.8471
Green Energy Exports
Generator | Gas price scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Bairnsdale | Green Energy Exports | 18.3191 | 17.6319 | 17.0673 | 14.7717 | 11.6081 | 10.746 | 10.6039 | 10.5147 | 10.3844 | 10.1188 | 9.9026 | 9.9025 | 9.9925 | 10.0642 | 10.0355 | 10.0652 | 10.1868 | 10.209 | 10.1527 | 10.0736 | 10.0926 | 10.2252 | 10.3314 | 10.4372 | 10.5303 | 10.5891 | 10.6527 | 10.668 | 10.6768 | 10.7647 | 10.8532 | 10.9425
Barcaldine Power Station | Green Energy Exports | 16.3028 | 15.4529 | 14.1699 | 12.808 | 11.1159 | 10.3602 | 10.3601 | 10.3545 | 10.3489 | 10.3166 | 10.4175 | 10.545 | 10.5524 | 10.5601 | 10.5892 | 10.7216 | 10.8517 | 10.7555 | 10.7734 | 10.9124 | 10.9125 | 10.9125 | 10.9125 | 10.9125 | 10.9125 | 10.9125 | 10.9125 | 10.8327 | 10.7528 | 10.7528 | 10.7528 | 10.7528
Barker Inlet Power Station | Green Energy Exports | 16.966 | 16.2571 | 15.0739 | 13.2833 | 11.2414 | 10.3991 | 10.2621 | 10.1582 | 9.987 | 9.6538 | 9.4199 | 9.4507 | 9.5262 | 9.6206 | 9.6685 | 9.7353 | 9.8667 | 9.905 | 9.9766 | 10.1214 | 10.2435 | 10.3462 | 10.4217 | 10.5274 | 10.6482 | 10.7438 | 10.8142 | 10.833 | 10.8551 | 10.9575 | 11.0609 | 11.1653
Bell Bay Three | Green Energy Exports | 19.1668 | 18.4725 | 17.9049 | 15.3896 | 11.8836 | 10.8798 | 10.7359 | 10.654 | 10.5021 | 10.2211 | 10.0256 | 10.0564 | 10.132 | 10.2263 | 10.2742 | 10.341 | 10.4724 | 10.5035 | 10.5679 | 10.7126 | 10.8381 | 10.9902 | 11.1118 | 11.2176 | 11.2912 | 11.3156 | 11.3618 | 11.3617 | 11.3498 | 11.4219 | 11.4945 | 11.5676
Bolivar Power Station | Green Energy Exports | 18.547 | 17.6224 | 16.1073 | 13.9919 | 11.7539 | 10.9241 | 10.7871 | 10.6832 | 10.512 | 10.1788 | 9.9449 | 9.9757 | 10.0512 | 10.1456 | 10.1935 | 10.2603 | 10.3917 | 10.4237 | 10.4891 | 10.6339 | 10.756 | 10.8587 | 10.9342 | 11.0399 | 11.1607 | 11.2563 | 11.3267 | 11.3417 | 11.3598 | 11.4621 | 11.5653 | 11.6694
Braemar | Green Energy Exports | 16.1516 | 15.2956 | 14.0161 | 12.7409 | 10.8911 | 9.8943 | 9.8937 | 9.8918 | 9.8918 | 9.8918 | 10.0149 | 10.1393 | 10.1405 | 10.1405 | 10.1393 | 10.2624 | 10.3886 | 10.3905 | 10.5149 | 10.6399 | 10.6399 | 10.6393 | 10.6374 | 10.6355 | 10.6349 | 10.6342 | 10.6355 | 10.6365 | 10.636 | 10.6355 | 10.635 | 10.6345
Braemar 2 Power Station | Green Energy Exports | 16.1516 | 15.2956 | 14.0161 | 12.7409 | 10.8911 | 9.8943 | 9.8937 | 9.8918 | 9.8918 | 9.8918 | 10.0149 | 10.1393 | 10.1405 | 10.1405 | 10.1393 | 10.2624 | 10.3886 | 10.3905 | 10.5149 | 10.6399 | 10.6399 | 10.6393 | 10.6374 | 10.6355 | 10.6349 | 10.6342 | 10.6355 | 10.6365 | 10.636 | 10.6355 | 10.635 | 10.6345
Colongra | Green Energy Exports | 19.106 | 18.3755 | 17.7374 | 15.4965 | 12.4453 | 11.6097 | 11.4654 | 11.374 | 11.2416 | 10.9739 | 10.795 | 10.8322 | 10.9201 | 11.029 | 11.077 | 11.1439 | 11.2635 | 11.2709 | 11.3151 | 11.4443 | 11.5495 | 11.6245 | 11.6705 | 11.7615 | 11.8872 | 11.9939 | 12.0471 | 12.0331 | 12.0364 | 12.1288 | 12.2218 | 12.3156
Condamine A | Green Energy Exports | 12.8717 | 12.6786 | 12.3826 | 11.0883 | 8.8968 | 7.8968 | 7.8968 | 7.8968 | 7.8968 | 7.8968 | 8.0218 | 8.1468 | 8.1468 | 8.1468 | 8.1468 | 8.2718 | 8.3968 | 8.3968 | 8.5218 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468
Darling Downs | Green Energy Exports | 12.8717 | 12.6786 | 12.3826 | 11.0883 | 8.8968 | 7.8968 | 7.8968 | 7.8968 | 7.8968 | 7.8968 | 8.0218 | 8.1468 | 8.1468 | 8.1468 | 8.1468 | 8.2718 | 8.3968 | 8.3968 | 8.5218 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468 | 8.6468
Dry Creek GT | Green Energy Exports | 18.547 | 17.6224 | 16.1073 | 13.9919 | 11.7539 | 10.9241 | 10.7871 | 10.6832 | 10.512 | 10.1788 | 9.9449 | 9.9757 | 10.0512 | 10.1456 | 10.1935 | 10.2603 | 10.3917 | 10.4237 | 10.4891 | 10.6339 | 10.756 | 10.8587 | 10.9342 | 11.0399 | 11.1607 | 11.2563 | 11.3267 | 11.3417 | 11.3598 | 11.4621 | 11.5653 | 11.6694
Hallett GT | Green Energy Exports | 16.966 | 16.2571 | 15.0739 | 13.2833 | 11.2414 | 10.3991 | 10.2621 | 10.1582 | 9.987 | 9.6538 | 9.4199 | 9.4507 | 9.5262 | 9.6206 | 9.6685 | 9.7353 | 9.8667 | 9.905 | 9.9766 | 10.1214 | 10.2435 | 10.3462 | 10.4217 | 10.5274 | 10.6482 | 10.7438 | 10.8142 | 10.833 | 10.8551 | 10.9575 | 11.0609 | 11.1653
Jeeralang A | Green Energy Exports | 16.5869 | 16.0416 | 15.5336 | 13.6402 | 10.82 | 9.7902 | 9.6463 | 9.5644 | 9.4125 | 9.1315 | 8.936 | 8.9668 | 9.0424 | 9.1367 | 9.1846 | 9.2514 | 9.3828 | 9.4269 | 9.5043 | 9.649 | 9.7744 | 9.9266 | 10.0482 | 10.1539 | 10.2393 | 10.2855 | 10.3542 | 10.3811 | 10.391 | 10.4778 | 10.5654 | 10.6536
Jeeralang B | Green Energy Exports | 16.5869 | 16.0416 | 15.5336 | 13.6402 | 10.82 | 9.7902 | 9.6463 | 9.5644 | 9.4125 | 9.1315 | 8.936 | 8.9668 | 9.0424 | 9.1367 | 9.1846 | 9.2514 | 9.3828 | 9.4269 | 9.5043 | 9.649 | 9.7744 | 9.9266 | 10.0482 | 10.1539 | 10.2393 | 10.2855 | 10.3542 | 10.3811 | 10.391 | 10.4778 | 10.5654 | 10.6536
Kurri Kurri | Green Energy Exports | 19.106 | 18.3755 | 17.7374 | 15.4965 | 12.4453 | 11.6097 | 11.4654 | 11.374 | 11.2416 | 10.9739 | 10.795 | 10.8322 | 10.9201 | 11.029 | 11.077 | 11.1439 | 11.2635 | 11.2709 | 11.3151 | 11.4443 | 11.5495 | 11.6245 | 11.6705 | 11.7615 | 11.8872 | 11.9939 | 12.0471 | 12.0331 | 12.0364 | 12.1288 | 12.2218 | 12.3156
Ladbroke Grove | Green Energy Exports | 17.5682 | 17.0267 | 16.5277 | 14.2686 | 11.2414 | 10.3991 | 10.2621 | 10.1582 | 9.987 | 9.6538 | 9.4199 | 9.4507 | 9.5262 | 9.6206 | 9.6685 | 9.7353 | 9.8667 | 9.905 | 9.9766 | 10.1214 | 10.2435 | 10.3462 | 10.4217 | 10.5274 | 10.6482 | 10.7438 | 10.8142 | 10.833 | 10.8551 | 10.9575 | 11.0609 | 11.1653
Laverton North | Green Energy Exports | 18.6291 | 17.9348 | 17.3672 | 14.8519 | 11.3325 | 10.3152 | 10.1713 | 10.0894 | 9.9375 | 9.6565 | 9.461 | 9.4918 | 9.5674 | 9.6617 | 9.7096 | 9.7764 | 9.9078 | 9.9456 | 10.0168 | 10.1615 | 10.2869 | 10.4391 | 10.5607 | 10.6664 | 10.7518 | 10.798 | 10.8667 | 10.8898 | 10.8958 | 10.9825 | 11.0698 | 11.1579
Mintaro GT | Green Energy Exports | 18.547 | 17.6224 | 16.1073 | 13.9919 | 11.7539 | 10.9241 | 10.7871 | 10.6832 | 10.512 | 10.1788 | 9.9449 | 9.9757 | 10.0512 | 10.1456 | 10.1935 | 10.2603 | 10.3917 | 10.4237 | 10.4891 | 10.6339 | 10.756 | 10.8587 | 10.9342 | 11.0399 | 11.1607 | 11.2563 | 11.3267 | 11.3417 | 11.3598 | 11.4621 | 11.5653 | 11.6694
Mortlake | Green Energy Exports | 18.8944 | 18.1945 | 17.6225 | 15.1632 | 11.7271 | 10.944 | 10.935 | 10.6342 | 10.3044 | 9.9357 | 9.6816 | 9.7104 | 9.7838 | 9.8761 | 9.922 | 9.9867 | 10.116 | 10.1494 | 10.2161 | 10.3588 | 10.4823 | 10.6325 | 10.7521 | 10.8559 | 10.9355 | 10.9723 | 11.0319 | 11.0459 | 11.0441 | 11.124 | 11.2044 | 11.2855
Newport | Green Energy Exports | 16.5869 | 16.0416 | 15.5336 | 13.6402 | 10.82 | 9.7902 | 9.6463 | 9.5644 | 9.4125 | 9.1315 | 8.936 | 8.9668 | 9.0424 | 9.1367 | 9.1846 | 9.2514 | 9.3828 | 9.4269 | 9.5043 | 9.649 | 9.7744 | 9.9266 | 10.0482 | 10.1539 | 10.2393 | 10.2855 | 10.3542 | 10.3811 | 10.391 | 10.4778 | 10.5654 | 10.6536
Oakey Power Station | Green Energy Exports | 16.3028 | 15.4529 | 14.1699 | 12.8168 | 10.8968 | 9.8968 | 9.8968 | 9.8968 | 9.8968 | 9.8968 | 10.0218 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.2718 | 10.3968 | 10.3968 | 10.5218 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468 | 10.6468
Osborne | Green Energy Exports | 14.4364 | 14.0726 | 13.4204 | 11.7995 | 9.7039 | 8.8241 | 8.6871 | 8.5832 | 8.412 | 8.0788 | 7.8449 | 7.8757 | 7.9512 | 8.0456 | 8.0935 | 8.1603 | 8.2917 | 8.3487 | 8.4391 | 8.5839 | 8.706 | 8.8087 | 8.8842 | 8.9899 | 9.1107 | 9.2063 | 9.2767 | 9.307 | 9.3409 | 9.444 | 9.5484 | 9.6538
Pelican Point | Green Energy Exports | 14.4364 | 14.0726 | 13.4204 | 11.7995 | 9.7039 | 8.8241 | 8.6871 | 8.5832 | 8.412 | 8.0788 | 7.8449 | 7.8757 | 7.9512 | 8.0456 | 8.0935 | 8.1603 | 8.2917 | 8.3487 | 8.4391 | 8.5839 | 8.706 | 8.8087 | 8.8842 | 8.9899 | 9.1107 | 9.2063 | 9.2767 | 9.307 | 9.3409 | 9.444 | 9.5484 | 9.6538
Quarantine | Green Energy Exports | 16.966 | 16.2571 | 15.0739 | 13.5333 | 11.7539 | 10.9241 | 10.7871 | 10.6832 | 10.512 | 10.1788 | 9.9449 | 9.9757 | 10.0512 | 10.1456 | 10.1935 | 10.2603 | 10.3917 | 10.4237 | 10.4891 | 10.6339 | 10.756 | 10.8587 | 10.9342 | 11.0399 | 11.1607 | 11.2563 | 11.3267 | 11.3417 | 11.3598 | 11.4621 | 11.5653 | 11.6694
Roma | Green Energy Exports | 15.0086 | 14.4088 | 13.4876 | 12.2815 | 10.3968 | 9.3968 | 9.3968 | 9.3968 | 9.3968 | 9.3968 | 9.5218 | 9.6468 | 9.6468 | 9.6468 | 9.6468 | 9.7718 | 9.8968 | 9.8968 | 10.0218 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.1468 | 10.1468
Smithfield Energy Facility | Green Energy Exports | 18.674 | 17.9445 | 17.3085 | 15.0697 | 12.0101 | 11.166 | 11.0239 | 10.9347 | 10.8044 | 10.5388 | 10.362 | 10.4012 | 10.4912 | 10.6023 | 10.6524 | 10.7214 | 10.843 | 10.8575 | 10.9086 | 11.0398 | 11.147 | 11.224 | 11.2719 | 11.3649 | 11.4964 | 11.6126 | 11.6751 | 11.6717 | 11.6844 | 11.7837 | 11.8838 | 11.9848
Somerton | Green Energy Exports | 16.5869 | 16.0416 | 15.5336 | 13.6402 | 10.82 | 9.7902 | 9.6463 | 9.5644 | 9.4125 | 9.1315 | 8.936 | 8.9668 | 9.0424 | 9.1367 | 9.1846 | 9.2514 | 9.3828 | 9.4269 | 9.5043 | 9.649 | 9.7744 | 9.9266 | 10.0482 | 10.1539 | 10.2393 | 10.2855 | 10.3542 | 10.3811 | 10.391 | 10.4778 | 10.5654 | 10.6536
Swanbank E GT | Green Energy Exports | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 8.9799 | 8.0075 | 7.8587 | 7.7922 | 7.7922 | 7.7922 | 7.9172 | 8.0422 | 8.0422 | 8.0422 | 8.0422 | 8.1672 | 8.2922 | 8.2922 | 8.4172 | 8.5422 | 8.5422 | 8.5422 | 8.5422 | 8.5422 | 8.5415 | 8.5402 | 8.5389 | 8.5379 | 8.5371 | 8.5364 | 8.5356 | 8.5348
Tallawarra | Green Energy Exports | 14.5406 | 14.2715 | 13.863 | 12.2304 | 9.9601 | 9.066 | 8.9239 | 8.8347 | 8.7044 | 8.4388 | 8.262 | 8.3012 | 8.3912 | 8.5023 | 8.5524 | 8.6214 | 8.743 | 8.7825 | 8.8586 | 8.9898 | 9.097 | 9.174 | 9.2219 | 9.3149 | 9.4464 | 9.5626 | 9.6251 | 9.6369 | 9.6653 | 9.7654 | 9.8666 | 9.9687
Tallawarra B | Green Energy Exports | 17.0842 | 16.5318 | 15.9833 | 14.1123 | 11.4976 | 10.641 | 10.4989 | 10.4097 | 10.2794 | 10.0138 | 9.837 | 9.8762 | 9.9662 | 10.0773 | 10.1274 | 10.1964 | 10.318 | 10.3387 | 10.3961 | 10.5273 | 10.6345 | 10.7115 | 10.7594 | 10.8524 | 10.9839 | 11.1001 | 11.1626 | 11.1632 | 11.1803 | 11.2804 | 11.3816 | 11.4837
Tamar Valley Combined Cycle | Green Energy Exports | 14.6287 | 14.322 | 13.9092 | 12.2752 | 9.8336 | 8.7798 | 8.6359 | 8.554 | 8.4021 | 8.1211 | 7.9256 | 7.9564 | 8.032 | 8.1263 | 8.1742 | 8.241 | 8.3724 | 8.4285 | 8.5179 | 8.6626 | 8.7881 | 8.9402 | 9.0618 | 9.1676 | 9.2412 | 9.2656 | 9.3118 | 9.3268 | 9.3303 | 9.4029 | 9.4761 | 9.5498
Tamar Valley Peaking | Green Energy Exports | 14.6287 | 14.322 | 13.9092 | 12.2752 | 9.8336 | 8.7798 | 8.6359 | 8.554 | 8.4021 | 8.1211 | 7.9256 | 7.9564 | 8.032 | 8.1263 | 8.1742 | 8.241 | 8.3724 | 8.4285 | 8.5179 | 8.6626 | 8.7881 | 8.9402 | 9.0618 | 9.1676 | 9.2412 | 9.2656 | 9.3118 | 9.3268 | 9.3303 | 9.4029 | 9.4761 | 9.5498
Torrens Island A | Green Energy Exports | 16.966 | 16.2571 | 15.0739 | 13.5333 | 11.7539 | 10.9241 | 10.7871 | 10.6832 | 10.512 | 10.1788 | 9.9449 | 9.9757 | 10.0512 | 10.1456 | 10.1935 | 10.2603 | 10.3917 | 10.4237 | 10.4891 | 10.6339 | 10.756 | 10.8587 | 10.9342 | 11.0399 | 11.1607 | 11.2563 | 11.3267 | 11.3417 | 11.3598 | 11.4621 | 11.5653 | 11.6694
Torrens Island B | Green Energy Exports | 16.966 | 16.2571 | 15.0739 | 13.5333 | 11.7539 | 10.9241 | 10.7871 | 10.6832 | 10.512 | 10.1788 | 9.9449 | 9.9757 | 10.0512 | 10.1456 | 10.1935 | 10.2603 | 10.3917 | 10.4237 | 10.4891 | 10.6339 | 10.756 | 10.8587 | 10.9342 | 11.0399 | 11.1607 | 11.2563 | 11.3267 | 11.3417 | 11.3598 | 11.4621 | 11.5653 | 11.6694
Townsville Power Station | Green Energy Exports | 12.8717 | 12.6786 | 12.3826 | 11.0795 | 8.8694 | 7.8669 | 7.8668 | 7.8614 | 7.8561 | 7.8253 | 7.9214 | 8.0429 | 8.0499 | 8.0572 | 8.085 | 8.211 | 8.335 | 8.3668 | 8.5106 | 8.6462 | 8.6464 | 8.6464 | 8.6464 | 8.6464 | 8.6464 | 8.6464 | 8.6464 | 8.6464 | 8.6464 | 8.6464 | 8.6464 | 8.6464
Uranquinty | Green Energy Exports | 17.0029 | 16.4536 | 15.9275 | 14.0109 | 11.3125 | 10.4247 | 10.2791 | 10.197 | 10.0616 | 9.7848 | 9.5893 | 9.6201 | 9.6956 | 9.79 | 9.8379 | 9.9047 | 10.0361 | 10.0724 | 10.142 | 10.2867 | 10.4121 | 10.5281 | 10.6134 | 10.7192 | 10.8367 | 10.9191 | 10.9791 | 10.9935 | 11.0085 | 11.1051 | 11.2025 | 11.3007
Valley Power | Green Energy Exports | 18.6291 | 17.9348 | 17.3672 | 14.8519 | 11.3325 | 10.3152 | 10.1713 | 10.0894 | 9.9375 | 9.6565 | 9.461 | 9.4918 | 9.5674 | 9.6617 | 9.7096 | 9.7764 | 9.9078 | 9.9456 | 10.0168 | 10.1615 | 10.2869 | 10.4391 | 10.5607 | 10.6664 | 10.7518 | 10.798 | 10.8667 | 10.8898 | 10.8958 | 10.9825 | 11.0698 | 11.1579
Yarwun Cogen | Green Energy Exports | 12.9828 | 12.7896 | 12.4937 | 11.1994 | 9.0078 | 8.0078 | 8.0078 | 8.0078 | 8.0078 | 8.0078 | 8.1328 | 8.2578 | 8.2578 | 8.2578 | 8.2578 | 8.3828 | 8.5078 | 8.5078 | 8.6328 | 8.7578 | 8.7578 | 8.7578 | 8.7578 | 8.7578 | 8.7578 | 8.7578 | 8.7578 | 8.7797 | 8.8236 | 8.8677 | 8.9121 | 8.9566
New generating stations
NSW new CCGT | Green Energy Exports | 14.5406 | 14.2715 | 13.863 | 12.2304 | 9.9601 | 9.066 | 8.9239 | 8.8347 | 8.7044 | 8.4388 | 8.262 | 8.3012 | 8.3912 | 8.5023 | 8.5524 | 8.6214 | 8.743 | 8.7825 | 8.8586 | 8.9898 | 9.097 | 9.174 | 9.2219 | 9.3149 | 9.4464 | 9.5626 | 9.6251 | 9.6369 | 9.6653 | 9.7654 | 9.8666 | 9.9687
NSW new OCGT | Green Energy Exports | 18.962 | 18.2318 | 17.5944 | 15.3542 | 12.3002 | 11.4618 | 11.3182 | 11.2276 | 11.0958 | 10.8288 | 10.6506 | 10.6885 | 10.7771 | 10.8868 | 10.9355 | 11.0031 | 11.1233 | 11.1331 | 11.1796 | 11.3095 | 11.4153 | 11.491 | 11.5376 | 11.6293 | 11.7569 | 11.8668 | 11.9231 | 11.9126 | 11.9191 | 12.0137 | 12.1091 | 12.2053
QLD new CCGT | Green Energy Exports | 13.4886 | 13.0195 | 12.4387 | 11.0985 | 9.1821 | 8.4078 | 8.2516 | 8.1818 | 8.1818 | 8.1818 | 8.3131 | 8.4443 | 8.4443 | 8.4443 | 8.4443 | 8.5756 | 8.7068 | 8.6032 | 8.6276 | 8.7558 | 8.7558 | 8.7558 | 8.7558 | 8.7558 | 8.755 | 8.7537 | 8.7524 | 8.6873 | 8.6225 | 8.6217 | 8.6209 | 8.6202
QLD new OCGT | Green Energy Exports | 16.202 | 15.348 | 14.0674 | 12.7633 | 11.1309 | 10.3794 | 10.3789 | 10.3757 | 10.3739 | 10.3631 | 10.4829 | 10.6125 | 10.6158 | 10.6184 | 10.6272 | 10.7575 | 10.8893 | 10.7719 | 10.7763 | 10.908 | 10.9081 | 10.9077 | 10.9064 | 10.9051 | 10.9047 | 10.9042 | 10.9051 | 10.826 | 10.7458 | 10.7455 | 10.7452 | 10.7448
SA new CCGT | Green Energy Exports | 14.4364 | 14.0726 | 13.4204 | 11.7995 | 9.7039 | 8.8241 | 8.6871 | 8.5832 | 8.412 | 8.0788 | 7.8449 | 7.8757 | 7.9512 | 8.0456 | 8.0935 | 8.1603 | 8.2917 | 8.3487 | 8.4391 | 8.5839 | 8.706 | 8.8087 | 8.8842 | 8.9899 | 9.1107 | 9.2063 | 9.2767 | 9.307 | 9.3409 | 9.444 | 9.5484 | 9.6538
SA new OCGT | Green Energy Exports | 18.0576 | 17.3245 | 16.3175 | 14.1302 | 11.4976 | 10.6616 | 10.5246 | 10.4207 | 10.2495 | 9.9163 | 9.6824 | 9.7132 | 9.7887 | 9.8831 | 9.931 | 9.9978 | 10.1292 | 10.1644 | 10.2329 | 10.3776 | 10.4997 | 10.6024 | 10.6779 | 10.7837 | 10.9045 | 11.0001 | 11.0704 | 11.0874 | 11.1074 | 11.2098 | 11.3131 | 11.4173
TAS new CCGT | Green Energy Exports | 14.6287 | 14.322 | 13.9092 | 12.2752 | 9.8336 | 8.7798 | 8.6359 | 8.554 | 8.4021 | 8.1211 | 7.9256 | 7.9564 | 8.032 | 8.1263 | 8.1742 | 8.241 | 8.3724 | 8.4285 | 8.5179 | 8.6626 | 8.7881 | 8.9402 | 9.0618 | 9.1676 | 9.2412 | 9.2656 | 9.3118 | 9.3268 | 9.3303 | 9.4029 | 9.4761 | 9.5498
TAS new OCGT | Green Energy Exports | 19.1668 | 18.4725 | 17.9049 | 15.3896 | 11.8836 | 10.8798 | 10.7359 | 10.654 | 10.5021 | 10.2211 | 10.0256 | 10.0564 | 10.132 | 10.2263 | 10.2742 | 10.341 | 10.4724 | 10.5035 | 10.5679 | 10.7126 | 10.8381 | 10.9902 | 11.1118 | 11.2176 | 11.2912 | 11.3156 | 11.3618 | 11.3617 | 11.3498 | 11.4219 | 11.4945 | 11.5676
VIC new CCGT | Green Energy Exports | 15.608 | 14.9882 | 14.4504 | 12.246 | 9.0263 | 7.9527 | 7.8088 | 7.7269 | 7.575 | 7.294 | 7.0985 | 7.1293 | 7.2049 | 7.2992 | 7.3471 | 7.4139 | 7.5453 | 7.6112 | 7.7105 | 7.8552 | 7.9807 | 8.1328 | 8.2544 | 8.3602 | 8.4455 | 8.4917 | 8.5605 | 8.6007 | 8.6243 | 8.7118 | 8.8002 | 8.8895
VIC new OCGT | Green Energy Exports | 17.608 | 16.9882 | 16.4504 | 14.246 | 11.0763 | 10.0527 | 9.9088 | 9.8269 | 9.675 | 9.394 | 9.1985 | 9.2293 | 9.3049 | 9.3992 | 9.4471 | 9.5139 | 9.6453 | 9.6862 | 9.7605 | 9.9052 | 10.0307 | 10.1828 | 10.3044 | 10.4102 | 10.4955 | 10.5417 | 10.6105 | 10.6355 | 10.6434 | 10.7302 | 10.8176 | 10.9057
Industrial fuel costs
Based on price forecasts delivered by ACIL Allen in July 2023.
Step Change
| Gas price scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Adelaide | Step Change | 13.0962 | 12.7361 | 12.2919 | 11.9023 | 10.7686 | 9.6326 | 9.2052 | 9.0468 | 9.2833 | 9.5615 | 9.6321 | 9.7379 | 9.8972 | 9.9832 | 9.9615 | 10.0957 | 10.277 | 10.2957 | 10.2521 | 10.334 | 10.4782 | 10.5718 | 10.7468 | 11.0069 | 11.1454 | 11.1415 | 11.1814 | 11.1473 | 11.0847 | 11.1564 | 11.2286 | 11.3013
Brisbane | Step Change | 12.8929 | 12.6583 | 12.1603 | 11.3123 | 10.1612 | 9.5023 | 9.345 | 9.295 | 9.4437 | 9.5827 | 9.7169 | 9.8459 | 9.8419 | 9.8113 | 9.75 | 9.8404 | 9.9654 | 9.9654 | 10.1247 | 10.2759 | 10.2678 | 10.2985 | 10.3624 | 10.5496 | 10.8788 | 11.0728 | 11.0929 | 11.174 | 11.3348 | 11.498 | 11.6635 | 11.8313
Darwin | Step Change | 7.0751 | 7.1076 | 7.173 | 7.2389 | 7.0032 | 6.5231 | 6.2814 | 6.2849 | 6.2705 | 6.5014 | 7.0046 | 7.4651 | 7.7381 | 7.811 | 7.8846 | 7.9589 | 8.034 | 8.1099 | 8.1865 | 8.2736 | 8.3794 | 8.4906 | 8.6115 | 8.7391 | 8.8378 | 8.9104 | 8.9756 | 9.0287 | 9.0738 | 9.1192 | 9.1648 | 9.2106
Hobart | Step Change | 14.9 | 14.7102 | 14.4455 | 14.1988 | 13.2772 | 11.6205 | 10.653 | 10.5964 | 10.5842 | 10.5454 | 10.5904 | 10.6943 | 10.8759 | 10.9742 | 10.9347 | 11.0382 | 11.1888 | 11.217 | 11.3264 | 11.6036 | 11.874 | 12.0636 | 12.2589 | 12.5106 | 12.6312 | 12.6017 | 12.6354 | 12.5813 | 12.4913 | 12.5528 | 12.6147 | 12.6769
Melbourne | Step Change | 12.3039 | 11.9627 | 11.5465 | 11.1549 | 10.0883 | 8.9464 | 8.4868 | 8.4239 | 8.7655 | 9.0774 | 9.1274 | 9.2429 | 9.4446 | 9.5538 | 9.5099 | 9.6249 | 9.7922 | 9.8836 | 10.069 | 10.3807 | 10.6811 | 10.8917 | 11.1088 | 11.3885 | 11.5478 | 11.5653 | 11.6516 | 11.659 | 11.618 | 11.7177 | 11.8182 | 11.9196
Sydney | Step Change | 13.2394 | 12.8949 | 12.4794 | 12.0902 | 10.9588 | 9.6339 | 9.0336 | 8.9167 | 9.2909 | 9.7477 | 9.8983 | 10.071 | 10.2452 | 10.3768 | 10.43 | 10.5586 | 10.711 | 10.6573 | 10.4404 | 10.3935 | 10.5227 | 10.5946 | 10.7185 | 10.9069 | 11.0004 | 11.0024 | 11.0887 | 11.0895 | 11.0282 | 11.1005 | 11.1733 | 11.2466
Progressive Change
| Gas price scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Adelaide | Progressive Change | 13.5455 | 13.3786 | 13.0115 | 11.8316 | 10.7154 | 10.3305 | 10.1227 | 10.1097 | 10.4863 | 10.7276 | 10.781 | 11.2904 | 11.521 | 11.528 | 11.5899 | 11.6085 | 11.6195 | 11.7699 | 11.8942 | 11.9177 | 12.1002 | 12.3683 | 12.547 | 12.6534 | 12.696 | 12.6883 | 13.2908 | 13.9366 | 14.1317 | 14.4349 | 14.7445 | 15.0608
Brisbane | Progressive Change | 13.2689 | 13.0506 | 12.6904 | 11.8129 | 10.9417 | 10.668 | 10.47 | 10.2747 | 10.54 | 11.0126 | 11.195 | 11.4359 | 11.5916 | 11.6168 | 11.6168 | 11.7418 | 11.8668 | 11.8668 | 11.9941 | 12.1215 | 12.1215 | 12.1255 | 12.1407 | 12.1595 | 12.1671 | 12.1671 | 12.1747 | 12.1876 | 12.1982 | 12.2088 | 12.2194 | 12.23
Darwin | Progressive Change | 7.1015 | 7.2881 | 7.5501 | 7.3797 | 7.056 | 6.8269 | 6.6748 | 6.6367 | 6.6456 | 6.686 | 6.7715 | 6.8097 | 7.0119 | 7.3268 | 7.4145 | 7.5477 | 7.6898 | 7.876 | 8.0518 | 8.1055 | 8.2219 | 8.3533 | 8.4223 | 8.7089 | 8.9559 | 8.9388 | 8.984 | 9.0564 | 9.1017 | 9.1472 | 9.1929 | 9.2389
Hobart | Progressive Change | 14.1355 | 14.064 | 13.817 | 12.6927 | 11.5812 | 11.1212 | 10.9103 | 10.9868 | 11.528 | 12.024 | 12.4738 | 13.2994 | 13.4534 | 13.2562 | 13.0773 | 12.9963 | 13.0845 | 13.3083 | 13.5771 | 13.752 | 13.9905 | 14.2717 | 14.4799 | 14.6253 | 14.7175 | 14.9166 | 15.4049 | 15.7137 | 15.8649 | 16.1355 | 16.4107 | 16.6906
Melbourne | Progressive Change | 12.478 | 12.4065 | 12.1595 | 11.0353 | 9.8821 | 9.3804 | 9.1695 | 9.246 | 9.8368 | 10.2369 | 10.2267 | 10.7195 | 11.033 | 11.1384 | 11.2972 | 11.448 | 11.5548 | 11.7787 | 12.017 | 12.1614 | 12.3998 | 12.6811 | 12.8892 | 13.022 | 13.1212 | 13.3585 | 13.8635 | 14.1879 | 14.3629 | 14.6469 | 14.9366 | 15.232
Sydney | Progressive Change | 13.5028 | 13.4116 | 13.106 | 11.9085 | 10.7758 | 10.2684 | 9.8462 | 9.8055 | 10.3852 | 10.9146 | 11.1301 | 11.6478 | 11.8613 | 11.8335 | 11.8778 | 11.8692 | 11.8673 | 11.9695 | 11.9412 | 11.8654 | 11.997 | 12.1768 | 12.3293 | 12.5197 | 12.6653 | 12.8945 | 13.4659 | 13.8939 | 14.1282 | 14.472 | 14.824 | 15.1847
Green Energy Exports
| Gas price scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Adelaide | Green Energy Exports | 11.2257 | 11.0357 | 10.6585 | 9.5683 | 7.7692 | 7.0495 | 7.2066 | 7.1077 | 6.9446 | 6.8807 | 6.9114 | 6.9408 | 7.0127 | 7.1026 | 7.1482 | 7.2119 | 7.337 | 7.4881 | 7.7151 | 7.898 | 8.0171 | 8.1173 | 8.191 | 8.2941 | 8.412 | 8.5053 | 8.5739 | 8.6709 | 8.7722 | 8.8746 | 8.9783 | 9.0831
Brisbane | Green Energy Exports | 11.3908 | 11.1355 | 10.8519 | 9.8928 | 8.1442 | 7.572 | 7.751 | 7.6846 | 7.6846 | 7.7421 | 7.9246 | 8.0496 | 8.0496 | 8.0496 | 8.0496 | 8.1746 | 8.2996 | 8.2996 | 8.4262 | 8.5528 | 8.5528 | 8.5528 | 8.5528 | 8.5528 | 8.5528 | 8.5528 | 8.5528 | 8.5528 | 8.5528 | 8.5528 | 8.5528 | 8.5528
Darwin | Green Energy Exports | 7.0751 | 7.1419 | 7.2073 | 7.2205 | 6.9047 | 6.1139 | 5.7181 | 5.7961 | 6.0072 | 6.1864 | 6.1735 | 6.1884 | 6.3553 | 6.7065 | 6.9506 | 7.0644 | 7.1481 | 7.2384 | 7.4014 | 7.5312 | 7.6789 | 7.8845 | 8.0045 | 8.056 | 8.1136 | 8.2242 | 8.3584 | 8.4348 | 8.477 | 8.5193 | 8.5619 | 8.6048
Hobart | Green Energy Exports | 11.8807 | 11.6986 | 11.3597 | 10.3614 | 8.4844 | 7.6218 | 7.7914 | 7.7135 | 7.5688 | 7.7307 | 7.9741 | 8.0035 | 8.0754 | 8.1653 | 8.2109 | 8.2745 | 8.3996 | 8.5507 | 8.7858 | 8.9767 | 9.099 | 9.2475 | 9.3661 | 9.4693 | 9.5283 | 9.527 | 9.5475 | 9.6096 | 9.6652 | 9.7211 | 9.7773 | 9.8339
Melbourne | Green Energy Exports | 10.4295 | 10.2474 | 9.9085 | 8.9103 | 7.0332 | 6.2637 | 6.425 | 6.265 | 6.185 | 6.278 | 6.4073 | 6.4367 | 6.5086 | 6.5985 | 6.6441 | 6.7077 | 6.8328 | 6.9839 | 7.2127 | 7.3973 | 7.5196 | 7.6681 | 7.7867 | 7.8899 | 7.9732 | 8.0182 | 8.0853 | 8.1868 | 8.2726 | 8.3594 | 8.4471 | 8.5357
Sydney | Green Energy Exports | 11.214 | 11.0851 | 10.7687 | 9.6965 | 7.8977 | 7.1635 | 7.3194 | 7.2344 | 7.1103 | 7.1432 | 7.2607 | 7.2981 | 7.3838 | 7.4896 | 7.5373 | 7.603 | 7.7188 | 7.8581 | 8.1028 | 8.2989 | 8.4034 | 8.4785 | 8.5253 | 8.616 | 8.7443 | 8.8576 | 8.9186 | 8.9999 | 9.0982 | 9.1976 | 9.298 | 9.3995
Liquid fuel price ($/GJ, real 2023 dollars)
Liquid Fuel Prices based on 2014 "Fuel and Technology Cost Review" by ACIL Allen, Medium scenario.
All modelling scenarios
Liquid fuel price | Liquid fuel price scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Liquid fuel | Medium | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Liquid fuel | Progressive Change | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Liquid fuel | Step Change | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Liquid fuel | Green Energy Exports | 42.6486 | 42.0245 | 41.4483 | 40.9133 | 40.4447 | 40.0274 | 39.6069 | 39.1984 | 38.8211 | 38.4794 | 38.1682 | 37.878 | 37.6028 | 37.3379 | 37.0813 | 36.8317 | 36.5865 | 36.3457 | 35.8851 | 35.4315 | 34.9849 | 34.5451 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112 | 34.112
Hydrogen price ($/GJ, real 2023 dollars)
Hydrogen price is developed based on a multi-sector model outcome (AusTIMES) conducted by CSIRO/CWA in 2022.
Hydrogen price | Hydrogen price scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Hydrogen | Progressive Change | N/A | N/A | N/A | 43.2178 | 42.0129 | 40.8384 | 39.6942 | 38.5805 | 37.4971 | 36.444 | 35.4213 | 34.429 | 33.4671 | 32.5355 | 31.6343 | 30.7635 | 29.923 | 29.1129 | 28.3332 | 27.5838 | 26.8648 | 26.1762 | 25.5179 | 24.89 | 24.2925 | 23.7253 | 23.1885 | 22.6821 | 22.2061 | 21.7604 | 21.3451 | 20.9601
Hydrogen | Step Change | N/A | N/A | N/A | 42.9047 | 41.4632 | 40.0621 | 38.7014 | 37.3811 | 36.1013 | 34.8619 | 33.6629 | 32.5043 | 31.3861 | 30.3084 | 29.271 | 28.2741 | 27.3176 | 26.4016 | 25.5259 | 24.6907 | 23.8959 | 23.1415 | 22.4275 | 21.754 | 21.1208 | 20.5281 | 19.9758 | 19.4639 | 18.9925 | 18.5615 | 18.1708 | 17.8206
Hydrogen | Green Energy Exports | N/A | N/A | N/A | 40.8769 | 39.4407 | 38.0458 | 36.6922 | 35.3798 | 34.1088 | 32.879 | 31.6904 | 30.5432 | 29.4372 | 28.3725 | 27.3491 | 26.3669 | 25.426 | 24.5264 | 23.6681 | 22.8511 | 22.0753 | 21.3408 | 20.6476 | 19.9956 | 19.3849 | 18.8155 | 18.2874 | 17.8005 | 17.355 | 16.9507 | 16.5876 | 16.2659
Hydrogen | Electrification alternatives | N/A | N/A | N/A | 42.9047 | 41.4632 | 40.0621 | 38.7014 | 37.3811 | 36.1013 | 34.8619 | 33.6629 | 32.5043 | 31.3861 | 30.3084 | 29.271 | 28.2741 | 27.3176 | 26.4016 | 25.5259 | 24.6907 | 23.8959 | 23.1415 | 22.4275 | 21.754 | 21.1208 | 20.5281 | 19.9758 | 19.4639 | 18.9925 | 18.5615 | 18.1708 | 17.8206
Biomethane price ($/GJ, real 2023 dollars)
Biomethane price is developed based on a multi-sector model outcome (AusTIMES) conducted by CSIRO/CWA in 2022.
Biomethane price | Biomethane price scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Biomethane | Progressive Change | 38.4507 | 37.4892 | 36.5556 | 35.6488 | 34.7682 | 34.1007 | 33.6051 | 32.7444 | 31.8838 | 30.8557 | 30.6301 | 30.5169 | 30.4121 | 30.3426 | 30.2727 | 30.1963 | 29.9997 | 28.1276 | 28.0515 | 28.0595 | 28.1135 | 28.099 | 27.9665 | 27.87 | 27.7603 | 27.6515 | 27.5436 | 27.4364 | 27.3301 | 28.3583 | 27.9124 | 27.8043
Biomethane | Step Change | 38.447 | 37.4822 | 36.5456 | 35.6362 | 34.7532 | 34.1365 | 33.7826 | 32.7905 | 32.5231 | 32.2849 | 31.9915 | 31.6439 | 31.3815 | 31.1416 | 30.8767 | 30.5815 | 30.2393 | 28.1371 | 28.0816 | 28.0839 | 28.122 | 28.1381 | 28.1151 | 28.0595 | 28.1472 | 28.1444 | 27.9413 | 27.8637 | 27.7094 | 28.1218 | 27.8601 | 27.7233
Biomethane | Green Energy Exports | 40.1058 | 40.7854 | 41.48 | 40.0804 | 38.624 | 37.9811 | 36.5455 | 36.7981 | 37.377 | 36.7069 | 35.6053 | 34.14 | 32.3603 | 30.3743 | 29.4727 | 28.6287 | 27.792 | 26.9088 | 26.3607 | 25.9179 | 25.5413 | 25.2476 | 24.9745 | 24.7105 | 24.5694 | 24.279 | 24.0865 | 24.0411 | 24.3857 | 24.3857 | 24.3857 | 24.3857
Biomethane | Electrification alternatives | 40.1058 | 40.7854 | 41.48 | 40.0804 | 38.624 | 37.9811 | 36.5455 | 36.7981 | 37.0032 | 35.6057 | 33.825 | 31.7502 | 29.3603 | 27.3743 | 26.4727 | 25.6287 | 24.792 | 23.9088 | 23.3607 | 22.9179 | 22.5413 | 22.2476 | 21.9745 | 21.7105 | 21.5694 | 21.279 | 21.0865 | 21.0411 | 21.3857 | 21.3857 | 21.3857 | 21.3857

## Retirement
Go to Assumptions Summary
Retirement
Announced retirements are based on participant submissions of expected closure years in theFebruary 2024 release of Generation information. Generators without announced retirement dates have been given an expected closure year of X years past the station's commissioning date, where X is the technical life of that technology type given in Aurecon's Costs and Technical Parameters workbook.
Units may be retired earlier than these dates by the model if doing so is found to be optimal.
Expected closure years |  |  |  | Retirement costs
Expected closure dates as per published values of the February 2024 update to AEMO's Generation Information and Generating unit expected closure year report. |  |  |  | Sourced from GHD 2018
https://www.aemo.com.au/Electricity/National-Electricity-Market-NEM/Planning-and-forecasting/Generation-information
Generator name | DUID | Expected Closure Year (Calendar year) | QEJP Expected Closure Year (Calendar year) - Phase 1 / Phase2 / Phase3 | Generator | Retirement / Rehabilitation cost (real 2023 $/MW)
Bayswater | BW01 | 2033 |  | Black Coal | 191000
Bayswater | BW02 | 2033 |  | Brown Coal | 191000
Bayswater | BW03 | 2033 |  | CCGT | 155000
Bayswater | BW04 | 2033 |  | OCGT | 54000
Callide B | CALL_B_1 | 2028 | 2027 / 2028 / 2035 | Pumped hydro | 128000
Callide B | CALL_B_2 | 2028 | 2027 / 2028 / 2035 | Single-axis tracking solar | 26000
Callide C | CPP_3 | 2051 |  | Wind | 13000
Callide C | CPP_4 | 2051
Eraring* | ER01 | 2025
Eraring | ER02 | 2025
Eraring | ER03 | 2025
Eraring | ER04 | 2025
Gladstone | GSTONE1 | 2035
Gladstone | GSTONE2 | 2035
Gladstone | GSTONE3 | 2035
Gladstone | GSTONE4 | 2035
Gladstone | GSTONE5 | 2035
Gladstone | GSTONE6 | 2035
Kogan Creek | KPP_1 | 2042 | 2035
Millmerran | MPP_1 | 2051
Millmerran | MPP_2 | 2051
Mt Piper | MP1 | 2040
Mt Piper | MP2 | 2040
Stanwell | STAN-1 | 2043 | 2030 / 2032 / 2035
Stanwell | STAN-2 | 2044 | 2030 / 2032 / 2035
Stanwell | STAN-3 | 2045 | 2030 / 2032 / 2035
Stanwell | STAN-4 | 2046 | 2030 / 2032 / 2035
Tarong | TARONG#1 | 2036 | 2030 / 2033 / 2035
Tarong | TARONG#2 | 2036 | 2030 / 2033 / 2035
Tarong | TARONG#3 | 2037 | 2030 / 2033 / 2035
Tarong | TARONG#4 | 2037 | 2030 / 2033 / 2035
Tarong North | TNPS1 | 2037 | 2030 / 2033 / 2035
Vales Point B | VP5 | 2033
Vales Point B | VP6 | 2033
Loy Yang A Power Station | LYA1 | 2035
Loy Yang A Power Station | LYA2 | 2035
Loy Yang A Power Station | LYA3 | 2035
Loy Yang A Power Station | LYA4 | 2035
Loy Yang B | LOYYB1 | 2047
Loy Yang B | LOYYB2 | 2047
Yallourn W | YWPS1 | 2028
Yallourn W | YWPS2 | 2028
Yallourn W | YWPS3 | 2028
Yallourn W | YWPS4 | 2028
Angaston | ANGAST1 | 2070
Bairnsdale | BDL01 | 2042
Bairnsdale | BDL02 | 2042
Barcaldine Power Station | BARCALDN | 2034
Barker Inlet Power Station | BARKIPS1 | 2044
Bell Bay Three | BBTHREE1 | 2040
Bell Bay Three | BBTHREE2 | 2040
Bell Bay Three | BBTHREE3 | 2040
Bolivar Power Station | BOLIVPS1 | 2045
Braemar | BRAEMAR1 | 2046
Braemar | BRAEMAR2 | 2046
Braemar | BRAEMAR3 | 2046
Braemar 2 Power Station | BRAEMAR5 | 2049
Braemar 2 Power Station | BRAEMAR6 | 2049
Braemar 2 Power Station | BRAEMAR7 | 2049
Colongra | CG1 | 2070
Colongra | CG2 | 2070
Colongra | CG3 | 2070
Colongra | CG4 | 2070
Condamine A | CPSA | 2039
Darling Downs | DDPS1 | 2045
Dry Creek GT | DRYCGT1 | 2030
Dry Creek GT | DRYCGT2 | 2030
Dry Creek GT | DRYCGT3 | 2030
Hallett GT | AGLHAL | 2032
Hallett GT | AGLHAL | 2032
Jeeralang A | JLA01 | 2039
Jeeralang A | JLA02 | 2039
Jeeralang A | JLA03 | 2039
Jeeralang A | JLA04 | 2039
Jeeralang B | JLB01 | 2039
Jeeralang B | JLB02 | 2039
Jeeralang B | JLB03 | 2039
Kogan Gas |  | 2066
Kurri Kurri OCGT |  | 2064
Ladbroke Grove | LADBROK1 | 2035
Ladbroke Grove | LADBROK2 | 2035
Laverton North | LNGS1 | 2070
Laverton North | LNGS2 | 2070
Lonsdale | LONSDALE | 2070
Mintaro GT | MINTARO | 2030
Mortlake | MORTLK11 | 2047
Mortlake | MORTLK12 | 2047
Mt Stuart | MSTUART1 | 2033
Mt Stuart | MSTUART2 | 2033
Mt Stuart | MSTUART3 | 2044
Newport | NPS | 2039
Oakey Power Station | OAKEY1 | 2050
Oakey Power Station | OAKEY2 | 2050
Osborne | OSB-AG | 2026
Pelican Point | PPCCGT | 2037
Port Lincoln GT | POR01 | 2027
Port Lincoln GT | POR03 | 2027
Port Stanvac 1 | PTSTAN1 | 2070
Quarantine | QPS1 | 2053
Quarantine | QPS2 | 2054
Quarantine | QPS3 | 2054
Quarantine | QPS4 | 2055
Quarantine | QPS5 | 2044
Roma | ROMA_7 | 2034
Roma | ROMA_8 | 2034
SA Hydrogen Turbine |  | 2065
Smithfield Energy Facility | SITHE01 | 2044
Smithfield Energy Facility | SITHE04 | 2044
Snapper Point Power Station | SNAPPER1 | 2046
Snuggery | SNUG1 | 2027
Somerton | AGLSOM | 2033
Swanbank E GT | SWAN_E | 2036
Tallawarra | TALWA1 | 2043
Tallawarra B | TALWB1 | 2053
Tamar Valley Combined Cycle | TVCC201 | 2050
Tamar Valley Peaking | TVPP104 | 2050
Torrens Island B | TORRB1 | 2026
Torrens Island B | TORRB2 | 2026
Torrens Island B | TORRB3 | 2026
Torrens Island B | TORRB4 | 2026
Townsville Power Station | YABULU | 2046
Townsville Power Station | YABULU2 | 2046
Uranquinty | URANQ11 | 2044
Uranquinty | URANQ12 | 2044
Uranquinty | URANQ13 | 2044
Uranquinty | URANQ14 | 2044
Valley Power | VPGS1 | 2070
Valley Power | VPGS2 | 2070
Valley Power | VPGS3 | 2070
Valley Power | VPGS4 | 2070
Valley Power | VPGS5 | 2070
Valley Power | VPGS6 | 2070
Yarwun Cogen | YARWUN_1 | 2050
Barron Gorge | BARRON-1 | 2042
Barron Gorge | BARRON-2 | 2042
Bastyan | BASTYAN | 2100
Blowering | BLOWERNG | 2070
Bogong / Mackay | MCKAY1 | 2057
Borumba |  | 2130
Catagunya / Liapootah / Wayatinah | LI_WY_CA | 2100
Cethana | CETHANA | 2100
Dartmouth | DARTM1 | 2057
Devils gate | DEVILS_G | 2100
Eildon | EILDON1 | 2057
Eildon | EILDON2 | 2057
Fisher | FISHER | 2100
Gordon | GORDON | 2100
Guthega | GUTHEGA | 2070
Hume Dam NSW | HUMENSW | 2057
Hume Dam VIC | HUMEV | 2057
John Butters | JBUTTERS | 2100
Kareeya | KAREEYA1 | 2037
Kareeya | KAREEYA2 | 2037
Kareeya | KAREEYA3 | 2037
Kareeya | KAREEYA4 | 2037
Kidston |  | 2105
Lake Echo | LK_ECHO | 2100
Lemonthyme / Wilmot | LEM_WIL | 2100
Mackintosh | MACKNTSH | 2100
Meadowbank | MEADOWBK | 2100
Murray 1 | MURRAY | 2070
Murray 2 | MURRAY | 2070
Poatina | POAT110 | 2100
Poatina | POAT220 | 2100
Reece | REECE1 | 2100
Reece | REECE2 | 2100
Shoalhaven | SHGEN | 2069
Snowy 2.0 | SNO2PH01 | 2129
Tarraleah | TARRALEA | 2100
Trevallyn | TREVALLN | 2100
Tribute | TRIBUTE | 2100
Tumut 3 | TUMUT3 | 2070
Tungatinah | TUNGATIN | 2100
Upper Tumut | UPPTUMUT | 2070
West Kiewa | WKIEWA1 | 2057
West Kiewa | WKIEWA2 | 2057
Wivenhoe | W/HOE#1 | 2084
Wivenhoe | W/HOE#2 | 2084
Adelaide Desalination Plant Solar Farm | ADPPV1 | 2041
Aramara Solar Farm |  | 2048
Avonlie Solar Farm | AVLSF1 | 2058
Banksia Solar Farm |  | 2055
Bannerton Solar Park | BANN1 | 2049
Beryl Solar Farm | BERYLSF1 | 2049
Bluegrass Solar Farm | BLUEGSF1 | 2057
Bolivar Waste Water Treatment Solar Farm | BOWWPV1 | 2045
Bomen Solar Farm | BOMENSF1 | 2050
Broken Hill Solar Farm | BROKENH1 | 2043
Bungala one Solar Farm | BNGSF1 | 2044
Bungala Two Solar Farm | BNGSF2 | 2044
Childers Solar Farm | CHILDSF1 | 2049
Clare Solar Farm | CLARESF1 | 2047
Clermont Solar Farm | CLERMSF1 | 2049
Cohuna Solar Farm | COHUNSF1 | 2045
Coleambally Solar Farm | COLEASF1 | 2038
Collinsville Solar Farm | CSPVPS1 | 2044
Columboola Solar Farm | COLUMSF1 | 2046
Corowa Solar Farm | CRWASF1 | 2051
Culcairn Solar Farm |  | 2050
Cultana Solar Farm |  | 2055
Darling Downs Solar Farm | DDSF1 | 2036
Darlington Point Solar Farm | DARLSF1 | 2055
Daydream Solar Farm | DAYDSF1 | 2048
Derby Solar Farm |  | 2053
Edenvale Solar Park |  | 2053
Emerald Solar Farm | EMERASF1 | 2048
Finley Solar Farm | FINLYSF1 | 2049
Frasers Solar Farm |  | 2054
Fulham Solar Farm |  | 2055
Gangarri Solar Farm | GANGARR1 | 2051
Gannawarra Solar Farm | GANNSF1 | 2048
Girgarre Solar Farm | GGSF | 2054
Glenrowan Solar Farm |  | 2053
Glenrowan West Solar Farm | GLRWNSF1 | 2051
Goonumbla Solar Farm | GOONSF1 | 2050
Gullen Range Solar Farm | GULLRSF1 | 2100
Gunnedah Solar Farm | GNNDHSF1 | 2056
Hamilton Solar Farm | HAMISF1 | 2048
Happy Valley Reservoir | HVWAPV1 | 2041
Haughton Solar Farm | HAUGHT11 | 2050
Hayman Solar Farm | HAYMSF1 | 2048
Hillston Sun Farm | HILLSTN1 | 2046
Horsham Solar Farm |  | 2066
Hughenden Solar Farm | HUGSF1 | 2048
Jemalong Solar | JEMALNG1 | 2050
Junee Solar Farm | JUNEESF1 | 2050
Karadoc Solar Farm | KARSF1 | 2048
Kennedy Energy Park Solar Farm | KEPSF1 | 2046
Kiamal Solar Farm – Stage 2 |  | 2056
Kiamal Solar Farm stage 1 | KIAMSF1 | 2049
Kidston Solar Farm | KSP1 | 2037
Lilyvale Solar Farm | LILYSF1 | 2048
Limondale Solar Farm 1 | LIMOSF11 | 2050
Limondale Solar Farm 2 | LIMOSF21 | 2050
Lockhart Hybrid Facility - Solar |  | 2055
Longreach Solar Farm | LRSF1 | 2043
Manildra Solar Farm | MANSLR1 | 2048
Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | MAPS2PV1 | 2041
Mannum Adelaide Pumping Station No 3 - MAPL3 (Tungkillo) | MAPS3PV1 | 2041
Mannum Solar Farm 2* | MANSF2 | 2058
Maryrorough Solar Farm | MARYRSF1 | 2048
Metz Solar Farm | METZSF1 | 2052
Middlemount Solar Farm | MIDDLSF1 | 2050
Molong Solar Farm | MOLNGSF1 | 2045
Moree Solar Farm | MOREESF1 | 2046
Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | MWPS1PV1 | 2031
Morgan To Whyalla Pipeline No 2 PS | MWPS2PV1 | 2041
Morgan To Whyalla Pipeline No 3 PS | MWPS3PV1 | 2045
Morgan To Whyalla Pipeline No 4 PS | MWPS4PV1 | 2041
Moura Solar Farm | MOUSF1 | 2057
Murray Bridge - Onkaparinga Pipeline Pump 2 | MBPS2PV1 | 2041
Nevertire Solar Farm | NEVERSF1 | 2049
New England Solar Farm | NEWENSF1 | 2052
New England Solar Farm - stage 2 |  | 2055
Numurkah Solar Farm | NUMURSF1 | 2044
Numurkah Solar Farm | NUMURSF2 | 2044
Nyngan Solar Plant | NYNGAN1 | 2042
Oakey 1 Solar Farm | OAKEYSF1 | 2043
Oakey 2 Solar Farm | OAKEY2SF | 2049
Parkes Solar Farm | PARSF1 | 2058
Port Augusta Renewable Energy Park - Solar |  | 2047
Quorn Park Solar Farm | QPSF | 2055
Riverina Solar Farm |  | 2047
Ross River Solar Farm | RRSF1 | 2043
Rugby Run Solar Farm | RUGBYR1 | 2049
Sebastopol Solar Farm | SEBSF1 | 2052
Stubbo Solar Farm |  | 2073
Sun Metals Corporation Solar Farm | SMCSF1 | 2042
Sunraysia Solar Farm | SUNRSF1 | 2049
Suntop Solar Farm | SUNTPSF1 | 2056
Susan River Solar Farm | SRSF1 | 2049
Tailem Bend Solar Farm | TBSF1 | 2049
Tailem Bend Solar Farm - stage 2 | TB2SF1 | 2053
Tamworth Solar Farm |  | 2053
Tilbuster Solar Farm |  | 2055
Wagga North Solar Farm | WAGGNSF1 | 2050
Walla Walla Solar Farm | WLWLSF1 | 2054
Walla Walla Solar Farm | WLWLSF2 | 2054
Wandoan South Solar Farm - stage 1 | WANDSF1 | 2053
Warwick Solar Farm | WARWSF1 | 2046
Warwick Solar Farm | WARWSF2 | 2045
Wellington North Solar Farm (Lightsource) | WELNSF1 | 2054
Wellington Solar Farm | WELLSF1 | 2051
Wemen Solar Farm | WEMENSF1 | 2049
West Wyalong Solar Farm | WSTWYSF1 | 2058
Western Downs Green Power Hub | WDGPH1 | 2046
White Rock Solar Farm | WRSF1 | 2043
Whitsunday Solar Farm | WHITSF1 | 2048
Winton Solar Farm | WINTSF1 | 2051
Wollar Solar Farm | WOLARSF1 | 2054
Woolooga Solar Farm | WOOLGSF1 | 2052
Wunghnu Solar Farm | WUNUSF1 | 2054
Wyalong Solar Farm | WYASF1 | 2053
Yarranlea Solar Farm | YARANSF1 | 2044
Yatpool Solar Farm | YATSF1 | 2050
Ararat Wind Farm | ARWF1 | 2047
Bald Hills Wind Farm | BALDHWF1 | 2040
Bango 973 Wind Farm | BANGOWF1 | 2045
Bango 999 Wind Farm | BANGOWF2 | 2045
Berrybank Wind Farm | BRYB1WF1 | 2050
Berrybank Wind Farm | BRYB2WF2 | 2052
Boco Rock Wind Farm | BOCORWF1 | 2040
Bodangora Wind Farm | BODWF1 | 2049
Bulgana Green Power Hub - Wind Farm | BULGANA1 | 2049
Canunda Wind Farm | CNUNDAWF | 2035
Capital Wind Farm | CAPTL_WF | 2040
Cathedral Rocks Wind Farm | CATHROCK | 2030
Cattle Hill Wind Farm | CTHLWF1 | 2044
Challicum Hills Wind Farm | CHALLHWF | 2033
Cherry Tree Wind Farm | CHYTWF1 | 2050
Clarke Creek Wind Farm | CLRKCWF1 | 2049
Clarke Creek Wind Farm | CLRKCWF2 | 2049
Clements Gap Wind Farm | CLEMGPWF | 2039
Collector Wind Farm | COLWF01 | 2046
Coopers Gap Wind Farm | COOPGWF1 | 2044
Coppabella Wind Farm | COPBEL | 2057
Crookwell 2 Wind Farm | CROOKWF2 | 2043
Crookwell 3 Wind Farm |  | 2054
Crowlands Wind Farm | CROWLWF1 | 2050
Crudine Ridge Wind Farm | CRURWF1 | 2041
Cullerin Range Wind Farm | CULLRGWF | 2038
Dulacca Wind Farm |  | 2053
Dundonnell Wind Farm | DUNDWF2 | 2045
Dundonnell Wind Farm | DUNDWF2 | 2045
Dundonnell Wind Farm | DUNDWF2 | 2045
Elaine Wind Farm | ELAINWF1 | 2049
Flyers Creek Wind Farm | FLYCRKWF | 2063
Golden Plains Wind Farm East |  | 2054
Goyder South Wind Farm 1A | GSWF1A | 2048
Goyder South Wind Farm 1B | GSWF1B | 2049
Granville Harbour Wind Farm | GRANWF1 | 2055
Gullen Range Wind Farm | GULLRWF1 | 2100
Gullen Range Wind Farm 2 | GULLRWF2 | 2120
Gunning Wind Farm | GUNNING1 | 2036
Hallett 4 North Brown Hill Wind Farm | NBHWF1 | 2036
Hallett 5 The Bluff Wind Farm | BLUFF1 | 2036
Hallett Stage 1 Brown Hill Wind Farm | HALLWF1 | 2043
Hallett Stage 2 Hallett Hill Wind Farm | HALLWF2 | 2035
Hawkesdale Wind Farm |  | 2054
Hornsdale Wind Farm Stage 1 | HDWF1 | 2056
Hornsdale Wind Farm Stage 2 | HDWF2 | 2057
Hornsdale Wind Farm Stage 3 | HDWF3 | 2057
Kaban Green Power Hub - Wind Farm | KABANWF1 | 2048
Kennedy Energy Park Wind Farm | KEPWF1 | 2046
Kiata Wind Farm | KiataWF1 | 2042
Lake Bonney 1 Wind Farm | LKBONNY1 | 2035
Lake Bonney 2 Wind Farm | LKBONNY2 | 2038
Lake Bonney 3 Wind Farm | LKBONNY3 | 2040
Lincoln Gap Wind Farm - stage 1 | LGAPWF1 | 2045
Lincoln Gap Wind Farm - stage 2 | LGAPWF2 | 2045
Macarthur Wind Farm | MACARTH1 | 2038
MacIntyre Wind Farm |  | 2053
Moorabool Wind Farm | MOORAWF1 | 2044
Mortlake South Wind Farm |  | 2047
Mortons Lane Wind Farm | MLWF1 | 2042
Mount Emerald Wind Farm | MEWF1 | 2043
Mount Millar Wind Farm | MTMILLAR | 2035
Mt Gellibrand Wind Farm | MTGELWF1 | 2043
Mt Mercer Wind Farm | MERCER01 | 2043
Murra Warra Wind Farm - stage 1 | MUWAWF1 | 2049
Murra Warra Wind Farm - stage 2 | MUWAWF2 | 2052
Musselroe Wind Farm | MUSSELR1 | 2050
Oaklands Hill Wind Farm | OAKLAND1 | 2037
Port Augusta Renewable Energy Park - Wind |  | 2052
Portland Wind Farm | PORTWF | 2040
Ryan Corner Wind Farm |  | 2054
Rye Park Wind Farm |  | 2048
Salt Creek Wind Farm | SALTCRK1 | 2043
Sapphire Wind Farm | SAPHWF1 | 2043
Silverton Wind Farm | STWF1 | 2043
Snowtown S2 Wind Farm | SNOWNTH1 | 2039
Snowtown S2 Wind Farm | SNOWNTH1 | 2039
Snowtown Wind Farm | SNOWTWN1 | 2033
Starfish Hill Wind Farm | STARHLWF | 2027
Stockyard Hill Wind Farm | STOCKYD1 | 2045
Taralga Wind Farm | TARALGA1 | 2040
Uungula Wind Farm |  | 2055
Wambo Wind Farm |  | 2055
Waterloo Wind Farm | WATERLWF | 2045
Wattle Point Wind Farm | WPWF | 2029
Waubra Wind Farm | WAUBRAWF | 2034
White Rock Wind Farm - Stage 1 | WRWF1 | 2038
Willogoleche Wind Farm | WGWF1 | 2043
Woodlawn Wind Farm | WOODLWN1 | 2041
Woolnorth Wind Farm | WOOLNTH1 | 2050
Woolsthorpe Wind Farm |  | 2055
Yaloak South Wind Farm | YSWF1 | 2048
Yambuk Wind Farm | YAMBUKWF | 2040
Yendon Wind Farm | YENDWF1 | 2049
Adelaide Desalination Plant BESS | ADPBA1G | 2041
Aldoga BESS Stage 1 |  | 2045
Ballarat Energy Storage System | BALBG1 | 2033
Blyth BESS |  | 2044
Bolivar Waste Water Treatment BESS | BOWWBA1G | 2045
Bouldercombe Battery project |  | 2042
Broken Hill BESS |  | 2043
Bulgana Green Power Hub BESS | BULBESG1 | 2049
Bungama Solar BESS |  | 2045
Capital Battery | CBESS1 | 2048
Chinchilla BESS |  | 2038
Christies Beach Wastewater Treatment Plant BESS | CBWWBA1G | 2041
Dalrymple BESS | DALNTH01 | 2030
Darlington Point Energy Storage System | DPNTBG1 | 2051
Derby Solar Project BESS |  | 2045
Eraring Big Battery |  | 2045
Fulham Solar Farm BESS |  | 2045
Gannawarra Energy Storage System | GANNBG1 | 2033
Gnarwarre BESS |  | 2054
Goulburn River BESS |  | 2045
Happy Valley Reservoir BESS | HVWABA1G | 2041
Hazelwood BESS | HBESSG1 | 2043
Hornsdale Power Reserve Unit 1 | HPRG1 | 2057
Horsham Solar Farm BESS |  | 2045
Kiamal Solar Farm – Stage 2 BESS |  | 2046
Koorangie Energy Storage System |  | 2055
Lake Bonney BESS | LBBG1 | 2034
Liddell BESS |  | 2045
Limondale BESS |  | 2045
Lincoln Gap Wind Farm BESS | LGAPWF1 | 2045
Lockhart Hybrid Facility - Battery |  | 2045
Melbourne Renewable Energy Hub - Side A |  | 2050
Mornington BESS |  | 2046
Mortlake Battery |  | 2047
Mt Fox BESS |  | 2046
New England Solar Farm BESS |  | 2046
Orana BESS | ORANA | 2065
Philip Island BESS | PIBESSG1 | 2038
Queanbeyan BESS |  | 2042
Quorn Park BESS | QPBESS | 2045
Rangebank BESS |  | 2044
Richmond Valley BESS |  | 2046
Riverina Energy Storage System 1 | RESS1G | 2051
Riverina Energy Storage System 2 | RIVNBG2 | 2051
Sapphire Wind Farm BESS |  | 2033
Silver City Energy Storage |  | 2057
Smithfield BESS |  | 2045
Stanwell BESS |  | 2047
Swanbank BESS |  | 2045
Tailem Bend Battery Project |  | 2048
Tamworth BESS |  | 2046
Tarong BESS |  | 2044
Templers BESS |  | 2049
Terang BESS | TRGBESS | 2045
Torrens Island BESS | TIBG1 / TIPL1 | 2043
Ulinda Park BESS | ULBESS | 2063
Victorian Big Battery | VBBG1 | 2041
Wallgrove Grid Battery project | WALGRVG1 | 2036
Wandoan South BESS | WANDBG1 | 2051
Waratah Super Battery | WARATAH | 2065
Western Downs Battery | WDBESS | 2048
Wooreen Energy Storage System |  | 2046
* Note that the recent announcement on the extension of Eraring Power Station (4 units) to August 2027 is reflected in the 'announced retirements', but not in the modelling.

## Heat rates
Go to Assumptions Summary
Heat rates
Encapsulates the efficiency of thermal generators for both Existing generators and New entrant technologies (as-gen, High Heating Value)
For key thermal power stations, as outlined in the ISP Methodology, affine heat rate curves may be applied in time-sequential modelling. These are outlined on the Affine Heat Rate worksheet.
Link: | Affine Heat Rates
Existing, Committed, Anticipated, and Additional generators |  |  | New entrant technologies
Generator | Technology | Heat rate (GJ/MWh) | Technology | Heat rate (GJ/MWh)
Bayswater | Steam Sub Critical | 9.4488 | OCGT (small GT) | 10.1902
Eraring | Steam Sub Critical | 9.5491 | OCGT (large GT) | 10.9312
Mt Piper | Steam Sub Critical | 9.2545 | CCGT | 7.2492
Vales Point B | Steam Sub Critical | 9.6774 | CCGT with CCS | 8.9631
Callide B | Steam Sub Critical | 9.1603 | Biomass | 17.37
Callide C | Steam Super Critical | 9.3023 | Hydrogen reciprocating engines | 11.7031
Gladstone | Steam Sub Critical | 9.4737 | Notes:
Kogan Creek | Steam Super Critical | 8.802 | 1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
Millmerran | Steam Super Critical | 9.2072
Stanwell | Steam Sub Critical | 9.068
Tarong | Steam Sub Critical | 9.2072
Tarong North | Steam Super Critical | 8.6538
Loy Yang A Power Station | Steam Sub Critical | 12.1622
Loy Yang B | Steam Sub Critical | 12.5436
Yallourn W | Steam Sub Critical | 13.8996
Tallawarra | CCGT | 6.9903
Condamine A | CCGT | 7.2874
Darling Downs | CCGT | 7.377
Swanbank E GT | CCGT | 7.438
Townsville Power Station | CCGT | 7.5949
Yarwun Cogen | CCGT | 10.3746
Osborne | CCGT | 8.1633
Pelican Point | CCGT | 7.3469
Tamar Valley Combined Cycle | CCGT | 7.2874
Colongra | OCGT | 11.1455
Smithfield Energy Facility3 | OCGT | 13.6882
Uranquinty | OCGT | 11.1455
Barcaldine Power Station | OCGT | 12.7208
Braemar | OCGT | 11.8812
Braemar 2 Power Station | OCGT | 11.8812
Mt Stuart | OCGT | 11.8812
Oakey Power Station | OCGT | 10.9422
Roma | OCGT | 11.8812
Port Lincoln GT | OCGT | 12.8114
Snuggery | OCGT | 13.4328
Dry Creek GT | OCGT | 13.6882
Hallett GT | OCGT | 14.876
Ladbroke Grove | OCGT | 11.8812
Mintaro GT | OCGT | 12.7208
Quarantine | OCGT | 10.7143
Bolivar Power Station1 | OCGT | 10.19
Bell Bay Three | OCGT | 12.0401
Tamar Valley Peaking | OCGT | 12.7208
Somerton | OCGT | 14.876
Bairnsdale | OCGT | 10.4956
Jeeralang A | OCGT | 15.2542
Jeeralang B | OCGT | 15.2542
Laverton North | OCGT | 11.5016
Mortlake | OCGT | 11.1455
Valley Power | OCGT | 14.876
Torrens Island B | Gas-powered steam turbine | 10.7143
Newport | Gas-powered steam turbine | 10.2857
Angaston | Reciprocating Engine | 12.775
Barker Inlet Power Station | Reciprocating Engine | 7.8947
Lonsdale | Reciprocating Engine | 7.8947
Port Stanvac 1 | Reciprocating Engine | 7.8947
Kurri Kurri OCGT2 | OCGT | 10.9312
Snapper Point Power Station1 | OCGT | 10.1902
Tallawarra B | OCGT | 10.9312
Kogan Gas | Hydrogen-based gas turbines | 12.72
SA Hydrogen Turbine | Hydrogen-based gas turbines | 12.72
Notes: Sourced from GHD 2018 AEMO Costs and Technical Parameter Review with the exception of 1. Bolivar Power Station and Snapper Point Power Station which are using the heat rate of new entrant OCGTs (small GT), 2. Kurri Kurri and Tallawara B which are using the heat rate of new entrant OCGTs (large GT) and 3. Smithfield Energy Facility which is using the heat rate of Dry Creek GT. 4. Values for Kogan Gas and Sa Hydrogen Turbine are sourced from Aurecon 2022 Costs and Technical Parameter Review.

## Auxiliary
Go to Assumptions Summary
Auxiliary load
Auxiliary load is also called "parasitic load" or "self load" and refers to energy generated by power stations for in-house use.
All units take the auxiliary rate of their respective fuel type.
Existing, committed, anticipated, and additional generators |  | New entrants
Fuel/Technology type | Auxiliary load (% of nameplate capacity) | Generator | Auxiliary load (% of nameplate capacity)
Black Coal QLD | 6.671 | OCGT (small GT) | 1.7
Black Coal NSW | 5.4639 | OCGT (large GT) | 1.1
Brown Coal VIC | 8.2146 | CCGT | 2.5
Hydro | 0.34269 | CCGT with CCS | 9.2
Gas-powered steam turbine | 5.0021 | Biomass | 7.3
CCGT | 1.7476 | Large scale Solar PV | 0.017458
OCGT | 0.6143 | Solar Thermal (15hrs storage) | 10
Liquid Fuel | 0.66986 | Battery storage (1hr storage) | 0
Solar | 0.017458 | Battery storage (2hrs storage) | 0
Wind | 0.069759 | Battery storage (4hrs storage) | 0
Hydrogen-based gas turbines | 1.5 | Battery Storage (8hrs storage) | 0
Battery Storage | 0 | Wind | 0.069759
Source: May 2023 Generation Information data collection, which contains the latest auxiliary load data as of publication. 1. Value for hydrogen-based gas turbines are sourced from Aurecon 2022 Costs and Technical Parameter Review. |  | Wind - offshore (fixed) | 0.069759
|  | Wind - offshore (floating) | 0.069759
|  | Pumped Hydro (8hrs storage) | 0.5
|  | Pumped Hydro (24hrs storage) | 0.5
|  | Pumped Hydro (48hrs storage) | 0.5
|  | BOTN - Cethana | 0.5
|  | Hydrogen reciprocating engines | 4
Notes:
1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
2. Pumped Hydro is sourced from information provided by Hydro Tasmania.
3. Battery auxiliary is included in the round-trip efficiency.
4. Wind and solar PV auxiliary rates using average rates for existing, committed and anticipated generation.

## Fixed OPEX
Go to Assumptions Summary
Fixed operating and maintenance cost (real 2023 dollars)
Costs that are incurred regardless of energy generated.
Existing, Committed, Anticipated, and Additional generators |  |  | New entrant technologies, after applying locational cost factors
Generator | Technology | Fixed OPEX ($/kW/year) | Generator | Fixed OPEX ($/kW sent out/year)
|  |  |  | NSW Low | NSW Medium | NSW High | QLD Low | QLD Medium | QLD High | SA Low | SA Medium | SA High | TAS Low | TAS Medium | TAS High | VIC Low | VIC Medium | VIC High
Bayswater | Steam Sub Critical | 64.5 | OCGT (small GT) | 13.4732 | 14.551 | 15.7636 | 13.4732 | 15.09 | 16.8415 | 13.4732 | 15.09 | 16.7067 | 13.4732 | 14.6858 | 15.7636 | 13.4732 | 13.8774 | 14.1468
Eraring | Steam Sub Critical | 64.5 | OCGT (large GT) | 10.9069 | 11.7794 | 12.761 | 10.9069 | 12.2157 | 13.6336 | 10.9069 | 12.2157 | 13.5245 | 10.9069 | 11.8885 | 12.761 | 10.9069 | 11.2341 | 11.4522
Liddell | Steam Sub Critical | 64.5 | CCGT | 11.6554 | 12.5878 | 13.6368 | 11.6554 | 13.054 | 14.5692 | 11.6554 | 13.054 | 14.4527 | 11.6554 | 12.7044 | 13.6368 | 11.6554 | 12.005 | 12.2381
Mt Piper | Steam Sub Critical | 64.5 | CCGT with CCS | 17.4831 | 18.8817 | 20.4552 | 17.4831 | 19.581 | 21.8538 | 17.4831 | 19.581 | 21.679 | 17.4831 | 19.0565 | 20.4552 | 17.4831 | 18.0075 | 18.3572
Vales Point B | Steam Sub Critical | 64.5 | Biomass | 161.4793 | 174.3976 | 188.9307 | 161.4793 | 180.8568 | 201.8491 | 161.4793 | 180.8568 | 200.2343 | 161.4793 | 176.0124 | 188.9307 | 161.4793 | 166.3236 | 169.5532
Callide B | Steam Sub Critical | 63.48 | Large scale Solar PV | 18.1781 | 19.6323 | 21.2684 | 18.1781 | 20.3595 | 22.7226 | 18.1781 | 20.3595 | 22.5408 | 18.1781 | 19.8141 | 21.2684 | 18.1781 | 18.7234 | 19.087
Callide C | Steam Super Critical | 63.48 | Solar Thermal (15hrs storage) | 141.1476 | 152.4394 | 165.1427 | 141.1476 | 158.0853 | 176.4345 | 141.1476 | 158.0853 | 175.023 | 141.1476 | 153.8509 | 165.1427 | 141.1476 | 145.382 | 148.205
Gladstone | Steam Sub Critical | 63.48 | Battery storage (1hr storage) | 7.592 | 8.1994 | 8.8827 | 7.592 | 8.5031 | 9.49 | 7.592 | 8.5031 | 9.4141 | 7.592 | 8.2753 | 8.8827 | 7.592 | 7.8198 | 7.9716
Kogan Creek | Steam Super Critical | 63.48 | Battery storage (2hrs storage) | 10.7999 | 11.6639 | 12.6359 | 10.7999 | 12.0959 | 13.4999 | 10.7999 | 12.0959 | 13.3919 | 10.7999 | 11.7719 | 12.6359 | 10.7999 | 11.1239 | 11.3399
Millmerran | Steam Super Critical | 63.48 | Battery storage (4hrs storage) | 17.3227 | 18.7085 | 20.2675 | 17.3227 | 19.4014 | 21.6533 | 17.3227 | 19.4014 | 21.4801 | 17.3227 | 18.8817 | 20.2675 | 17.3227 | 17.8423 | 18.1888
Stanwell | Steam Sub Critical | 63.48 | Battery Storage (8hrs storage) | 30.6889 | 33.144 | 35.906 | 30.6889 | 34.3716 | 38.3611 | 30.6889 | 34.3716 | 38.0542 | 30.6889 | 33.4509 | 35.906 | 30.6889 | 31.6096 | 32.2234
Tarong | Steam Sub Critical | 63.48 | Wind | 26.7325 | 28.8711 | 31.277 | 26.7325 | 29.9404 | 33.4156 | 26.7325 | 29.9404 | 33.1483 | 26.7325 | 29.1384 | 31.277 | 26.7325 | 27.5345 | 28.0691
Tarong North | Steam Super Critical | 63.48 | Wind - offshore (fixed) | 169.7311 | 183.3095 | 198.5853 | 169.7311 | 190.0988 | 212.1638 | 169.7311 | 190.0988 | 210.4665 | 169.7311 | 185.0069 | 198.5853 | 169.7311 | 174.823 | 178.2176
Loy Yang A Power Station | Steam Sub Critical | 163.64 | Wind - offshore (floating) | 625.6348 | 675.6856 | 731.9927 | 625.6348 | 700.7109 | 782.0435 | 625.6348 | 700.7109 | 775.7871 | 625.6348 | 681.9419 | 731.9927 | 625.6348 | 644.4038 | 656.9165
Loy Yang B | Steam Sub Critical | 163.64 | Pumped Hydro (8hrs storage) | 19.0925 | 20.6199 | 22.3382 | 19.0925 | 21.3836 | 23.8656 | 19.0925 | 21.3836 | 23.6747 | 19.0925 | 20.8108 | 22.3382 | 19.0925 | 19.6653 | 20.0471
Yallourn W | Steam Sub Critical | 163.64 | Pumped Hydro (24hrs storage) | 19.0925 | 20.6199 | 22.3382 | 19.0925 | 21.3836 | 23.8656 | 19.0925 | 21.3836 | 23.6747 | 19.0925 | 20.8108 | 22.3382 | 19.0925 | 19.6653 | 20.0471
Tallawarra | CCGT | 12.53 | Pumped Hydro (48hrs storage) | 19.0925 | 20.6199 | 22.3382 | 19.0925 | 21.3836 | 23.8656 | 19.0925 | 21.3836 | 23.6747 | 19.0925 | 20.8108 | 22.3382 | 19.0925 | 19.6653 | 20.0471
Condamine A | CCGT | 12.53 | BOTN - Cethana | [10 empty] | 20.8108
Darling Downs | CCGT | 12.53 | Hydrogen reciprocating engines | 35.2869 | 38.1099 | 41.2857 | 35.2869 | 39.5213 | 44.1086 | 35.2869 | 39.5213 | 43.7558 | 35.2869 | 38.4627 | 41.2857 | 35.2869 | 36.3455 | 37.0512
Swanbank E GT | CCGT | 12.53 | Notes:
Townsville Power Station | CCGT | 12.53 | 1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
Yarwun Cogen | CCGT | 12.53 | 2. Locational cost factors applied for the O&M Costs component of new entrants.
Osborne | CCGT | 12.53 | 3. Wind, Large-Scale Solar PV and Solar Thermal Variable O&M costs are assumed to be included in the Fixed O&M costs as per Aurecon's report.
Pelican Point | CCGT | 12.53 | 4. The cost of extended warranties are included in the Fixed O&M costs for Battery storage to cover a 20-year battery life.
Tamar Valley Combined Cycle | CCGT | 125.93 | 5. Pumped Hydro Fixed O&M costs are sourced from Entura 2018 Pumped Hydro Cost Modelling.
Colongra | OCGT | 18.08
Smithfield Energy Facility | OCGT | 18.08
Uranquinty | OCGT | 18.08
Barcaldine Power Station | OCGT | 18.08
Braemar | OCGT | 18.08
Braemar 2 Power Station | OCGT | 18.08
Mt Stuart | OCGT | 18.08
Oakey Power Station | OCGT | 18.08
Roma | OCGT | 18.08
Dry Creek GT | OCGT | 18.08
Hallett GT | OCGT | 18.08
Ladbroke Grove | OCGT | 18.08
Mintaro GT | OCGT | 18.08
Port Lincoln GT | OCGT | 18.08
Quarantine | OCGT | 18.08
Snapper Point Power Station | OCGT | 13.47
Snuggery | OCGT | 18.08
Bell Bay Three | OCGT | 18.08
Tamar Valley Peaking | OCGT | 18.08
Bairnsdale | OCGT | 18.08
Jeeralang A | OCGT | 18.08
Jeeralang B | OCGT | 18.08
Laverton North | OCGT | 18.08
Mortlake | OCGT | 18.08
Somerton | OCGT | 18.08
Valley Power | OCGT | 18.08
Newport | Gas-powered steam turbine | 56.24
Torrens Island B | Gas-powered steam turbine | 56.24
Angaston | Reciprocating Engine | 18.04
Barker Inlet Power Station | Reciprocating Engine | 18.04
Lonsdale | Reciprocating Engine | 18.04
Port Stanvac 1 | Reciprocating Engine | 18.04
Kurri Kurri OCGT | OCGT | 10.91
Tallawarra B | OCGT | 10.91
Bolivar Power Station | OCGT | 13.47
Kogan Gas | Hydrogen-based gas turbines | 69.5045
SA Hydrogen Turbine | Hydrogen-based gas turbines | 69.5045
All Battery storage (1hr storage) | Battery storage (1hr storage) | 7.59
All Battery storage (2hrs storage) | Battery storage (2hrs storage) | 10.8
All Battery storage (4hrs storage) | Battery storage (4hrs storage) | 17.32
All Battery storage (8hrs storage) | Battery storage (8hrs storage) | 30.6889
All Hydro | Hydro | 69.51
All Pumped Hydro | Pumped Hydro | 19.0925
All Large scale solar PV | Large scale Solar PV | 18.18
All Wind | Wind | 26.73
Notes:
1. Sourced from GHD with the following exceptions: (1) OCGTs, which are from ACIL Allen 2014 Fuel and Technical costs review based on consultation feedback from participants, (2) Brown coal, NSW black coal and Tamar Valley Combined Cycle plant, which are based on feedback from participants
2. New entrant data (Low) is used for existing, committed and anticipated Wind, Solar, Battery storage and Pumped hydro. Existing battery storages are mapped to the closest MW/MWh configuration
3. Bolivar Power Station and Snapper Point Power Station use the Fixed OPEX of new entrant OCGTs (small GT) in the SA Low cost zone.
4. Kurri Kurri and Tallawara B use the Fixed OPEX of new entrant OCGTs (large GT) in the NSW Low cost zone.
5. FOM for battery storage technologies are based sourced from Aurecon 2022 Costs and Technical Parameter Review.
6. Values for hydrogen-based gas turbines are sourced from Aurecon 2022 Costs and Technical Parameter Review.

## Variable OPEX
Go to Assumptions Summary
Variable operating and maintenance cost (real 2023 dollars)
Costs that can be expressed in terms of energy generated, not including fuel costs.
Existing, Committed, Anticipated, and Additional generators |  |  | New entrant technologies, after applying locational cost factors
Generator | Technology | Variable OPEX ($/MWh sent out)1 | Generator | Variable OPEX ($/MWh sent out)
|  |  |  | NSW Low | NSW Medium | NSW High | QLD Low | QLD Medium | QLD High | SA Low | SA Medium | SA High | TAS Low | TAS Medium | TAS High | VIC Low | VIC Medium | VIC High
Bayswater | Steam Sub Critical | 5.1012 | OCGT (small GT) | 12.8316 | 13.8581 | 15.013 | 12.8316 | 14.3714 | 16.0395 | 12.8316 | 14.3714 | 15.9112 | 12.8316 | 13.9864 | 15.013 | 12.8316 | 13.2165 | 13.4732
Eraring | Steam Sub Critical | 5.1012 | OCGT (large GT) | 7.8059 | 8.4304 | 9.1329 | 7.8059 | 8.7426 | 9.7574 | 7.8059 | 8.7426 | 9.6793 | 7.8059 | 8.5084 | 9.1329 | 7.8059 | 8.0401 | 8.1962
Liddell | Steam Sub Critical | 5.1012 | CCGT | 3.9564 | 4.2729 | 4.629 | 3.9564 | 4.4312 | 4.9455 | 3.9564 | 4.4312 | 4.9059 | 3.9564 | 4.3125 | 4.629 | 3.9564 | 4.0751 | 4.1542
Mt Piper | Steam Sub Critical | 5.1012 | CCGT with CCS | 7.699 | 8.3149 | 9.0078 | 7.699 | 8.6228 | 9.6237 | 7.699 | 8.6228 | 9.5467 | 7.699 | 8.3919 | 9.0078 | 7.699 | 7.9299 | 8.0839
Vales Point B | Steam Sub Critical | 5.1012 | Biomass | 10.3294 | 11.1558 | 12.0854 | 10.3294 | 11.569 | 12.9118 | 10.3294 | 11.569 | 12.8085 | 10.3294 | 11.2591 | 12.0854 | 10.3294 | 10.6393 | 10.8459
Callide B | Steam Sub Critical | 5.0237 | Large scale Solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Callide C | Steam Super Critical | 5.0237 | Solar Thermal (15hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gladstone | Steam Sub Critical | 5.0237 | Battery storage (1hr storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kogan Creek | Steam Super Critical | 5.0237 | Battery storage (2hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Millmerran | Steam Super Critical | 5.0237 | Battery storage (4hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Stanwell | Steam Sub Critical | 5.0237 | Battery Storage (8hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tarong | Steam Sub Critical | 5.0237 | Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tarong North | Steam Super Critical | 5.0237 | Wind - offshore (fixed) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Loy Yang A Power Station | Steam Sub Critical | 4.7846 | Wind - offshore (floating) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Loy Yang B | Steam Sub Critical | 4.7846 | Pumped Hydro (8hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yallourn W | Steam Sub Critical | 4.7846 | Pumped Hydro (24hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tallawarra | CCGT | 8.7945 | Pumped Hydro (48hrs storage) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Condamine A | CCGT | 8.7945 | BOTN - Cethana | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Darling Downs | CCGT | 8.7945 | Hydrogen reciprocating engines | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Swanbank E GT | CCGT | 8.7945 | Notes:
Townsville Power Station | CCGT | 8.7945 | 1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
Yarwun Cogen | CCGT | 8.7945 | 2. Locational cost factors applied for the O&M Costs component of new entrants.
Osborne | CCGT | 8.7945 | 3. Wind, Large-scale Solar PV and Solar Thermal Variable O&M costs are assumed to be included in the Fixed O&M costs as per Aurecon's report.
Pelican Point | CCGT | 8.7945 | 4. Pumped Hydro is sourced from GHD 2018 AEMO Costs and Technical Parameter Review.
Tamar Valley Combined Cycle | CCGT | 8.7945
Colongra | OCGT | 12.5652
Smithfield Energy Facility | OCGT | 12.5652
Uranquinty | OCGT | 12.5652
Barcaldine Power Station | OCGT | 12.5652
Braemar | OCGT | 12.5652
Braemar 2 Power Station | OCGT | 12.5652
Mt Stuart | OCGT | 12.5652
Oakey Power Station | OCGT | 12.5652
Roma | OCGT | 12.5652
Dry Creek GT | OCGT | 12.5652
Hallett GT | OCGT | 12.5652
Ladbroke Grove | OCGT | 12.5652
Mintaro GT | OCGT | 12.5652
Port Lincoln GT | OCGT | 12.5652
Quarantine | OCGT | 12.5652
Snapper Point Power Station | OCGT | 12.8318
Snuggery | OCGT | 12.5652
Bell Bay Three | OCGT | 12.5652
Tamar Valley Peaking | OCGT | 12.5652
Bairnsdale | OCGT | 12.5652
Jeeralang A | OCGT | 12.5652
Jeeralang B | OCGT | 12.5652
Laverton North | OCGT | 12.5652
Mortlake | OCGT | 12.5652
Somerton | OCGT | 12.5652
Valley Power | OCGT | 12.5652
Newport | Gas-powered steam turbine | 2.7787
Torrens Island B | Gas-powered steam turbine | 2.7787
Angaston | Reciprocating Engine | 13.3409
Barker Inlet Power Station | Reciprocating Engine | 13.3409
Lonsdale | Reciprocating Engine | 13.3409
Port Stanvac 1 | Reciprocating Engine | 13.3409
Kurri Kurri OCGT | OCGT | 7.806
Tallawarra B | OCGT | 7.806
Bolivar Power Station | OCGT | 12.8318
Kogan Gas | Hydrogen-based gas turbines | 40.6334
SA Hydrogen Turbine | Hydrogen-based gas turbines | 40.6334
All Battery storage (1hr storage) | Battery storage (1hr storage) | 0
All Battery storage (2hrs storage) | Battery storage (2hrs storage) | 0
All Battery storage (4hrs storage) | Battery storage (4hrs storage) | 0
All Battery storage (8hrs storage) | Battery storage (8hrs storage) | 0
All Hydro | Hydro | 8.5797
All Pumped Hydro | Pumped Hydro | 0
All Large scale solar PV | Large scale Solar PV | 0
All Wind | Wind | 0
Note:
1. Sourced from GHD 2018 AEMO costs and technical parameter review, with the exception of (a) Smithfield Energy Facility plant which is now operated as an OCGT unit and (b) brown coal and NSW black coal for which GHD assumptions were adjusted based on feedback from participants
2. New entrant data is used for existing, committed and anticipated Wind, Solar, Battery storage and Pumped hydro.
3. Bolivar Power Station and Snapper Point South Station use the Variable OPEX of new entrant OCGTs (small GT) in SA low cost region.
4. Kurri Kurri and Tallawara B use the Variable OPEX of new entrant OCGTs (large GT) in the NSW low cost region.
5. Values for hydrogen-based gas turbines are sourced from Aurecon 2022 Costs and Technical Parameter Review.

## Emissions intensity
Go to Assumptions Summary
Emissions intensity
Existing, Committed, Anticipated, Additional generators |  |  | New entrant technologies
The scope 1 emissions intensity for existing facilities is provided by the Clean Energy Regulator - Greenhouse and energy information by designated generation facility 2021-22. |  |  | The scope 1 emissions intensity for committed and new entrant generators is calculated by AEMO as the product of the technology heat rate from Aurecon 2022 and emission factors from GHD 2018.
Generator | Technology | Scope 1 emissions intensity (kg/MWh as-gen) | Generator | Scope 1 emissions intensity (kg/MWh as-gen)
Bayswater | Steam Sub Critical | 889.202 | OCGT (small GT) | 541.6007
Eraring | Steam Sub Critical | 878.938 | OCGT (large GT) | 580.9847
Mt Piper | Steam Sub Critical | 801.1644 | CCGT | 377.6704
Vales Point B | Steam Sub Critical | 944.7033 | CCGT with CCS | 57.447
Callide B | Steam Sub Critical | 942.8409 | Biomass | 20.844
Callide C | Steam Super Critical | 873.9527 | Large scale Solar PV | 0
Gladstone | Steam Sub Critical | 985.8045 | Solar Thermal (15hrs storage) | 0
Kogan Creek | Steam Super Critical | 861.9335 | Battery Storage (1hr storage) | 0
Millmerran | Steam Super Critical | 825.2499 | Battery storage (2hrs storage) | 0
Stanwell | Steam Sub Critical | 863.4613 | Battery storage (4hrs storage) | 0
Tarong | Steam Sub Critical | 886.5998 | Battery storage (8hrs storage) | 0
Tarong North | Steam Super Critical | 886.5998 | Wind | 0
Loy Yang A Power Station | Steam Sub Critical | 1168.8606 | Wind - offshore (fixed) | 0
Loy Yang B | Steam Sub Critical | 1111.1528 | Wind - offshore (floating) | 0
Yallourn W | Steam Sub Critical | 1286.6019 | Pumped Hydro (8hrs storage) | 0
Tallawarra | CCGT | 370.9712 | Pumped Hydro (24hrs storage) | 0
Condamine A | CCGT | 448.78 | Pumped Hydro (48hrs storage) | 0
Darling Downs | CCGT | 420.6678 | BOTN - Cethana | 0
Swanbank E GT | CCGT | 393.9767 | Hydrogen reciprocating engines | 0
Townsville Power Station | CCGT | 571.8092 | 1. The biomass combustion emission is based on the dry wood solid fuel category in the 2022 Australian National Greenhouse Accounts Factors of the Department of Climate Change, Energy, the Environment and Water (DCCEEW).
Yarwun Cogen | CCGT | 458.8084
Osborne | CCGT | 414.6692
Pelican Point | CCGT | 400.2491
Tamar Valley Combined Cycle | CCGT | 618.7694
Colongra | OCGT | 625.4489
Smithfield Energy Facility | OCGT | 704.9693
Uranquinty | OCGT | 564.2196
Barcaldine Power Station | OCGT | 793.2629
Braemar | OCGT | 616.5276
Braemar 2 Power Station | OCGT | 616.5276
Mt Stuart | OCGT | 1001.6306
Oakey Power Station | OCGT | 663.6832
Roma | OCGT | 649.8984
Dry Creek GT | OCGT | 892.1893
Hallett GT | OCGT | 642.6559
Ladbroke Grove | OCGT | 516.2364
Mintaro GT | OCGT | 693.5416
Port Lincoln GT | OCGT | 1334.5888
Quarantine | OCGT | 603.9767
Snapper Point Power Station | OCGT | 541.6007
Snuggery | OCGT | 1106.8763
Bell Bay Three | OCGT | 618.7694
Tamar Valley Peaking | OCGT | 618.7694
Bairnsdale | OCGT | 537.0489
Jeeralang A | OCGT | 757.9581
Jeeralang B | OCGT | 757.9581
Laverton North | OCGT | 638.1801
Mortlake | OCGT | 467.1118
Somerton | OCGT | 732.5947
Valley Power | OCGT | 805.7837
Torrens Island B | Gas-powered steam turbine | 593.0411
Newport | Gas-powered steam turbine | 532.5429
Angaston | Reciprocating Engine | 685.758
Barker Inlet Power Station | Reciprocating Engine | 567.5073
Lonsdale | Reciprocating Engine | 657.9846
Port Stanvac 1 | Reciprocating Engine | 657.9846
Kurri Kurri OCGT | OCGT | 580.9847
Tallawarra B | OCGT | 580.9847
Bolivar Power Station | OCGT | 541.6007
Kogan Gas | Hydrogen-based gas turbines | 580.9847
SA Hydrogen Turbine | Hydrogen-based gas turbines | 580.9847
All Pumped Hydro | Pumped Hydro | 0
All Large scale solar PV | Large scale solar PV | 0
All Wind | Wind | 0
All Hydro | Hydro | 0
All Battery Storage | Battery Storage | 0
Notes:
1. Yarwun Cogen emission is an average of CCGT values in QLD
2. Bolivar Power Station and Snapper Point South Station use the emission intensity of new entrant OCGTs (small GT).
3. Kurri Kurri and Tallawara B use the emission intensity of new entrant OCGTs (large GT).
4. Emissions for all gas based generators are dependent on the blending biomethane into the gas network , the values presented here are for a 100% gas operation.
5. Emissions for Kogan Gas and SA Hydrogen Turbine are dependent on the H2 blending which can be found on the sheet "H2 GPG_emissions reduction", the values presented here are for a 100% gas operation and use the emission intensity of new entrant OCGTs (large GT).
1

## H2 GPG_emissions reduction
Go to Assumptions Summary
Gas fired generation emissions reduction factor from hydrogen for Kogan Gas and SA Hydrogen Turbine
The tables below represent the estimated emissions intensity reduction factors achieved by partial hydrogen firing of gas turbines, for usage in AEMO's forecasting models, to be applied to individual gas fired generators.
In the ISP model, these factors are multiplied by the figures stated in the 'Emissions intensity' tab to produce the assumed emissions for the above mentioned GT's only in Queensland and South Australia
The factors are calculated by AEMO from the results of the 2022 multi-sector modelling, and AEMO assumptions using the forecast ratio of natural gas/hydrogen for the two individual projects
The assumed emissions factor for combustion of Hydrogen is 0.00 kgCO2e/GJ, consistent with the CSIRO multi-sector modelling.
In this workbook, Kogan Gas pertains to Brigalow/Kogan Creek in Queensland and SA Hydrogen Turbine pertains to Whyalla Hydrogen plant in South Australia.
| Kogan Gas | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Kogan Gas | Progressive Change | N/A | N/A | N/A | N/A | 100% | 100% | 95% | 90% | 85% | 65% | 50% | 30% | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Kogan Gas | Step Change | N/A | N/A | N/A | N/A | 100% | 100% | 95% | 85% | 75% | 50% | 30% | 15% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Kogan Gas | Green Energy Exports | N/A | N/A | N/A | N/A | 100% | 100% | 90% | 70% | 50% | 30% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| SA Hydrogen Turbine | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
SA Hydrogen Turbine | Progressive Change | N/A | N/A | N/A | 90% | 75% | 50% | 30% | 15% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
SA Hydrogen Turbine | Step Change | N/A | N/A | N/A | 90% | 75% | 50% | 30% | 15% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
SA Hydrogen Turbine | Green Energy Exports | N/A | N/A | N/A | 90% | 75% | 50% | 30% | 15% | 10% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%

## GPG emissions reduction - BioM
Go to Assumptions Summary
Gas fired generation emissions reduction factor from biomethane
The table below represents the estimated emissions intensity reduction factors achieved by blending biomethane into the gas network for usage in AEMO's forecasting models, to be applied to individual gas fired generators.
In the ISP model, these factors are multiplied by the figures stated in the 'Emissions intensity' tab to produce the assumed emissions from each gas generator in each year.
The factors are calculated by AEMO from the results of the 2022 multi-sector modelling, using the forecast ratio of natural gas/biomethane across the NEM.
The assumed emissions factor for combustion of biomethane is 0.13 kgCO2e/GJ, consistent with the CSIRO multi-sector modelling.
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Progressive Change | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.66% | 85.11% | 71.5% | 58.36% | 55.5% | 50.83% | 47.56% | 47.49%
Step Change | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.58% | 99.58% | 99.58%
Green Energy Exports | 100% | 100% | 100% | 100% | 92.69% | 85.22% | 82.59% | 81.26% | 79.06% | 75.55% | 72.13% | 70.16% | 68.98% | 67.66% | 65.62% | 62.91% | 61.66% | 61.02% | 60.1% | 58.98% | 58.26% | 57.46% | 56.94% | 56.76% | 55.97% | 54.94% | 50.99% | 47.99% | 48.07% | 45.94% | 41.46% | 41.31%

## Marginal Loss Factors
Go to Assumptions Summary
Marginal Loss Factors (MLFs)
Marginal loss factors represent the impact of network losses on spot prices. No impacts on long term generation expansion, however, marginal loss factors do impact the short term dispatch modelling.
See https://aemo.com.au/en/energy-systems/electricity/national-electricity-market-nem/market-operations/loss-factors-and-regional-boundaries The existing generators marginal loss factors have been updated based on March 2023 update for financial year 2023-24: See https://aemo.com.au/-/media/files/electricity/nem/security_and_reliability/loss_factors_and_regional_boundaries/2023-24/marginal-loss-factors-for-the-2023-24-financia-year-pdf.pdf?la=en
Existing generators |  | Committed Projects 1 |  |  | Generic new entrant units |  |  | Anticipated projects |  |  | Existing, Committed and Anticipated Batteries |  |  | Additional projects*
Generator | MLF | Generator | MLF | Shadow connection point | Generator | MLF | Shadow connection point | Generator | MLF | Shadow connection point | Battery | MLF - Generation | Shadow connection point | Policy | Project | MLF - Generation | Shadow connection point
Adelaide Desalination Plant Solar Farm | 1.0039 | Kurri Kurri OCGT | 0.9831 | Colongra PS Unit 1 | NE_CAN | 0.8383 | Uranquinty PS Unit 11 | SA Hydrogen Turbine | 0.9601 | Lincoln Gap Wind Farm | Adelaide Desalination Plant BESS | 1.0036 | Adelaide Desalination Plant Battery (Generation) | VRET2 | Derby Solar Project BESS | 0.9756 | Ballarat BESS (Generation)
Angaston | 1.0048 | Tallawarra B* | 0.9856 | Tallawarra PS | NE_SNW | 0.9831 | Colongra PS Unit 1 | Borumba | 0.9736 | Woolooga Solar Farm | Ballarat Energy Storage System | 0.9756 | Ballarat BESS (Generation) | VRET2 | Fulham Solar Farm BESS | 0.9804 | Bairnsdale
Ararat Wind Farm | 0.8899 | Snowy 2.0 | 0.9092 | Lower Tumut Generation – dual MLF | NE_NNSW | 0.9646 | Bayswater PS Unit 1 | Aramara Solar Farm | 0.9704 | Childers Solar Farm | Blyth BESS | 0.8968 | Snowtown Wind Farm | VRET2 | Fulham Solar Farm | 0.9804 | Bairnsdale
Avonlie Solar Farm | 1 | Kidston | 0.9222 | Hughenden Solar Farm | NE_CNSW | 0.9646 | Bayswater PS Unit 1 | Banksia Solar Farm | 0.9704 | Childers Solar Farm | Bolivar Waste Water Treatment BESS | 1.0002 | Bolivar Waste Water Treatment Plant Reserve BESS (Generation) | VRET2 | Kiamal Solar Farm – Stage 2 | 0.8775 | Kiamal Solar Farm stage 1
Bairnsdale | 0.9804 | Girgarre Solar Farm | 0.9738 | Numurkah Solar Farm | NE_SNSW | 0.8383 | Uranquinty PS Unit 11 | Culcairn Solar Farm | 0.907 | Wagga North Solar Farm | Bouldercombe Battery project | 0.9181 | Stanwell PS | VRET2 | Kiamal Solar Farm – Stage 2 BESS | 0.8775 | Kiamal Solar Farm stage 1
Bald Hills Wind Farm | 0.9825 | Glenrowan Solar Farm | 0.9671 | Winton SF | NE_NQ | 0.9164 | Mt Stuart PS Unit 1 | Cultana Solar Farm | 0.9601 | Bungala One Solar Farm | Broken Hill BESS | 0.8324 | Broken Hill Solar Farm | VRET2 | Horsham Solar Farm BESS | 0.8821 | Bulgana BESS (Generation)
Bango 973 Wind Farm | 0.9159 | Mannum Solar Farm 2* | 0.9943 | Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | NE_CQ | 0.9096 | Callide C PS Unit 3 | Derby Solar Farm | 0.9413 | Cohuna Solar Farm | Bulgana Green Power Hub BESS | 0.8821 | Bulgana BESS (Generation) | LTESA Round 1 | Coppabella Wind Farm | 0.9437 | Cullerin Range Wind Farm
Bango 999 Wind Farm | 0.9288 | Metz Solar Farm | 0.8831 | Metz Solar Farm | NE_GG | 0.9329 | Gladstone PS (275 kV) Unit 1 | Frasers Solar Farm | 0.9764 | Jeeralang A | Capital Battery | 0.9575 | Capital Wind Farm | LTESA Round 1 | New England Solar Farm - stage 2 | 0.8718 | New England Solar Farm
Bannerton Solar Park | 0.8947 | Riverina Solar Farm | 0.8894 | Coleambally Solar Farm | NE_SQ | 0.9987 | Swanbank E GT | Horsham Solar Farm | 0.8775 | Kiamal Solar Farm stage 1 | Chinchilla BESS | 0.9712 | Western Downs Green Power Hub | LTESA Round 1 | Limondale BESS | 0.8255 | Limondale Solar Farm 1
Barcaldine Power Station | 0.938 | Sebastopol Solar Farm | 0.9108 | Junee Solar Farm | NE_CSA | 0.9997 | Torrens Island B | Lockhart Hybrid Facility - Solar | 0.907 | Wagga North Solar Farm | Christies Beach Wastewater Treatment Plant BESS | 1.0036 | Christies Beach BESS Gen | LTESA Round 1 | Goulburn River BESS | 0.9831 | Colongra PS Unit 1
Barker Inlet Power Station | 1 | Stubbo Solar Farm | 0.9339 | Beryl Solar Farm | NE_SESA | 0.9553 | Ladbroke Grove | Quorn Park Solar Farm | 0.9 | Parkes Solar Farm | Dalrymple BESS | 0.8954 | Dalrymple North BESS (Generation) | LTESA Round 1 | Silver City Energy Storage | 0.8324 | Broken Hill Solar Farm
Barron Gorge | 0.959 | Walla Walla Solar Farm | 1 | Default | NE_VIC1 | 0.9937 | Newport PS | Tamworth Solar Farm | 0.8289 | White Rock Solar Farm | Darlington Point Energy Storage System | 0.8958 | Darlington Point Solar Farm | CIS | Smithfield BESS | 1.001 | Wallgrove BESS (Generation)
Bastyan | 0.9202 | Wandoan South Solar Farm - stage 1 | 0.9832 | Wandoan South Solar Farm - stage 1 | NE_TAS1 | 1 | Tamar Valley CCGT | Tilbuster Solar Farm | 0.8718 | New England Solar Farm 1 | Eraring Big Battery | 0.9848 | Eraring | QEJP | Kogan Gas | 0.9673 | Kogan Creek
Bayswater | 0.9651 | Wellington North Solar Farm (Lightsource) | 0.9439 | Wellington Solar Farm | REZ_Q1_Solar | 0.9222 | Hughenden Solar Farm | Woolsthorpe Wind Farm | 0.9933 | Terang | Gannawarra Energy Storage System | 1.029 | Gannawarra BESS (Generation) | *These projects are not included in the July 2023 Generation Information as an Existing, Committed, or Anticipated project. However they are included in AEMO's modelling under the following policy frameworks: 1) 2020 amendment to the National Electricity (Victoria) Act 2005 (NEVA). 2) Victorian Renewable Energy Target auction (VRET2) 3) New South Wales Long-Term Energy Service Agreements (LTESAs) 4) Queensland Energy and Jobs Plan 5) South Australia – Hydrogen Jobs Plan
Bell Bay Three | 0.9968 | Wollar Solar Farm | 0.9339 | Beryl Solar Farm | REZ_Q2_Solar | 0.9222 | Hughenden Solar Farm | Uungula Wind Farm | 0.9622 | Bodangora Wind Farm | Gnarwarre BESS | 0.9848 | Victorian Big Battery
Berrybank Wind Farm | 0.9397 | Woolooga Solar Farm | 0.9832 | Woolooga Solar Farm | REZ_Q3_Solar | 0.9222 | Hughenden Solar Farm | MacIntyre Wind Farm | 1 | Default | Happy Valley Reservoir BESS | 1.0041 | Happy Valley BESS (Generation)
Beryl Solar Farm | 0.9339 | Wunghnu Solar Farm | 1 | Default | REZ_Q4_Solar | 0.8981 | Clare Solar Farm |  |  |  | Hazelwood BESS | 0.9764 | Jeeralang A PS Unit 1
Blowering | 0.9241 | Clarke Creek Wind Farm | 1 | Default | REZ_Q5_Solar | 0.915 | Barcaldine Solar at Lilyvale (132) |  |  |  | Hornsdale Power Reserve Unit 1 | 0.9653 | Hornsdale Battery (Generation)
Bluegrass Solar Farm | 0.9546 | Crookwell 3 Wind Farm | 0.9611 | Crookwell 2 | REZ_Q6_Solar | 0.9329 | Gladstone PS (275 kV) Unit 1 |  |  |  | Koorangie Energy Storage System | 1.029 | Gannawarra BESS (Generation)
Boco Rock Wind Farm | 0.9444 | Flyers Creek Wind Farm | 0.926 | Crudine Ridge Wind Farm | REZ_Q7_Solar | 0.9601 | Bungala One Solar Farm |  |  |  | Lake Bonney BESS | 0.979 | Lake Bonney BESS (Generation)
Bodangora Wind Farm | 0.9622 | Golden Plains Wind Farm East | 0.9576 | Mt Mercer Wind Farm | REZ_Q8_Solar | 0.9762 | Darling Downs Solar Farm |  |  |  | Lincoln Gap Wind Farm BESS | 0.9601 | Lincoln Gap Wind Farm
Bogong / Mackay | 0.9715 | Goyder South Wind Farm 1A | 0.957 | Hallett Stage 2 Hallett Hill Wind Farm | REZ_Q9_Solar | 0.9222 | Hughenden Solar Farm |  |  |  | New England Solar Farm BESS | 0.8718 | New England Solar Farm
Bolivar Power Station | 0.9949 | Goyder South Wind Farm 1B | 0.957 | Hallett Stage 2 Hallett Hill Wind Farm | REZ_N1_Solar | 0.7977 | Moree Solar Farm |  |  |  | Orana BESS | 0.9439 | Narromine Solar Farm
Bolivar Waste Water Treatment Solar Farm | 0.9949 | Hawkesdale Wind Farm | 0.9849 | Macarthur Wind Farm | REZ_N2_Solar | 0.8697 | White Rock Solar Farm |  |  |  | Philip Island BESS | 0.9825 | Bald Hills Wind Farm
Bomen Solar Farm | 0.911 | Ryan Corner Wind Farm | 0.9849 | Macarthur Wind Farm | REZ_N3_Solar | 0.9897 | Burrendong Hydro PS |  |  |  | Queanbeyan BESS | 0.9575 | Capital Wind Farm
Braemar | 0.9617 | Rye Park Wind Farm | 1 | Default | REZ_N4_Solar | 0.8324 | Broken Hill Solar Farm |  |  |  | Quorn Park BESS | 0.9865 | Parkes 132kV load
Braemar 2 Power Station | 0.9617 | Wambo Wind Farm | 0.9658 | Coopers Gap Wind Farm | REZ_N5_Solar | 0.8894 | Coleambally Solar Farm |  |  |  | Rangebank BESS | 0.9764 | Jeeralang A PS Unit 1
Broken Hill Solar Farm | 0.8324 | Note: where a appropriate shadow gen cannot be identified 'default' is used, which is 1 |  |  | REZ_N6_Solar | 0.911 | Bomen Solar Farm |  |  |  | Riverina Energy Storage System 1 | 0.8958 | Darlington Point Solar Farm
Bulgana Green Power Hub - Wind Farm | 0.8821 | 1. Committed * projects are marked with an "*" and are assumed to commence beyond the T-1 year (at the earliest) according to the ESOO and Reliability Forecasting Methodology. |  |  | REZ_N7_Solar | 1 | Default |  |  |  | Riverina Energy Storage System 2 | 0.8958 | Darlington Point Solar Farm
Bungala One Solar Farm | 0.9601 |  |  |  | REZ_N8_Solar | 0.9668 | Royalla Solar Farm |  |  |  | Sapphire Wind Farm BESS | 0.9086 | Sapphire Wind Farm
Bungala Two Solar Farm | 0.9601 |  |  |  | REZ_N9_Solar | 0.9439 | Wellington Solar Farm |  |  |  | Swanbank BESS | 0.9987 | Swanbank E GT
Callide B | 0.9138 |  |  |  | REZ_V1_Solar | 1 | Default |  |  |  | Tailem Bend Battery Project | 1.003 | Tailem Bend Solar Farm
Callide C | 0.9138 |  |  |  | REZ_V2_Solar | 0.8947 | Bannerton Solar Farm |  |  |  | Templers BESS | 1.0048 | Angaston
Canunda Wind Farm | 0.9671 |  |  |  | REZ_V3_Solar | 0.8894 | Coleambally Solar Farm |  |  |  | Torrens Island BESS | 1 | Torrens Island PS Load
Capital Wind Farm | 0.9575 |  |  |  | REZ_V4_Solar | 1 | Default |  |  |  | Ulinda Park BESS | 0.9712 | Western Downs Green Power Hub
Catagunya / Liapootah / Wayatinah | 0.9809 |  |  |  | REZ_V5_Solar | 0.9825 | Bald Hills Wind Farm |  |  |  | Victorian Big Battery | 0.9885 | Victorian Big Battery (Generation)
Cathedral Rocks Wind Farm | 0.9319 |  |  |  | REZ_V6_Solar | 0.9413 | Cohuna Solar Farm |  |  |  | Wallgrove Grid Battery project | 1.001 | Wallgrove BESS (Generation)
Cattle Hill Wind Farm | 0.8888 |  |  |  | REZ_S1_Solar | 1.003 | Tailem Bend Solar Farm |  |  |  | Wandoan South BESS | 0.9751 | Wandoan BESS (Generation)
Cethana | 0.9504 |  |  |  | REZ_S2_Solar | 0.9601 | Bungala One Solar Farm |  |  |  | Waratah Super Battery | 0.9831 | Colongra PS Unit 1
Challicum Hills Wind Farm | 0.9759 |  |  |  | REZ_S3_Solar | 0.9601 | Bungala One Solar Farm |  |  |  | Western Downs Battery | 0.9673 | Kogan Creek
Cherry Tree Wind Farm | 0.9974 |  |  |  | REZ_S4_Solar | 0.8073 | Wattle Point Wind Farm |  |  |  | Wooreen Energy Storage System | 0.9764 | Jeeralang A PS Unit 1
Childers Solar Farm | 0.9704 |  |  |  | REZ_S5_Solar | 0.9601 | Bungala One Solar Farm |  |  |  | Aldoga BESS Stage 1 | 0.9329 | Gladstone PS (275 kV) Unit 1
Clare Solar Farm | 0.8981 |  |  |  | REZ_S6_Solar | 0.9601 | Bungala One Solar Farm |  |  |  | Bungama Solar BESS | 0.8968 | Snowtown Wind Farm
Clements Gap Wind Farm | 0.9522 |  |  |  | REZ_S7_Solar | 0.9601 | Bungala One Solar Farm |  |  |  | Liddell BESS | 0.9831 | Colongra PS Unit 1
Clermont Solar Farm | 0.915 |  |  |  | REZ_S8_Solar | 0.9601 | Bungala One Solar Farm |  |  |  | Lockhart Hybrid Facility - Battery | 0.8383 | Uranquinty PS Unit 11
Cohuna Solar Farm | 0.9413 |  |  |  | REZ_S9_Solar | 0.9601 | Bungala One Solar Farm |  |  |  | Melbourne Renewable Energy Hub - Side A | 0.9885 | Victorian Big Battery
Coleambally Solar Farm | 0.8894 |  |  |  | REZ_T1_Solar | 0.9119 | Musselroe |  |  |  | Mornington BESS | 0.9885 | Victorian Big Battery
Collector Wind Farm | 0.9576 |  |  |  | REZ_T2_Solar | 0.9555 | Poatina |  |  |  | Mortlake Battery | 0.9885 | Victorian Big Battery
Collinsville Solar Farm | 0.9132 |  |  |  | REZ_T3_Solar | 0.8888 | Lake Echo |  |  |  | Mt Fox BESS | 0.9559 | Kareeya PS Unit 1
Colongra | 0.9831 |  |  |  | N0_Solar | 1 | Default |  |  |  | Richmond Valley BESS | 0.8718 | New England Solar Farm 1
Columboola Solar Farm | 0.9746 |  |  |  | V0_Solar | 1 | Default |  |  |  | Stanwell BESS | 0.9181 | Stanwell PS Unit 1
Condamine A | 0.9832 |  |  |  | REZ_Q1_Wind | 0.9472 | Mount Emerald Wind farm |  |  |  | Tamworth BESS | 0.9831 | Colongra PS Unit 1
Coopers Gap Wind Farm | 0.9658 |  |  |  | REZ_Q2_Wind | 0.9938 | Woree |  |  |  | Tarong BESS | 0.9751 | Wandoan Battery Energy Storage System (BESS)
Corowa Solar Farm | 0.9365 |  |  |  | REZ_Q3_Wind | 0.9472 | Mount Emerald Wind farm |  |  |  | Terang BESS | 0.9756 | Ballarat BESS
Crookwell 2 Wind Farm | 0.9608 |  |  |  | REZ_Q4_Wind | 0.9938 | Woree |  |  |  | *Note, seperate load/generation MLF is no longer utilised for storage
Crowlands Wind Farm | 0.8904 |  |  |  | REZ_Q5_Wind | 0.9329 | Gladstone PS (275 kV) Unit 1
Crudine Ridge Wind Farm | 0.926 |  |  |  | REZ_Q6_Wind | 0.9329 | Gladstone PS (275 kV) Unit 1
Cullerin Range Wind Farm | 0.9437 |  |  |  | REZ_Q7_Wind | 0.9259 | Mt Millar Wind Farm
Darling Downs | 0.9617 |  |  |  | REZ_Q8_Wind | 0.9762 | Darling Downs Solar Farm
Darling Downs Solar Farm | 0.9762 |  |  |  | REZ_Q9_Wind | 0.9472 | Mount Emerald Wind farm
Darlington Point Solar Farm | 0.8958 |  |  |  | REZ_N1_Wind | 0.8697 | White Rock Solar Farm
Dartmouth | 0.9622 |  |  |  | REZ_N2_Wind | 0.8697 | White Rock Solar Farm
Daydream Solar Farm | 0.9098 |  |  |  | REZ_N3_Wind | 0.9622 | Bodangora Wind Farm
Devils Gate | 0.9537 |  |  |  | REZ_N4_Wind | 0.8101 | Silverton Wind Farm
Dry Creek GT | 0.9992 |  |  |  | REZ_N5_Wind | 1 | Default
Dulacca Wind Farm | 0.9776 |  |  |  | REZ_N6_Wind | 1 | Default
Dundonnell Wind Farm | 0.987 |  |  |  | REZ_N7_Wind | 1 | Default
Edenvale Solar Park | 0.972 |  |  |  | REZ_N8_Wind | 0.9444 | Boco Rock Wind Farm
Eildon | 0.9975 |  |  |  | REZ_N9_Wind | 0.9622 | Bodangora Wind Farm
Elaine Wind Farm | 0.9576 |  |  |  | REZ_N10_Wind | 0.9848 | Eraring 330 PS Unit 1
Emerald Solar Farm | 0.9111 |  |  |  | REZ_N11_Wind | 0.9856 | Tallawarra PS
Eraring | 0.9848 |  |  |  | REZ_V1_Wind | 1 | Default
Finley Solar Farm | 0.9255 |  |  |  | REZ_V2_Wind | 0.8899 | Ararat Wind Farm
Fisher | 0.9557 |  |  |  | REZ_V3_Wind | 0.924 | Waubra Wind Farm
Gangarri Solar Farm | 0.9837 |  |  |  | REZ_V4_Wind | 0.9849 | Macarthur Wind Farm
Gannawarra Solar Farm | 0.9413 |  |  |  | REZ_V5_Wind | 0.9825 | Bald Hills Wind Farm
Gladstone | 0.9323 |  |  |  | REZ_V6_Wind | 0.8899 | Ararat Wind Farm
Glenrowan West Solar Farm | 0.9675 |  |  |  | REZ_V7_Wind | 0.9825 | Bald Hills Wind Farm
Goonumbla Solar Farm | 0.9 |  |  |  | REZ_V8_Wind | 0.9849 | Macarthur Wind Farm
Gordon | 0.9731 |  |  |  | REZ_S1_Wind | 0.9656 | Lake Bonney Wind Farm
Granville Harbour Wind Farm | 0.9388 |  |  |  | REZ_S2_Wind | 0.9599 | Waterloo Wind Farm
Gullen Range Solar Farm | 0.958 |  |  |  | REZ_S3_Wind | 0.9467 | Hornsdale Wind Farm Stage 1
Gullen Range Wind Farm | 0.958 |  |  |  | REZ_S4_Wind | 0.8899 | Ararat Wind Farm
Gullen Range Wind Farm 2 | 0.958 |  |  |  | REZ_S5_Wind | 0.9812 | Davenport 33
Gunnedah Solar Farm | 0.8273 |  |  |  | REZ_S6_Wind | 0.9812 | Davenport 33
Gunning Wind Farm | 0.9437 |  |  |  | REZ_S7_Wind | 0.9601 | Lincoln Gap Wind Farm
Guthega | 0.893 |  |  |  | REZ_S8_Wind | 0.9259 | Mt Millar Wind Farm
Hallett 4 North Brown Hill Wind Farm | 0.9599 |  |  |  | REZ_S9_Wind | 0.9259 | Mt Millar Wind Farm
Hallett 5 The Bluff Wind Farm | 0.957 |  |  |  | REZ_T1_Wind | 1 | George Town
Hallett GT | 0.9599 |  |  |  | REZ_T2_Wind | 0.9555 | Poatina
Hallett Stage 1 Brown Hill Wind Farm | 0.9599 |  |  |  | REZ_T3_Wind | 0.9836 | Wild Cattle Hill Wind Farm
Hallett Stage 2 Hallett Hill Wind Farm | 0.957 |  |  |  | REZ_T4_Wind | 0.9555 | Poatina
Hamilton Solar Farm | 0.906 |  |  |  | REZ_T5_Wind | 1 | George Town
Happy Valley Reservoir | 1.0041 |  |  |  | N0_Wind | 1 | Default
Haughton Solar Farm | 0.9151 |  |  |  | V0_Wind | 1 | Default
Hayman Solar Farm | 0.9098 |  |  |  | Note: where a appropriate shadow gen cannot be identified 'default' is used, which is 1
Hillston Sun Farm | 0.8979
Hornsdale Wind Farm Stage 1 | 0.9467
Hornsdale Wind Farm Stage 2 | 0.9467
Hornsdale Wind Farm Stage 3 | 0.9467
Hughenden Solar Farm | 0.9222
Hume Dam NSW | 0.9205
Hume Dam VIC | 0.9389
Jeeralang A | 0.9764
Jeeralang B | 0.9764
Jemalong Solar | 0.8964
John Butters | 0.9208
Junee Solar Farm | 0.9108
Kaban Green Power Hub - Wind Farm | 0.9575
Karadoc Solar Farm | 0.8877
Kareeya | 0.9559
Kennedy Energy Park Solar Farm | 0.9667
Kennedy Energy Park Wind Farm | 0.9667
Kiamal Solar Farm stage 1 | 0.8775
Kiata Wind Farm | 0.8827
Kidston Solar Farm | 0.9222
Kogan Creek | 0.9673
Ladbroke Grove | 0.9736
Lake Bonney 1 Wind Farm | 0.9656
Lake Bonney 2 Wind Farm | 0.9656
Lake Bonney 3 Wind Farm | 0.9656
Lake Echo | 0.8888
Laverton North | 0.9979
Lemonthyme / Wilmot | 0.9567
Lilyvale Solar Farm | 0.9064
Limondale Solar Farm 1 | 0.8255
Limondale Solar Farm 2 | 0.831
Lincoln Gap Wind Farm - stage 1 | 0.9601
Lincoln Gap Wind Farm - stage 2 | 0.9601
Longreach Solar Farm | 0.915
Lonsdale | 1.0039
Loy Yang A Power Station | 0.9782
Loy Yang B | 0.9782
Macarthur Wind Farm | 0.9849
Mackintosh | 0.9059
Manildra Solar Farm | 0.9557
Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | 0.9943
Mannum Adelaide Pumping Station No 3 - MAPL3 (Tungkillo) | 0.9946
Maryrorough Solar Farm | 0.9914
Meadowbank | 0.9688
Middlemount Solar Farm | 0.9111
Millmerran | 0.9763
Mintaro GT | 0.9746
Molong Solar Farm | 0.9733
Moorabool Wind Farm | 0.9576
Moree Solar Farm | 0.7977
Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | 0.9847
Morgan To Whyalla Pipeline No 2 PS | 0.988
Morgan To Whyalla Pipeline No 3 PS | 0.9847
Morgan To Whyalla Pipeline No 4 PS | 0.9796
Mortlake | 0.9927
Mortlake South Wind Farm | 0.9528
Mortons Lane Wind Farm | 0.9933
Mount Emerald Wind Farm | 0.9472
Mount Millar Wind Farm | 0.9259
Moura Solar Farm | 0.9081
Mt Gellibrand Wind Farm | 0.9896
Mt Mercer Wind Farm | 0.9576
Mt Piper | 0.9164
Mt Stuart | 0.9164
Murra Warra Wind Farm - stage 1 | 0.8768
Murra Warra Wind Farm - stage 2 | 0.8768
Murray 1 | 0.985
Murray 2 | 0.985
Murray Bridge - Onkaparinga Pipeline Pump 2 | 1.0006
Musselroe Wind Farm | 0.9119
Nevertire Solar Farm | 0.9439
New England Solar Farm | 0.8718
Newport | 0.9937
Numurkah Solar Farm | 0.9738
Nyngan Solar Plant | 0.9897
Oakey 1 Solar Farm | 0.9869
Oakey 2 Solar Farm | 0.9869
Oakey Power Station | 0.9628
Oaklands Hill Wind Farm | 0.9933
Osborne | 0.9997
Parkes Solar Farm | 0.9
Pelican Point | 0.9984
Poatina | 0.9555
Port Augusta Renewable Energy Park - Solar | 0.9654
Port Augusta Renewable Energy Park - Wind | 0.9654
Port Lincoln GT | 0.9822
Port Stanvac 1 | 1.0039
Portland Wind Farm | 0.9656
Quarantine | 0.9946
Reece | 0.9052
Roma | 0.9643
Ross River Solar Farm | 0.9222
Rugby Run Solar Farm | 0.9185
Salt Creek Wind Farm | 0.9476
Sapphire Wind Farm | 0.9086
Shoalhaven | 0.9732
Silverton Wind Farm | 0.8101
Smithfield Energy Facility | 1
Snapper Point Power Station | 0.9993
Snowtown S2 Wind Farm | 0.9638
Snowtown Wind Farm | 0.8968
Snuggery | 0.9877
Somerton | 0.996
Stanwell | 0.9181
Starfish Hill Wind Farm | 1.0039
Stockyard Hill Wind Farm | 0.9869
Sun Metals Corporation Solar Farm | 0.9979
Sunraysia Solar Farm | 0.8255
Suntop Solar Farm | 0.9224
Susan River Solar Farm | 0.9704
Swanbank E GT | 0.9987
Tailem Bend Solar Farm | 1.003
Tailem Bend Solar Farm - stage 2 | 1.0079
Tallawarra | 0.9856
Tamar Valley Combined Cycle | 1
Tamar Valley Peaking | 0.9968
Taralga Wind Farm | 1.0095
Tarong | 0.9712
Tarong North | 0.9712
Tarraleah | 0.8977
Torrens Island B | 0.9997
Townsville Power Station | 0.9519
Trevallyn | 0.9825
Tribute | 0.9089
Tumut 3 | 0.9318
Tungatinah | 0.8782
Upper Tumut | 0.9318
Uranquinty | 0.8383
Vales Point B | 0.9869
Valley Power | 0.9782
Wagga North Solar Farm | 0.907
Warwick Solar Farm | 0.9914
Waterloo Wind Farm | 0.9599
Wattle Point Wind Farm | 0.8073
Waubra Wind Farm | 0.924
Wellington Solar Farm | 0.9439
Wemen Solar Farm | 0.8947
West Kiewa | 1.011
West Wyalong Solar Farm | 0.9108
Western Downs Green Power Hub | 0.9712
White Rock Solar Farm | 0.8289
White Rock Wind Farm - Stage 1 | 0.8289
Whitsunday Solar Farm | 0.901
Willogoleche Wind Farm | 0.9534
Winton Solar Farm | 0.9675
Wivenhoe | 0.9994
Woodlawn Wind Farm | 0.9575
Woolnorth Wind Farm | 0.9112
Wyalong Solar Farm | 0.9108
Yallourn W | 0.9624
Yaloak South Wind Farm | 0.9759
Yambuk Wind Farm | 0.9933
Yarranlea Solar Farm | 0.9914
Yarwun Cogen | 0.9349
Yatpool Solar Farm | 0.8877
Yendon Wind Farm | 0.9522

## Affine Heat rates
Go to Assumptions Summary
Affine Heat rates (Time-Sequential Model)
Parameters to model in detailed the efficiency of thermal generators (as-gen, HHV) via a no-load component and a constant marginal heat rate
For the steam turbines of CCGT the heat rate represents the conversion of exhaust heat from the gas turbines (rather than fuel) into electricity
Existing generators |  |  |  |  | New entrant technologies
Station | Generating Unit | Technology Type | No load heat input (GJ/h) | Marginal heat rate (GJ/MWh) | Technology | Unit nominal capacity (MW) | No load heat input (GJ/h) | Marginal heat rate (GJ/MWh)
Bayswater | BW01 | Steam Sub Critical | 420.42 | 8.8118 | OCGT (small GT) | 49 | 133.2669 | 7.4705
Bayswater | BW02 | Steam Sub Critical | 420.42 | 8.8118 | OCGT (large GT) | 265 | 720.7293 | 8.2115
Bayswater | BW03 | Steam Sub Critical | 420.42 | 8.8118 | CCGT | 409 | 390.1276 | 6.2954
Bayswater | BW04 | Steam Sub Critical | 420.42 | 8.8118 | CCGT with CCS | 409 | 390.1276 | 8.0093
Callide B | CALL_B_1 | Steam Sub Critical | 222.95 | 8.5233 | Biomass | 30 | 39.8 | 16.0433
Callide B | CALL_B_2 | Steam Sub Critical | 222.95 | 8.5233 | Hydrogen reciprocating engines | 17.6 | 0 | 11.7031
Callide C | CPP_3 | Steam Super Critical | 286.65 | 8.6653 | Notes: 1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
Callide C | CPP_4 | Steam Super Critical | 286.65 | 8.6653
Eraring | ER01 | Steam Sub Critical | 458.64 | 8.9121
Eraring | ER02 | Steam Sub Critical | 458.64 | 8.9121
Eraring | ER03 | Steam Sub Critical | 458.64 | 8.9121
Eraring | ER04 | Steam Sub Critical | 458.64 | 8.9121
Gladstone | GSTONE1 | Steam Sub Critical | 178.36 | 8.8367
Gladstone | GSTONE2 | Steam Sub Critical | 178.36 | 8.8367
Gladstone | GSTONE3 | Steam Sub Critical | 178.36 | 8.8367
Gladstone | GSTONE4 | Steam Sub Critical | 178.36 | 8.8367
Gladstone | GSTONE5 | Steam Sub Critical | 178.36 | 8.8367
Gladstone | GSTONE6 | Steam Sub Critical | 178.36 | 8.8367
Kogan Creek | KPP_1 | Steam Super Critical | 473.928 | 8.165
Millmerran | MPP_1 | Steam Super Critical | 271.362 | 8.5702
Millmerran | MPP_2 | Steam Super Critical | 271.362 | 8.5702
Mt Piper | MP1 | Steam Sub Critical | 420.42 | 8.6175
Mt Piper | MP2 | Steam Sub Critical | 420.42 | 8.6175
Stanwell | STAN-1 | Steam Sub Critical | 232.505 | 8.431
Stanwell | STAN-2 | Steam Sub Critical | 232.505 | 8.431
Stanwell | STAN-3 | Steam Sub Critical | 232.505 | 8.431
Stanwell | STAN-4 | Steam Sub Critical | 232.505 | 8.431
Tarong | TARONG#1 | Steam Super Critical | 222.95 | 8.5702
Tarong | TARONG#2 | Steam Super Critical | 222.95 | 8.5702
Tarong | TARONG#3 | Steam Super Critical | 222.95 | 8.5702
Tarong | TARONG#4 | Steam Super Critical | 222.95 | 8.5702
Tarong North | TNPS1 | Steam Sub Critical | 286.65 | 8.0168
Vales Point B | VP5 | Steam Sub Critical | 420.42 | 9.0404
Vales Point B | VP6 | Steam Sub Critical | 420.42 | 9.0404
Loy Yang A Power Station | LYA1 | Steam Sub Critical | 412.84 | 11.4249
Loy Yang A Power Station | LYA2 | Steam Sub Critical | 390.7236 | 11.4249
Loy Yang A Power Station | LYA3 | Steam Sub Critical | 412.84 | 11.4249
Loy Yang A Power Station | LYA4 | Steam Sub Critical | 412.84 | 11.4249
Loy Yang B | LOYYB1 | Steam Sub Critical | 394.4096 | 11.8063
Loy Yang B | LOYYB2 | Steam Sub Critical | 394.4096 | 11.8063
Yallourn W | YWPS1 | Steam Sub Critical | 258.025 | 13.1624
Yallourn W | YWPS2 | Steam Sub Critical | 258.025 | 13.1624
Yallourn W | YWPS3 | Steam Sub Critical | 276.4554 | 13.1624
Yallourn W | YWPS4 | Steam Sub Critical | 276.4554 | 13.1624
Swanbank E GT | SWAN_E | CCGT | 367.235 | 6.4842
Tallawarra | TALWA1 | CCGT | 419.6971 | 6.0364
Yarwun Cogen | YARWUN_1 | CCGT Cogen | 171.6943 | 9.4208
Condamine A | CPSA_GT1 | CCGT - Gas Turbine | 132.4956 | 8.9248
Condamine A | CPSA_GT2 | CCGT - Gas Turbine | 132.4956 | 8.9248
Condamine A | CPSA_ST | CCGT - Steam Turbine | 0 | 13.0425
Darling Downs | DDPS1_GT1 | CCGT - Gas Turbine | 427.6689 | 9.524
Darling Downs | DDPS1_GT2 | CCGT - Gas Turbine | 427.6689 | 9.524
Darling Downs | DDPS1_GT3 | CCGT - Gas Turbine | 427.6689 | 9.524
Darling Downs | DDPS1_ST | CCGT - Steam Turbine | 0 | 12.294
Osborne | OsborneGT | CCGT - Gas Turbine | 299.0206 | 9.9184
Osborne | OsborneST | CCGT - Steam Turbine | 0 | 16.8482
Pelican Point | PPCCGTGT1 | CCGT - Gas Turbine | 436.3338 | 8.445
Pelican Point | PPCCGTGT2 | CCGT - Gas Turbine | 436.3338 | 8.445
Pelican Point | PPCCGTST | CCGT - Steam Turbine | 0 | 15.1328
Tamar Valley Combined Cycle | TVCC201_GT | CCGT - Gas Turbine | 344.206 | 8.3685
Tamar Valley Combined Cycle | TVCC201_ST | CCGT - Steam Turbine | 0 | 14.8793
Townsville Power Station | YABULU | CCGT - Gas Turbine | 411.7537 | 9.0088
Townsville Power Station | YABULU2 | CCGT - Steam Turbine | 0 | 15.2043
Newport | NPS | Gas-powered steam turbine | 385.3212 | 9.5151
Torrens Island B | TORRB1 | Gas-powered steam turbine | 154.1285 | 9.9436
Torrens Island B | TORRB2 | Gas-powered steam turbine | 154.1285 | 9.9436
Torrens Island B | TORRB3 | Gas-powered steam turbine | 154.1285 | 9.9436
Torrens Island B | TORRB4 | Gas-powered steam turbine | 154.1285 | 9.9436
Bairnsdale | BDL01 | OCGT | 127.8275 | 7.7759
Bairnsdale | BDL02 | OCGT | 127.8275 | 7.7759
Barcaldine Power Station | BARCALDN | OCGT | 100.6301 | 10.0011
Bell Bay Three | BBTHREE1 | OCGT | 108.7893 | 9.3204
Bell Bay Three | BBTHREE2 | OCGT | 108.7893 | 9.3204
Bell Bay Three | BBTHREE3 | OCGT | 108.7893 | 9.3204
Braemar | BRAEMAR1 | OCGT | 456.9152 | 9.1615
Braemar | BRAEMAR2 | OCGT | 456.9152 | 9.1615
Braemar | BRAEMAR3 | OCGT | 456.9152 | 9.1615
Braemar 2 Power Station | BRAEMAR5 | OCGT | 470.5139 | 9.1615
Braemar 2 Power Station | BRAEMAR6 | OCGT | 470.5139 | 9.1615
Braemar 2 Power Station | BRAEMAR7 | OCGT | 470.5139 | 9.1615
Bolivar Power Station | BOLIVPS1_1 | OCGT | 83.7678 | 7.4703
Bolivar Power Station | BOLIVPS1_2 | OCGT | 83.7678 | 7.4703
Bolivar Power Station | BOLIVPS1_3 | OCGT | 83.7678 | 7.4703
Bolivar Power Station | BOLIVPS1_4 | OCGT | 83.7678 | 7.4703
Colongra | CG1 | OCGT | 492.2717 | 8.4258
Colongra | CG2 | OCGT | 492.2717 | 8.4258
Colongra | CG3 | OCGT | 492.2717 | 8.4258
Colongra | CG4 | OCGT | 492.2717 | 8.4258
Dry Creek GT | DRYCGT1 | OCGT | 141.4261 | 10.9685
Dry Creek GT | DRYCGT2 | OCGT | 141.4261 | 10.9685
Dry Creek GT | DRYCGT3 | OCGT | 141.4261 | 10.9685
Hallett GT | AGLHAL01 | OCGT | 46.2355 | 12.1563
Hallett GT | AGLHAL02 | OCGT | 46.2355 | 12.1563
Hallett GT | AGLHAL03 | OCGT | 46.2355 | 12.1563
Hallett GT | AGLHAL04 | OCGT | 46.2355 | 12.1563
Hallett GT | AGLHAL05 | OCGT | 56.4345 | 12.1563
Hallett GT | AGLHAL06 | OCGT | 56.4345 | 12.1563
Hallett GT | AGLHAL07 | OCGT | 44.1685 | 12.1563
Hallett GT | AGLHAL08 | OCGT | 44.1685 | 12.1563
Hallett GT | AGLHAL09 | OCGT | 73.4328 | 12.1563
Hallett GT | AGLHAL10 | OCGT | 69.6252 | 12.1563
Hallett GT | AGLHAL11 | OCGT | 59.1814 | 12.1563
Hallett GT | AGLHAL12 | OCGT | 48.9552 | 12.1563
Hallett GT | AGLHALRE | OCGT | 95.1907 | 12.1563
Jeeralang A | JLA01 | OCGT | 144.1459 | 12.5345
Jeeralang A | JLA02 | OCGT | 144.1459 | 12.5345
Jeeralang A | JLA03 | OCGT | 144.1459 | 12.5345
Jeeralang A | JLA04 | OCGT | 144.1459 | 12.5345
Jeeralang B | JLB01 | OCGT | 206.6997 | 12.5345
Jeeralang B | JLB02 | OCGT | 206.6997 | 12.5345
Jeeralang B | JLB03 | OCGT | 206.6997 | 12.5345
Ladbroke Grove | LADBROK1 | OCGT | 108.7893 | 9.1615
Ladbroke Grove | LADBROK2 | OCGT | 108.7893 | 9.1615
Laverton North | LNGS1 | OCGT | 424.2784 | 8.7819
Laverton North | LNGS2 | OCGT | 424.2784 | 8.7819
Mintaro GT | MINTARO | OCGT | 244.776 | 10.0011
Mortlake | MORTLK11 | OCGT | 794.1621 | 8.4258
Mortlake | MORTLK12 | OCGT | 794.1621 | 8.4258
Mt Stuart | MSTUART1 | OCGT | 397.0811 | 9.1615
Mt Stuart | MSTUART2 | OCGT | 397.0811 | 9.1615
Mt Stuart | MSTUART3 | OCGT | 357.6449 | 9.1615
Oakey Power Station | OAKEY1 | OCGT | 470.5139 | 8.2225
Oakey Power Station | OAKEY2 | OCGT | 470.5139 | 8.2225
Port Lincoln GT | POR01-1 | OCGT | 67.9933 | 10.0917
Port Lincoln GT | POR01-2 | OCGT | 67.9933 | 10.0917
Port Lincoln GT | POR01-3 | OCGT | 63.9137 | 10.0917
Quarantine | QPS1 | OCGT | 78.8723 | 7.9946
Quarantine | QPS2 | OCGT | 65.2736 | 7.9946
Quarantine | QPS3 | OCGT | 65.2736 | 7.9946
Quarantine | QPS4 | OCGT | 65.2736 | 7.9946
Quarantine | QPS5 | OCGT | 348.1259 | 7.9946
Roma | ROMA_7 | OCGT | 108.7893 | 9.1615
Roma | ROMA_8 | OCGT | 108.7893 | 9.1615
Smithfield Energy Facility | SITHE01 | OCGT | 108.1067 | 10.9685
Smithfield Energy Facility | SITHE02 | OCGT | 113.5271 | 10.9685
Smithfield Energy Facility | SITHE03 | OCGT | 113.5271 | 10.9685
Smithfield Energy Facility | SITHE04 | OCGT | 167.987 | 10.9685
Snapper Point Power Station | SNAPPER1_1 | OCGT | 83.7678 | 7.4705
Snapper Point Power Station | SNAPPER1_2 | OCGT | 83.7678 | 7.4705
Snapper Point Power Station | SNAPPER1_3 | OCGT | 83.7678 | 7.4705
Snapper Point Power Station | SNAPPER1_4 | OCGT | 83.7678 | 7.4705
Snapper Point Power Station | SNAPPER1_5 | OCGT | 83.7678 | 7.4705
Snuggery | SNUG1 | OCGT | 57.1144 | 10.7131
Snuggery | SNUG2 | OCGT | 57.1144 | 10.7131
Snuggery | SNUG3 | OCGT | 57.1144 | 10.7131
Somerton | AGLSOM01 | OCGT | 115.5887 | 12.1563
Somerton | AGLSOM02 | OCGT | 115.5887 | 12.1563
Somerton | AGLSOM03 | OCGT | 115.5887 | 12.1563
Somerton | AGLSOM04 | OCGT | 115.5887 | 12.1563
Tamar Valley Peaking | TVPP104 | OCGT | 157.7445 | 10.0011
Uranquinty | URANQ11 | OCGT | 451.4757 | 8.4258
Uranquinty | URANQ12 | OCGT | 451.4757 | 8.4258
Uranquinty | URANQ13 | OCGT | 451.4757 | 8.4258
Uranquinty | URANQ14 | OCGT | 451.4757 | 8.4258
Valley Power | VPGS1 | OCGT | 135.9867 | 12.1563
Valley Power | VPGS2 | OCGT | 135.9867 | 12.1563
Valley Power | VPGS3 | OCGT | 135.9867 | 12.1563
Valley Power | VPGS4 | OCGT | 135.9867 | 12.1563
Valley Power | VPGS5 | OCGT | 135.9867 | 12.1563
Valley Power | VPGS6 | OCGT | 135.9867 | 12.1563
Angaston | ANGAS1 | Reciprocating Engine | 0 | 12.775
Angaston | ANGAS2 | Reciprocating Engine | 0 | 12.775
Barker Inlet Power Station | BIPS1_01 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_02 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_03 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_04 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_05 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_06 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_07 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_08 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_09 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_10 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_11 | Reciprocating Engine | 0 | 7.8947
Barker Inlet Power Station | BIPS1_12 | Reciprocating Engine | 0 | 7.8947
Lonsdale | LONSDALE | Reciprocating Engine | 0 | 7.8947
Port Stanvac 1 | PTSTAN1_1 | Reciprocating Engine | 0 | 7.8947
Port Stanvac 1 | PTSTAN1_2 | Reciprocating Engine | 0 | 7.8947
Note: Sourced from GHD 2018 AEMO costs and technical parameter review and AEMO internal analysis (for Gas-fired steam turbines).
Committed/Anticipated generators
Station | Generating Unit | Technology Type | No load heat input (GJ/h) | Marginal heat rate (GJ/MWh)
Tallawarra B | Tallawarra B | OCGT | 870.3147 | 8.2115
Kurri Kurri | Kurri Kurri 1 | OCGT | 1019.9 | 8.2115
Kurri Kurri | Kurri Kurri 2 | OCGT | 1019.9 | 8.2115
Kogan Gas | Kogan Gas | Hydrogen-based gas turbines | 543.9467 | 10.0003
SA Hydrogen Turbine | SA Hydrogen Turbine | Hydrogen-based gas turbines | 543.9467 | 10.0003
Note: Sourced from Aurecon 2022 -23 AEMO costs and technical parameter review and AEMO internal analysis.

## Max Ramp Rates
Go to Assumptions Summary
Maximum Ramp Rates (Time-Sequential Model)
Maximum rate of change in output of existing coal generators is based on 90th percentile bid ramp rates from Apr-20 to Mar-23. For other existing thermal generators this has been sourced from GHD 2018
For CCGTs modelled as separate gas and steam turbines, the ramp limit is applied to the gas turbine only
For technologies not listed, it is assumed that ramp rate does not limit dispatch.
Existing generators |  |  |  |  | New entrant technologies
Generator Station | Generating Unit | Technology Type | Max Ramp Up (MW/min) | Max Ramp Down (MW/min) | Technology | Max Ramp Up (MW/min) | Max Ramp Down (MW/min)
Bayswater | BW01 | Black Coal | 4 | 4 | OCGT (small GT) | 22 | 22
Bayswater | BW02 | Black Coal | 4 | 4 | OCGT (large GT) | 22 | 22
Bayswater | BW03 | Black Coal | 4 | 4 | CCGT | 22 | 22
Bayswater | BW04 | Black Coal | 4 | 4 | CCGT with CCS | 22 | 22
Callide B | CALL_B_1 | Black Coal | 4 | 4 | Biomass | 1 | 1
Callide B | CALL_B_2 | Black Coal | 4 | 4 | Hydrogen reciprocating engines | 12.48 | 12.48
Callide C | CPP_3 | Black Coal | 4 | 4 | Notes: 1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
Callide C | CPP_4 | Black Coal | 4 | 4
Eraring | ER01 | Black Coal | 5 | 5
Eraring | ER02 | Black Coal | 5 | 5
Eraring | ER03 | Black Coal | 5 | 5
Eraring | ER04 | Black Coal | 5 | 5
Gladstone | GSTONE1 | Black Coal | 5 | 5
Gladstone | GSTONE2 | Black Coal | 5 | 5
Gladstone | GSTONE3 | Black Coal | 5 | 5
Gladstone | GSTONE4 | Black Coal | 5 | 5
Gladstone | GSTONE5 | Black Coal | 5 | 5
Gladstone | GSTONE6 | Black Coal | 5 | 5
Kogan Creek | KPP_1 | Black Coal | 8 | 8
Millmerran | MPP_1 | Black Coal | 5 | 5
Millmerran | MPP_2 | Black Coal | 5 | 5
Mt Piper | MP1 | Black Coal | 3 | 3
Mt Piper | MP2 | Black Coal | 3 | 3
Stanwell | STAN-1 | Black Coal | 4 | 4
Stanwell | STAN-2 | Black Coal | 4 | 4
Stanwell | STAN-3 | Black Coal | 4 | 4
Stanwell | STAN-4 | Black Coal | 4 | 4
Tarong | TARONG#1 | Black Coal | 4 | 4
Tarong | TARONG#2 | Black Coal | 4 | 4
Tarong | TARONG#3 | Black Coal | 4 | 4
Tarong | TARONG#4 | Black Coal | 4 | 4
Tarong North | TNPS1 | Black Coal | 4 | 4
Vales Point B | VP5 | Black Coal | 6 | 6
Vales Point B | VP6 | Black Coal | 6 | 6
Loy Yang A Power Station | LYA1 | Brown Coal | 5 | 5
Loy Yang A Power Station | LYA2 | Brown Coal | 5 | 5
Loy Yang A Power Station | LYA3 | Brown Coal | 5 | 5
Loy Yang A Power Station | LYA4 | Brown Coal | 5 | 5
Loy Yang B | LOYYB1 | Brown Coal | 10 | 10
Loy Yang B | LOYYB2 | Brown Coal | 10 | 10
Yallourn W | YWPS1 | Brown Coal | 3 | 3
Yallourn W | YWPS2 | Brown Coal | 3 | 3
Yallourn W | YWPS3 | Brown Coal | 3 | 3
Yallourn W | YWPS4 | Brown Coal | 3 | 3
Swanbank E GT | SWAN_E | CCGT | 17 | 17
Tallawarra | TALWA1 | CCGT | 8 | 8
Yarwun Cogen | YARWUN_1 | CCGT | 10 | 10
Condamine | CPSA_GT1 | CCGT - Gas Turbine | 1 | 1
Condamine | CPSA_GT2 | CCGT - Gas Turbine | 1 | 1
Darling Downs | DDPS1_GT1 | CCGT - Gas Turbine | 2 | 2
Darling Downs | DDPS1_GT2 | CCGT - Gas Turbine | 2 | 2
Darling Downs | DDPS1_GT3 | CCGT - Gas Turbine | 2 | 2
Osborne | OsborneGT | CCGT - Gas Turbine | 2.67 | 2.67
Pelican Point | PPCCGTGT1 | CCGT - Gas Turbine | 3 | 3
Pelican Point | PPCCGTGT2 | CCGT - Gas Turbine | 3 | 3
Tamar Valley | TVCC201_GT | CCGT - Gas Turbine | 6 | 6
Townsville Power Station | YABULU | CCGT - Gas Turbine | 5.7 | 5.7
Newport | NPS | Gas-powered steam turbine | 5.6 | 5.6
Torrens Island B | TORRB1 | Gas-powered steam turbine | 5 | 5
Torrens Island B | TORRB2 | Gas-powered steam turbine | 5 | 5
Torrens Island B | TORRB3 | Gas-powered steam turbine | 5 | 5
Torrens Island B | TORRB4 | Gas-powered steam turbine | 5 | 5
Kogan Gas | Kogan Gas | Hydrogen-based gas turbines | 22 | 22
SA Hydrogen Turbine | SA Hydrogen Turbine | Hydrogen-based gas turbines | 22 | 22

## CCGT Unit Max Capacity
Go to Assumptions Summary
CCGTs Modelled as separate gas and steam turbines (Time-Sequential Model)
Separate Maximum Capacities for the gas and steam turbines of CCGTs
Sourced from NEM Generation Information (July 2022 release)
Existing generators
Generator Station | Generating Unit | Technology Type | Max Capacity (MW)
Condamine | CPSA_GT1 | CCGT - Gas Turbine | 43.7
Condamine | CPSA_GT2 | CCGT - Gas Turbine | 43.7
Condamine | CPSA_ST | CCGT - Steam Turbine | 57
Darling Downs | DDPS1_GT1 | CCGT - Gas Turbine | 121.5
Darling Downs | DDPS1_GT2 | CCGT - Gas Turbine | 121.5
Darling Downs | DDPS1_GT3 | CCGT - Gas Turbine | 121.5
Darling Downs | DDPS1_ST | CCGT - Steam Turbine | 280
Osborne | OsborneGT | CCGT - Gas Turbine | 118
Osborne | OsborneST | CCGT - Steam Turbine | 62
Pelican Point | PPCCGTGT1 | CCGT - Gas Turbine | 179
Pelican Point | PPCCGTGT2 | CCGT - Gas Turbine | 179
Pelican Point | PPCCGTST | CCGT - Steam Turbine | 171
Tamar Valley | TVCC201_GT | CCGT - Gas Turbine | 140
Tamar Valley | TVCC201_ST | CCGT - Steam Turbine | 68
Townsville Power Station | YABULU | CCGT - Gas Turbine | 160
Townsville Power Station | YABULU2 | CCGT - Steam Turbine | 84

## GPG Min Stable Level
Go to Assumptions Summary
Minimum Stable Level (Time-Sequential Model)
Minimum Stable Levels for CCGT and Gas-fired steam turbines
These assumptions are based on AEMO internal analysis of historical generation and operational experience
Where a generator is not listed in these tables, the Min Stable Level outlined previously on the Generation Limits worksheet is applied.
Link | Generation limits
Existing generators |  |  |  | New entrant technologies
Generator Station | Generating Unit | Technology Type | Min Stable Level (MW) | Technology | Min Stable Level (% of nameplate)
Condamine | CPSA_GT1 | CCGT - Gas Turbine | 20 | CCGT | 46%
Condamine | CPSA_GT2 | CCGT - Gas Turbine | 20 | CCGT with CCS | 46%
Condamine | CPSA_ST | CCGT - Steam Turbine | 13.1 | Biomass | 40%
Darling Downs | DDPS1_GT1 | CCGT - Gas Turbine | 58.3 | Note: 1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
Darling Downs | DDPS1_GT2 | CCGT - Gas Turbine | 58.3
Darling Downs | DDPS1_GT3 | CCGT - Gas Turbine | 58.3
Darling Downs | DDPS1_ST | CCGT - Steam Turbine | 38.9
Newport | NPS | Gas-powered steam turbine | 100
Osborne | OsborneGT | CCGT - Gas Turbine | 90
Osborne | OsborneST | CCGT - Steam Turbine | 20
Pelican Point | PPCCGTGT1 | CCGT - Gas Turbine | 60
Pelican Point | PPCCGTGT2 | CCGT - Gas Turbine | 60
Pelican Point | PPCCGTST | CCGT - Steam Turbine | 42
Quarantine | QPS5 | OCGT | 73.5
Swanbank E GT | SWAN_E | CCGT | 95
Tallawarra | TALWA1 | CCGT | 190
Torrens Island B | TORRB1 | Gas-powered steam turbine | 40
Torrens Island B | TORRB2 | Gas-powered steam turbine | 40
Torrens Island B | TORRB3 | Gas-powered steam turbine | 40
Torrens Island B | TORRB4 | Gas-powered steam turbine | 40
Tamar Valley | TVCC201_GT | CCGT - Gas Turbine | 70.8
Tamar Valley | TVCC201_ST | CCGT - Steam Turbine | 41.4
Townsville Power Station | YABULU | CCGT - Gas Turbine | 83
Townsville Power Station | YABULU2 | CCGT - Steam Turbine | 57
Yarwun Cogen | YARWUN_1 | CCGT | 106

## Min Up&Down Times
Go to Assumptions Summary
Minimum Up and Down Times (Time-Sequential Model)
Minimum times for CCGT and gas-powered steam turbine units to be online (Up) or offline (Down) in unit commitment model
For CCGTs modelled as separate gas and steam turbines, the min up time is applied to the gas turbine only
Sourced from ACIL 2014 and validated by AEMO analysis
Existing generators |  |  |  | New entrant technologies
Generator Station | Generating Unit | Technology Type | Min Up/Down Time (h) | Technology | Min Up/Down Time (h)
Condamine | CPSA_GT1 | CCGT - Gas Turbine | 4 | OCGT (small GT) | 1
Condamine | CPSA_GT2 | CCGT - Gas Turbine | 4 | OCGT (large GT) | 1
Darling Downs | DDPS1_GT1 | CCGT - Gas Turbine | 4 | CCGT | 4
Darling Downs | DDPS1_GT2 | CCGT - Gas Turbine | 4 | CCGT with CCS | 4
Darling Downs | DDPS1_GT3 | CCGT - Gas Turbine | 4 | Note: Sourced from ACIL Allen 2014 AEMO Fuel and Technology Cost Review
Newport | NPS | Gas-powered steam turbine | 4
Osborne | OsborneGT | CCGT - Gas Turbine | 4
Pelican Point | PPCCGTGT1 | CCGT - Gas Turbine | 4
Pelican Point | PPCCGTGT2 | CCGT - Gas Turbine | 4
Swanbank E GT | SWAN_E | CCGT | 4
Tallawarra | TALWA1 | CCGT | 4
Torrens Island B | TORRB1 | Gas-powered steam turbine | 4
Torrens Island B | TORRB2 | Gas-powered steam turbine | 4
Torrens Island B | TORRB3 | Gas-powered steam turbine | 4
Torrens Island B | TORRB4 | Gas-powered steam turbine | 4
Tamar Valley | TVCC201_GT | CCGT - Gas Turbine | 4
Townsville Power Station | YABULU | CCGT - Gas Turbine | 4

## Costs Summary - PEM
Go to Assumptions Summary
Locational Cost Factors - Hydrogen Technologies
Locational cost factors for each cost region and cost component have been estimated by GHD to provide an indication of the variation in each cost component of the project costs between geographic regions.
Technology cost break down ratios are estimated from the technology cost for each of the cost components given by Aurecon.
The technology-specific locational factors are calculated as the sum of the adjustments in each technology cost component, which is calculated by multiplying its share in total capital cost of the technology by the locational cost factor.
CSIRO build costs projections for new entrants are overnight costs for construction in low cost zones as detailed in the Locational Cost Factors worksheet. To calculate the costs of these technologies elsewhere in Australia, use the locational cost factors given in that worksheet.
Locational cost factors
Region | Equipment costs | Fuel connection costs | Cost of land and development | Installation costs
NSW Low | 1 | 1 | 1 | 1
NSW Medium | 1.05 | 1.07 | 0.79 | 1.1
NSW High | 1.1 | 1.16 | 0.21 | 1.2
QLD Low | 1 | 1 | 1 | 1
QLD Medium | 1.05 | 1.1 | 0.49 | 1.15
QLD High | 1.1 | 1.21 | 0.21 | 1.31
SA Low | 1 | 1 | 1 | 1
SA Medium | 1.05 | 1.1 | 0.33 | 1.15
SA High | 1.1 | 1.2 | 0.17 | 1.29
TAS Low | 1 | 1 | 1 | 1
TAS Medium | 1.05 | 1.07 | 0.72 | 1.1
TAS High | 1.1 | 1.14 | 0.64 | 1.21
VIC Low | 1 | 1 | 1 | 1
VIC Medium | 1.03 | 1.03 | 0.69 | 1.03
VIC High | 1.05 | 1.05 | 0.36 | 1.05
Notes:
1. Sourced from GHD 2018 AEMO Costs and Technical Parameter Review, adjusted to be rebased to one in each region.
2. Operations and maintenance locational cost factors are independent to capital costs, however for the purposes of modelling, fixed O&M costs are combined with capital costs and discounted over the project life, as described in the Hydrogen technology Fixed OPEX section below.
Technology cost breakdown ratios
Technology | Equipment costs | Fuel connection costs | Cost of land and development | Installation costs
Electrolysers - Proton Exchange Membrane | 64.81% | 0% | 7.407% | 27.78%
Notes:
1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
Technology-specific locational cost factors
Electrolysers - Proton Exchange Membrane
VIC Low | 1
QLD Low | 1
NSW Low | 1
SA Low | 1
TAS Low | 1
NSW Medium | 1.0446
SA Medium | 1.0244
Hydrogen technology build costs, after application of locational cost factors ($/kW)
Build costs for new entrant generators by location for the selected scenario and technology. Does not include connection costs.
Cost trajectories calculated by applying locationl cost factors to baseline provided for a region-specific cost estimate, as developed by CSIRO and Aurecon.
Technology and scenario choices are available through the drop down menus.
Technology: | Scenario:
Electrolysers - Proton Exchange Membrane | Green Energy Exports
Technology type | Cost scenario | Sub-region | Regional cost zone | Locational cost factor | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Electrolysers - Proton Exchange Membrane | Green Energy Exports | NQ | QLD Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Electrolysers - Proton Exchange Membrane | Green Energy Exports | CQ | QLD Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Electrolysers - Proton Exchange Membrane | Green Energy Exports | GG | QLD Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Electrolysers - Proton Exchange Membrane | Green Energy Exports | SQ | QLD Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Electrolysers - Proton Exchange Membrane | Green Energy Exports | NNSW | NSW Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Electrolysers - Proton Exchange Membrane | Green Energy Exports | CNSW | NSW Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Electrolysers - Proton Exchange Membrane | Green Energy Exports | SNW | NSW Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Electrolysers - Proton Exchange Membrane | Green Energy Exports | SNSW | NSW Medium | 104.5% | 3357.7695 | 2929.9499 | 2626.1198 | 2297.7152 | 2009.5234 | 1758.1934 | 1538.1399 | 1346.0121 | 1177.3417 | 1029.8947 | 901.4371 | 788.6179 | 690.3199 | 603.1921 | 528.3516 | 462.4473 | 404.3621 | 352.9791 | 309.4152 | 284.8407 | 264.7343 | 250.213 | 236.8088 | 225.6385 | 216.7024 | 205.5321 | 196.596 | 187.6598 | 174.2555 | 174.2555 | 168.6704 | 168.6704
Electrolysers - Proton Exchange Membrane | Green Energy Exports | CSA | SA Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Electrolysers - Proton Exchange Membrane | Green Energy Exports | SESA | SA Medium | 102.4% | 3292.888 | 2873.335 | 2575.3758 | 2253.3169 | 1970.6938 | 1724.2201 | 1508.4187 | 1320.0033 | 1154.5921 | 1009.9942 | 884.0188 | 773.3795 | 676.981 | 591.5368 | 518.1424 | 453.5115 | 396.5487 | 346.1585 | 303.4364 | 279.3368 | 259.6189 | 245.3782 | 232.233 | 221.2786 | 212.5151 | 201.5607 | 192.7972 | 184.0337 | 170.8884 | 170.8884 | 165.4112 | 165.4112
Electrolysers - Proton Exchange Membrane | Green Energy Exports | VIC | VIC Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Electrolysers - Proton Exchange Membrane | Green Energy Exports | TAS | TAS Low | 100% | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643
Hydrogen technology Fixed OPEX, after application of locational cost factors ($/kW/year)
Fixed OPEX is based on 3% of capex per annum, based on the year of commissioning (Source: Aurecon 2022 Costs and Technical Parameter Review). For the purpose of modelling, the discounted Fixed OPEX over the project life will be added to the build cost.
Technology type | Cost scenario | Sub-region | Regional cost zone | Locational cost factor | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Electrolysers - Proton Exchange Membrane | Green Energy Exports | NQ | QLD Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Electrolysers - Proton Exchange Membrane | Green Energy Exports | CQ | QLD Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Electrolysers - Proton Exchange Membrane | Green Energy Exports | GG | QLD Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Electrolysers - Proton Exchange Membrane | Green Energy Exports | SQ | QLD Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Electrolysers - Proton Exchange Membrane | Green Energy Exports | NNSW | NSW Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Electrolysers - Proton Exchange Membrane | Green Energy Exports | CNSW | NSW Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Electrolysers - Proton Exchange Membrane | Green Energy Exports | SNW | NSW Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Electrolysers - Proton Exchange Membrane | Green Energy Exports | SNSW | NSW Medium | 104.5% | 93.2714 | 81.3875 | 72.9478 | 63.8254 | 55.8201 | 48.8387 | 42.7261 | 37.3892 | 32.7039 | 28.6082 | 25.0399 | 21.9061 | 19.1756 | 16.7553 | 14.6764 | 12.8458 | 11.2323 | 9.805 | 8.5949 | 7.9122 | 7.3537 | 6.9504 | 6.578 | 6.2677 | 6.0195 | 5.7092 | 5.461 | 5.2128 | 4.8404 | 4.8404 | 4.6853 | 4.6853
Electrolysers - Proton Exchange Membrane | Green Energy Exports | CSA | SA Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Electrolysers - Proton Exchange Membrane | Green Energy Exports | SESA | SA Medium | 102.4% | 91.4691 | 79.8149 | 71.5382 | 62.5921 | 54.7415 | 47.895 | 41.9005 | 36.6668 | 32.072 | 28.0554 | 24.5561 | 21.4828 | 18.805 | 16.4316 | 14.3928 | 12.5975 | 11.0152 | 9.6155 | 8.4288 | 7.7594 | 7.2116 | 6.8161 | 6.4509 | 6.1466 | 5.9032 | 5.5989 | 5.3555 | 5.112 | 4.7469 | 4.7469 | 4.5948 | 4.5948
Electrolysers - Proton Exchange Membrane | Green Energy Exports | VIC | VIC Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Electrolysers - Proton Exchange Membrane | Green Energy Exports | TAS | TAS Low | 100% | 89.2866 | 77.9104 | 69.8312 | 61.0986 | 53.4353 | 46.7522 | 40.9007 | 35.7918 | 31.3067 | 27.386 | 23.9701 | 20.9702 | 18.3563 | 16.0395 | 14.0494 | 12.2969 | 10.7524 | 9.3861 | 8.2277 | 7.5742 | 7.0396 | 6.6534 | 6.297 | 6 | 5.7623 | 5.4653 | 5.2277 | 4.9901 | 4.6336 | 4.6336 | 4.4851 | 4.4851
Notes:
1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
Hydrogen technology Variable OPEX, after application of locational cost factors ($/MWh sent out)
Technology Type | Variable OPEX ($/kW/year)
| VIC Low | VIC Medium | VIC High | QLD Low | 2022-23: QLD Medium; 2023-24: QLD High; 2024-25: NSW Low; 2025-26: NSW Medium; 2026-27: NSW High; 2027-28: SA Low; 2028-29: SA Medium; 2029-30: SA High; 2030-31: TAS Low; 2031-32: TAS Medium; 2032-33: TAS High
Electrolysers - Proton Exchange Membrane | 0 | 0 | 0 | 0 | 2022-23: 0; 2023-24: 0; 2024-25: 0; 2025-26: 0; 2026-27: 0; 2027-28: 0; 2028-29: 0; 2029-30: 0; 2030-31: 0; 2031-32: 0; 2032-33: 0
Notes:
1. Sourced from Aurecon 2022 Costs and Technical Parameter Review.
2. Electrolysers Variable O&M costs are assumed to be included in the Fixed O&M costs as per Aurecon's report.

## Build Costs - PEM
Go to Assumptions Summary
| Capital cost projections ($/kW), real 2023 dollars | [11 empty] | GenCost scenario mapping
| These capital cost trajectories are developed by CSIRO's GALLM (see GenCost 2022-23 Final report for more details) based on the technology-specific capital cost estimates provided by Aurecon (2022 AEMO Costs and Technical Parameter Review). The capital costs are overnight costs for construction in low cost zones as detailed in the Locational Cost Factors worksheet. To calculate the capital costs of these technologies elsewhere in Australia, use the locational cost factors given in that worksheet. | [12 empty] | Green Energy Exports | Step Change | Progressive Change
[13 empty] | GenCost scenario | Global NZE by 2050 | Global NZE post 2050 | Current Policies
Build cost ($/kW) | Build cost ($/kW)
|  | Scenario | GenCost scenario | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
| Electrolysers - Proton Exchange Membrane | Progressive Change | Current Policies | 3214.3158 | 2804.7739 | 2513.9243 | 2273.3318 | 2056.2639 | 1859.5127 | 1682.0089 | 1521.6139 | 1376.1891 | 1244.6652 | 1124.9036 | 1017.9736 | 920.6673 | 831.9154 | 752.7872 | 681.1441 | 615.9168 | 557.1053 | 503.6403 | 491.878 | 480.1157 | 452.3139 | 438.413 | 425.5814 | 405.2647 | 383.8787 | 367.8392 | 350.7304 | 331.483 | 331.483 | 327.2058 | 327.2058
Step Change Electrolysers - Proton Exchange Membrane | Electrolysers - Proton Exchange Membrane | Step Change | Global NZE post 2050 | 3214.3158 | 2804.7739 | 2513.9243 | 2259.4309 | 2030.6007 | 1825.2951 | 1640.3062 | 1474.5647 | 1324.8627 | 1191.2002 | 1070.3693 | 962.37 | 865.0637 | 777.3811 | 698.2529 | 627.6791 | 564.5904 | 506.8482 | 455.5218 | 434.1358 | 417.027 | 398.8489 | 382.8094 | 368.9085 | 357.1462 | 345.3839 | 334.6909 | 317.5821 | 299.404 | 299.404 | 295.1268 | 295.1268
Green Energy Exports Electrolysers - Proton Exchange Membrane | Electrolysers - Proton Exchange Membrane | Green Energy Exports | Global NZE by 2050 | 3214.3158 | 2804.7739 | 2513.9243 | 2199.5501 | 1923.6707 | 1683.0782 | 1472.4261 | 1288.5065 | 1127.0422 | 985.8946 | 862.9251 | 754.9258 | 660.8274 | 577.422 | 505.7789 | 442.6902 | 387.0866 | 337.8988 | 296.1961 | 272.6715 | 253.4241 | 239.5232 | 226.6916 | 215.9986 | 207.4442 | 196.7512 | 188.1968 | 179.6424 | 166.8108 | 166.8108 | 161.4643 | 161.4643

## Hydrogen demand - Domestic
Go to Assumptions Summary
Total additional domestic hydrogen consumption per NEM ISP subregions, excluding for Green Steel (Mt of H2)
Additional domestic hydrogen consumption is developed based on 2022 multi-sector model outcome (AusTIMES) conducted by CSIRO/ClimateWorks Centre.
'Additional' means any extra consumption of hydrogen in addition to the existing consumption for feedstock productions (such as Ammonia and fertilisers) as a result of emerging hydrogen applications.
All hydrogen is assumed to be produced by electrolysers, with none from steam methane reforming (SMR).
To estimate the electricity load required for the electrolysers, multiply 'Mts' to 'electrolysers electricity consumption rate (kWh/kg H2)' detailed in the sheet 'Other hydrogen assumptions'.
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | Progressive Change | Orchestrated Step Change | Hydrogen Export
Progressive Change
Region | ISP Subregion | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | SNSW | 0 | 0.0001042 | 0.00041971 | 0.0010292 | 0.0020589 | 0.0036958 | 0.0062694 | 0.009803 | 0.009242 | 0.0091398 | 0.0094494 | 0.011093 | 0.011207 | 0.011208 | 0.011208 | 0.011279 | 0.011354 | 0.011405 | 0.011405 | 0.011483 | 0.01157 | 0.011629 | 0.011652 | 0.011694 | 0.01172 | 0.019467 | 0.027121 | 0.034769 | 0.034798 | 0.034785 | 0.034748 | 0.034748
NSW | SNW | 0 | 0.00053095 | 0.0021209 | 0.0052517 | 0.010503 | 0.018887 | 0.031345 | 0.046654 | 0.047215 | 0.047318 | 0.048979 | 0.057951 | 0.058537 | 0.058536 | 0.058536 | 0.05854 | 0.058915 | 0.059162 | 0.059162 | 0.059573 | 0.05962 | 0.059888 | 0.059973 | 0.060174 | 0.060284 | 0.10012 | 0.13966 | 0.17922 | 0.17919 | 0.17921 | 0.17924 | 0.17924
QLD | CQ | 1.1455e-05 | 9.9673e-05 | 0.00018129 | 0.00020152 | 0.00020164 | 0.00018066 | 0.0058802 | 0.020811 | 0.0169 | 0.02077 | 0.027099 | 0.030639 | 0.033019 | 0.033356 | 0.033688 | 0.034012 | 0.034427 | 0.034941 | 0.035207 | 0.03562 | 0.03609 | 0.036505 | 0.036961 | 0.037371 | 0.037747 | 0.038222 | 0.038781 | 0.038781 | 0.038781 | 0.05394 | 0.055142 | 0.056733
QLD | SQ | 7.3549e-06 | 5.7957e-05 | 9.6338e-05 | 7.611e-05 | 7.5986e-05 | 9.6975e-05 | 0.0023747 | 0.0050948 | 0.010019 | 0.021343 | 0.033733 | 0.041913 | 0.047673 | 0.048365 | 0.049044 | 0.049714 | 0.050502 | 0.051422 | 0.051952 | 0.052691 | 0.053541 | 0.054326 | 0.055171 | 0.055933 | 0.056585 | 0.057463 | 0.058303 | 0.058303 | 0.058303 | 0.069592 | 0.070829 | 0.072872
SA | CSA | 5.3118e-05 | 0.00011269 | 0.00011891 | 0.0054519 | 0.016151 | 0.021527 | 0.021803 | 0.022122 | 0.022097 | 0.021626 | 0.020921 | 0.0207 | 0.020697 | 0.020695 | 0.020692 | 0.020686 | 0.020681 | 0.020676 | 0.020671 | 0.020667 | 0.025544 | 0.025644 | 0.025645 | 0.027214 | 0.027231 | 0.027218 | 0.02977 | 0.036157 | 0.036206 | 0.036216 | 0.03632 | 0.036349
SA | SESA | 8.5725e-06 | 1.8163e-05 | 1.9404e-05 | 0.00086163 | 0.0025125 | 0.0033122 | 0.0030359 | 0.0027173 | 0.0027422 | 0.0032127 | 0.003918 | 0.0041389 | 0.0041425 | 0.0041445 | 0.0041468 | 0.0041529 | 0.004158 | 0.004163 | 0.0041686 | 0.0041726 | 0.0051664 | 0.0051914 | 0.0052193 | 0.0055394 | 0.0055224 | 0.0055351 | 0.0061083 | 0.0074572 | 0.0074656 | 0.0074555 | 0.007471 | 0.0074769
TAS | TAS | 0 | 0 | 0 | 0 | 0 | 0 | 0.00010357 | 0.00044538 | 0.00094615 | 0.0012687 | 0.0018712 | 0.0018842 | 0.0020162 | 0.0020901 | 0.0020901 | 0.0038278 | 0.0038279 | 0.0038464 | 0.003847 | 0.0039342 | 0.0039566 | 0.0040445 | 0.0040703 | 0.0040703 | 0.0040703 | 0.0040703 | 0.0040703 | 0.0040703 | 0.0040703 | 0.0040703 | 0.0040703 | 0.0040703
VIC | VIC | 1.237e-05 | 0.00016949 | 0.00080847 | 0.0013024 | 0.0013024 | 0.0013024 | 0.012232 | 0.033872 | 0.051092 | 0.077357 | 0.13792 | 0.13861 | 0.1419 | 0.14272 | 0.14272 | 0.14557 | 0.14649 | 0.14731 | 0.14731 | 0.14763 | 0.14905 | 0.15009 | 0.15089 | 0.15185 | 0.15185 | 0.15383 | 0.15383 | 0.17015 | 0.17015 | 0.17015 | 0.17147 | 0.17158
NEM domestic |  | 9.287e-05 | 0.0010931 | 0.003765 | 0.014174 | 0.032806 | 0.049002 | 0.083044 | 0.14152 | 0.16025 | 0.20203 | 0.28389 | 0.30693 | 0.3192 | 0.32111 | 0.32213 | 0.32778 | 0.33035 | 0.33293 | 0.33373 | 0.33577 | 0.34454 | 0.34732 | 0.34958 | 0.35384 | 0.355 | 0.40592 | 0.45765 | 0.52891 | 0.52897 | 0.55542 | 0.55929 | 0.56307
Step Change
Region | ISP Subregion | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | SNSW | 0 | 0.00014777 | 0.00061873 | 0.0014688 | 0.0028154 | 0.0050277 | 0.0083086 | 0.01311 | 0.013234 | 0.013215 | 0.013345 | 0.018131 | 0.021449 | 0.023893 | 0.026353 | 0.028982 | 0.031907 | 0.034515 | 0.037123 | 0.041862 | 0.044688 | 0.047364 | 0.05243 | 0.053329 | 0.055668 | 0.058798 | 0.066625 | 0.066637 | 0.066646 | 0.066653 | 0.081831 | 0.0935
NSW | SNW | 0 | 0.00048738 | 0.0019218 | 0.004812 | 0.0097463 | 0.017555 | 0.029306 | 0.043347 | 0.043223 | 0.043243 | 0.043112 | 0.0587 | 0.069277 | 0.077023 | 0.084849 | 0.093154 | 0.10237 | 0.11052 | 0.11864 | 0.13356 | 0.14156 | 0.14982 | 0.16559 | 0.16817 | 0.17538 | 0.1851 | 0.20963 | 0.20961 | 0.20961 | 0.2096 | 0.25734 | 0.29403
QLD | CQ | 1.1471e-05 | 0.00011692 | 0.00023561 | 0.0002354 | 0.00023509 | 0.00023468 | 0.0052042 | 0.022456 | 0.040152 | 0.057125 | 0.082731 | 0.082491 | 0.10072 | 0.1107 | 0.12102 | 0.13098 | 0.13774 | 0.16069 | 0.1696 | 0.18228 | 0.19262 | 0.20338 | 0.21165 | 0.22138 | 0.23121 | 0.23804 | 0.24999 | 0.2591 | 0.26488 | 0.2762 | 0.31828 | 0.3802
QLD | SQ | 7.3385e-06 | 4.0707e-05 | 4.2023e-05 | 4.2229e-05 | 4.2538e-05 | 4.2949e-05 | 0.00097048 | 0.004242 | 0.0077338 | 0.011905 | 0.018748 | 0.036405 | 0.05329 | 0.058655 | 0.064183 | 0.069508 | 0.073147 | 0.085381 | 0.090277 | 0.09709 | 0.10254 | 0.10838 | 0.11289 | 0.11819 | 0.12354 | 0.12729 | 0.13378 | 0.13876 | 0.14196 | 0.14812 | 0.13703 | 0.16369
SA | CSA | 5.3787e-05 | 0.00011449 | 0.00012245 | 0.0057777 | 0.01723 | 0.022962 | 0.023171 | 0.023151 | 0.023125 | 0.021869 | 0.021722 | 0.02173 | 0.021735 | 0.021739 | 0.021782 | 0.02613 | 0.028034 | 0.030044 | 0.031498 | 0.034055 | 0.036775 | 0.038557 | 0.041662 | 0.041687 | 0.041708 | 0.042395 | 0.051056 | 0.051101 | 0.051132 | 0.051163 | 0.068411 | 0.071731
SA | SESA | 7.9032e-06 | 1.6364e-05 | 1.586e-05 | 0.0005359 | 0.0014337 | 0.0018773 | 0.0016683 | 0.001688 | 0.0017145 | 0.0029706 | 0.0031169 | 0.0031087 | 0.0031044 | 0.0031001 | 0.0031034 | 0.0037169 | 0.00398 | 0.0042562 | 0.0044526 | 0.0048184 | 0.0052087 | 0.0054619 | 0.005891 | 0.0058657 | 0.0058452 | 0.0059377 | 0.007117 | 0.0070715 | 0.0070405 | 0.0070096 | 0.0093445 | 0.0097981
TAS | TAS | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027225 | 0.0063301 | 0.010823 | 0.016099 | 0.024458 | 0.025681 | 0.027538 | 0.02805 | 0.028274 | 0.029419 | 0.030433 | 0.030892 | 0.031519 | 0.032618 | 0.033099 | 0.03356 | 0.034616 | 0.034616 | 0.034808 | 0.035577 | 0.036316 | 0.036506 | 0.036506 | 0.036506 | 0.036917 | 0.037907
VIC | VIC | 1.237e-05 | 0.00016949 | 0.00080847 | 0.0013024 | 0.0013024 | 0.0013024 | 0.0024397 | 0.0062368 | 0.013671 | 0.042354 | 0.1009 | 0.10967 | 0.12389 | 0.12998 | 0.1366 | 0.14573 | 0.15572 | 0.16357 | 0.16936 | 0.18207 | 0.18886 | 0.19595 | 0.21727 | 0.22153 | 0.22153 | 0.2274 | 0.23663 | 0.24357 | 0.24365 | 0.24588 | 0.25327 | 0.27138
NEM domestic |  | 9.287e-05 | 0.0010931 | 0.003765 | 0.014174 | 0.032806 | 0.049002 | 0.073791 | 0.12056 | 0.15368 | 0.20878 | 0.30814 | 0.35592 | 0.421 | 0.45314 | 0.48616 | 0.52763 | 0.56333 | 0.61987 | 0.65247 | 0.70836 | 0.74535 | 0.78247 | 0.84201 | 0.86476 | 0.88968 | 0.92054 | 0.99113 | 1.0124 | 1.0214 | 1.0411 | 1.1624 | 1.3222
Green Energy Exports
Region | ISP Subregion | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | SNSW | 0 | 0.00015113 | 0.0005789 | 0.0012599 | 0.0023942 | 0.0041192 | 0.0065942 | 0.0098182 | 0.013487 | 0.02187 | 0.032684 | 0.038018 | 0.042921 | 0.04823 | 0.054624 | 0.060434 | 0.066274 | 0.068154 | 0.073294 | 0.077787 | 0.086583 | 0.089135 | 0.093356 | 0.098174 | 0.10232 | 0.10444 | 0.10562 | 0.10593 | 0.1077 | 0.10769 | 0.11092 | 0.11252
NSW | SNW | 0 | 0.00048401 | 0.0019617 | 0.0050209 | 0.010168 | 0.018464 | 0.03102 | 0.046639 | 0.062544 | 0.099656 | 0.14711 | 0.16907 | 0.1879 | 0.20965 | 0.23626 | 0.26057 | 0.28233 | 0.28614 | 0.30664 | 0.32806 | 0.3633 | 0.36892 | 0.39069 | 0.41604 | 0.43387 | 0.4413 | 0.44604 | 0.44662 | 0.45228 | 0.45967 | 0.47912 | 0.48601
QLD | CQ | 1.5824e-05 | 0.00010311 | 0.00017812 | 0.00019398 | 0.00020165 | 0.00017353 | 0.013323 | 0.025137 | 0.046075 | 0.072739 | 0.10369 | 0.11797 | 0.12133 | 0.13769 | 0.15587 | 0.1737 | 0.18754 | 0.20316 | 0.21998 | 0.2381 | 0.25742 | 0.27583 | 0.2895 | 0.30668 | 0.32569 | 0.33804 | 0.42975 | 0.44911 | 0.45354 | 0.46095 | 0.49081 | 0.51762
QLD | SQ | 2.9861e-06 | 5.4522e-05 | 9.9514e-05 | 8.3653e-05 | 7.5977e-05 | 0.0001041 | 0.011105 | 0.024066 | 0.043749 | 0.064367 | 0.087655 | 0.09212 | 0.091843 | 0.096935 | 0.098486 | 0.10503 | 0.11025 | 0.11621 | 0.1222 | 0.1283 | 0.13411 | 0.14257 | 0.14717 | 0.1499 | 0.15358 | 0.1594 | 0.20265 | 0.21178 | 0.21387 | 0.21736 | 0.21721 | 0.22908
SA | CSA | 5.2537e-05 | 0.00011485 | 0.00011944 | 0.0054282 | 0.016064 | 0.021434 | 0.021453 | 0.021664 | 0.021934 | 0.022007 | 0.032237 | 0.038256 | 0.042349 | 0.046559 | 0.053884 | 0.062102 | 0.063906 | 0.068699 | 0.073269 | 0.077798 | 0.082407 | 0.086928 | 0.091568 | 0.091646 | 0.091706 | 0.091795 | 0.091182 | 0.095172 | 0.096892 | 0.095661 | 0.096839 | 0.099474
SA | SESA | 9.1532e-06 | 1.5998e-05 | 1.8868e-05 | 0.00088539 | 0.0025994 | 0.0034055 | 0.0033863 | 0.0031753 | 0.0029052 | 0.0028322 | 0.0039443 | 0.0042773 | 0.0042563 | 0.0045712 | 0.0052143 | 0.0056975 | 0.0055004 | 0.0058485 | 0.0061768 | 0.0064747 | 0.0067774 | 0.0070506 | 0.0073148 | 0.0072367 | 0.0071774 | 0.0070882 | 0.0084708 | 0.0090715 | 0.008293 | 0.0095239 | 0.010477 | 0.010762
TAS | TAS | 0 | 0 | 0 | 0 | 0 | 0 | 0.00043379 | 0.00090445 | 0.0020039 | 0.0037703 | 0.0059866 | 0.0071524 | 0.0083226 | 0.0096437 | 0.01119 | 0.012944 | 0.014113 | 0.014993 | 0.016202 | 0.017278 | 0.018207 | 0.018988 | 0.020197 | 0.020506 | 0.020506 | 0.020506 | 0.020711 | 0.020711 | 0.020711 | 0.020711 | 0.020711 | 0.020711
VIC | VIC | 1.237e-05 | 0.00016949 | 0.00080847 | 0.0013024 | 0.0013024 | 0.0013024 | 0.0283 | 0.060369 | 0.10291 | 0.1537 | 0.21667 | 0.23847 | 0.25388 | 0.27596 | 0.29744 | 0.31934 | 0.31934 | 0.33472 | 0.35372 | 0.37257 | 0.39173 | 0.41158 | 0.43101 | 0.43819 | 0.44555 | 0.45296 | 0.46083 | 0.50065 | 0.50065 | 0.50065 | 0.57432 | 0.58017
NEM domestic |  | 9.287e-05 | 0.0010931 | 0.003765 | 0.014174 | 0.032806 | 0.049002 | 0.11562 | 0.19177 | 0.29561 | 0.44094 | 0.62998 | 0.70534 | 0.75281 | 0.82924 | 0.91297 | 0.99981 | 1.0492 | 1.0979 | 1.1715 | 1.2464 | 1.3405 | 1.401 | 1.4708 | 1.5284 | 1.5804 | 1.6155 | 1.7653 | 1.839 | 1.8539 | 1.8722 | 2.0004 | 2.0563
Electrification Alternatives Sensitivity
Region | ISP Subregion | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NSW | SNSW | 0 | 0.00014777 | 0.00061873 | 0.0014688 | 0.0028154 | 0.0050277 | 0.0083086 | 0.01311 | 0.013234 | 0.013215 | 0.013345 | 0.018131 | 0.021449 | 0.023893 | 0.026353 | 0.028982 | 0.031907 | 0.034515 | 0.037123 | 0.041862 | 0.044688 | 0.047364 | 0.05243 | 0.053329 | 0.055668 | 0.058798 | 0.066625 | 0.066637 | 0.066646 | 0.066653 | 0.081831 | 0.0935
NSW | SNW | 0 | 0.00048738 | 0.0019218 | 0.004812 | 0.0097463 | 0.017555 | 0.029306 | 0.043347 | 0.043223 | 0.043243 | 0.043112 | 0.0587 | 0.069277 | 0.077023 | 0.084849 | 0.093154 | 0.10237 | 0.11052 | 0.11864 | 0.13356 | 0.14156 | 0.14982 | 0.16559 | 0.16817 | 0.17538 | 0.1851 | 0.20963 | 0.20961 | 0.20961 | 0.2096 | 0.25734 | 0.29403
QLD | CQ | 1.1471e-05 | 0.00011692 | 0.00023561 | 0.0002354 | 0.00023509 | 0.00023468 | 0.0052042 | 0.022456 | 0.040152 | 0.057125 | 0.082731 | 0.082491 | 0.10072 | 0.1107 | 0.12102 | 0.13098 | 0.13774 | 0.16069 | 0.1696 | 0.18228 | 0.19262 | 0.20338 | 0.21165 | 0.22138 | 0.23121 | 0.23804 | 0.24999 | 0.2591 | 0.26488 | 0.2762 | 0.31828 | 0.3802
QLD | SQ | 7.3385e-06 | 4.0707e-05 | 4.2023e-05 | 4.2229e-05 | 4.2538e-05 | 4.2949e-05 | 0.00097048 | 0.004242 | 0.0077338 | 0.011905 | 0.018748 | 0.036405 | 0.05329 | 0.058655 | 0.064183 | 0.069508 | 0.073147 | 0.085381 | 0.090277 | 0.09709 | 0.10254 | 0.10838 | 0.11289 | 0.11819 | 0.12354 | 0.12729 | 0.13378 | 0.13876 | 0.14196 | 0.14812 | 0.13703 | 0.16369
SA | CSA | 5.3787e-05 | 0.00011449 | 0.00012245 | 0.0057777 | 0.01723 | 0.022962 | 0.023171 | 0.023151 | 0.023125 | 0.021869 | 0.021722 | 0.02173 | 0.021735 | 0.021739 | 0.021782 | 0.02613 | 0.028034 | 0.030044 | 0.031498 | 0.034055 | 0.036775 | 0.038557 | 0.041662 | 0.041687 | 0.041708 | 0.042395 | 0.051056 | 0.051101 | 0.051132 | 0.051163 | 0.068411 | 0.071731
SA | SESA | 7.9032e-06 | 1.6364e-05 | 1.586e-05 | 0.0005359 | 0.0014337 | 0.0018773 | 0.0016683 | 0.001688 | 0.0017145 | 0.0029706 | 0.0031169 | 0.0031087 | 0.0031044 | 0.0031001 | 0.0031034 | 0.0037169 | 0.00398 | 0.0042562 | 0.0044526 | 0.0048184 | 0.0052087 | 0.0054619 | 0.005891 | 0.0058657 | 0.0058452 | 0.0059377 | 0.007117 | 0.0070715 | 0.0070405 | 0.0070096 | 0.0093445 | 0.0097981
TAS | TAS | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027225 | 0.0063301 | 0.010823 | 0.016099 | 0.024458 | 0.025681 | 0.027538 | 0.02805 | 0.028274 | 0.029419 | 0.030433 | 0.030892 | 0.031519 | 0.032618 | 0.033099 | 0.03356 | 0.034616 | 0.034616 | 0.034808 | 0.035577 | 0.036316 | 0.036506 | 0.036506 | 0.036506 | 0.036917 | 0.037907
VIC | VIC | 1.237e-05 | 0.00016949 | 0.00080847 | 0.0013024 | 0.0013024 | 0.0013024 | 0.0024397 | 0.0062368 | 0.013671 | 0.042354 | 0.1009 | 0.10967 | 0.12389 | 0.12998 | 0.1366 | 0.14573 | 0.15572 | 0.16357 | 0.16936 | 0.18207 | 0.18886 | 0.19595 | 0.21727 | 0.22153 | 0.22153 | 0.2274 | 0.23663 | 0.24357 | 0.24365 | 0.24588 | 0.25327 | 0.27138
NEM domestic |  | 9.287e-05 | 0.0010931 | 0.003765 | 0.014174 | 0.032806 | 0.049002 | 0.073791 | 0.12056 | 0.15368 | 0.20878 | 0.30814 | 0.35592 | 0.421 | 0.45314 | 0.48616 | 0.52763 | 0.56333 | 0.61987 | 0.65247 | 0.70836 | 0.74535 | 0.78247 | 0.84201 | 0.86476 | 0.88968 | 0.92054 | 0.99113 | 1.0124 | 1.0214 | 1.0411 | 1.1624 | 1.3222

## Hydrogen demand_Export&Steel
Go to Assumptions Summary
Total hydrogen export from NEM electrolysers (Mt of H2)
Export hydrogen production is developed based on 2022 multi-sector model outcome (AusTIMES) conducted by CSIRO/ClimateWorks Centre.
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | Progressive Change | Orchestrated Step Change | Hydrogen Export
Progressive Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NEM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Step Change
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NEM | 0 | 0 | 0 | 0 | 0 | 0.0041086 | 0.016434 | 0.04314 | 0.065738 | 0.082165 | 0.09242 | 0.10271 | 0.10271 | 0.11299 | 0.12326 | 0.13352 | 0.13353 | 0.1474 | 0.15407 | 0.15407 | 0.16434 | 0.17462 | 0.17462 | 0.18489 | 0.19516 | 0.19516 | 0.20542 | 0.2157 | 0.22597 | 0.23625 | 0.24652 | 0.24652
Green Energy Exports
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NEM | 0 | 0 | 0 | 0 | 0 | 0.10226 | 0.24544 | 0.4602 | 0.68724 | 0.97151 | 1.0943 | 1.2272 | 1.3806 | 1.5545 | 1.7386 | 1.9635 | 2.209 | 2.4749 | 2.7919 | 3.1294 | 3.5283 | 3.968 | 4.4589 | 5.0111 | 5.635 | 6.3406 | 7.1281 | 8.0178 | 9.0098 | 10.1348 | 11.3927 | 12.8142
Additional hydrogen demand for green steel production (Mt of H2)
Hydrogen demand for green steel production is developed based on a multi-sector model outcome (AusTIMES) conducted by CSIRO/ClimateWorks Centre.
Green Energy Exports
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NEM | 0 | 0 | 0 | 0 | 0 | 0.047617 | 0.095343 | 0.28935 | 0.39762 | 0.51479 | 0.53393 | 0.55637 | 0.57677 | 0.60786 | 0.64599 | 0.7061 | 0.75578 | 0.83909 | 0.87457 | 0.91486 | 0.96101 | 1.0144 | 1.0769 | 1.1511 | 1.2406 | 1.2406 | 1.2406 | 1.2406 | 1.2406 | 1.2406 | 1.2406 | 1.2406
Electricity demand for green steel production (TWh)
This electricity demand is an additional inflexible load (for the purpose of arc furnaces) to the flexible electrolysers' load that are required for green steel production.
This load is estimated based on a multi-sector model outcome (AusTIMES) conducted by CSIRO/ClimateWorks Centre.
Green Energy Exports
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
NEM | 0 | 0 | 0 | 0 | 0 | 1.1571 | 2.3168 | 7.0311 | 9.6621 | 10.0834 | 10.5483 | 11.0937 | 11.5895 | 12.345 | 13.2714 | 14.7321 | 15.9395 | 17.9639 | 18.826 | 19.8051 | 20.9265 | 22.2243 | 23.7435 | 25.5466 | 27.7215 | 27.7215 | 27.7215 | 27.7215 | 27.7215 | 27.7215 | 27.7215 | 27.7215

## Hydrogen monthly profiles
Go to Assumptions Summary
NEM monthly hydrogen consumption profiles
These tables show the assumed monthly consumption profiles for domestic hydrogen usage across all sectors in the NEM
Residential and commercial sectors consumption profiles are assumed to be seasonal. Conversely industrial and transport sectors are assumed to be flat across the year.
Source: 2022 multi-sector model outcome (AusTIMES) conducted by CSIRO/ClimateWorks Centre and AEMO analysis
Consultant forecast mapping
| Progressive Change | Step Change | Green Energy Exports
Consultant's scenario name | Progressive Change | Step Change | Hydrogen Export
Progressive Change
NEM | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
January | 8.031% | 7.925% | 7.923% | 7.919% | 7.853% | 7.904% | 7.901% | 8.019% | 7.998% | 8.04% | 8.101% | 8.135% | 8.147% | 8.156% | 8.164% | 8.174% | 8.182% | 8.19% | 8.199% | 8.208% | 8.222% | 8.229% | 8.237% | 8.244% | 8.25% | 8.257% | 8.267% | 8.292% | 8.295% | 8.308% | 8.312% | 8.317%
February | 8.046% | 7.945% | 7.943% | 7.939% | 7.877% | 7.925% | 7.922% | 8.034% | 8.015% | 8.054% | 8.112% | 8.145% | 8.157% | 8.165% | 8.172% | 8.181% | 8.189% | 8.197% | 8.206% | 8.215% | 8.228% | 8.235% | 8.241% | 8.248% | 8.254% | 8.261% | 8.27% | 8.294% | 8.297% | 8.309% | 8.313% | 8.318%
March | 8.087% | 8.001% | 7.999% | 7.996% | 7.943% | 7.984% | 7.981% | 8.077% | 8.061% | 8.094% | 8.144% | 8.172% | 8.182% | 8.189% | 8.195% | 8.203% | 8.21% | 8.217% | 8.224% | 8.232% | 8.243% | 8.249% | 8.255% | 8.26% | 8.266% | 8.271% | 8.279% | 8.3% | 8.302% | 8.313% | 8.316% | 8.32%
April | 8.173% | 8.117% | 8.116% | 8.114% | 8.079% | 8.106% | 8.105% | 8.167% | 8.156% | 8.178% | 8.21% | 8.228% | 8.235% | 8.24% | 8.244% | 8.249% | 8.253% | 8.257% | 8.262% | 8.267% | 8.275% | 8.278% | 8.282% | 8.286% | 8.289% | 8.293% | 8.298% | 8.311% | 8.313% | 8.32% | 8.322% | 8.325%
May | 8.525% | 8.592% | 8.593% | 8.595% | 8.637% | 8.605% | 8.607% | 8.532% | 8.545% | 8.519% | 8.48% | 8.459% | 8.451% | 8.445% | 8.441% | 8.434% | 8.429% | 8.424% | 8.418% | 8.412% | 8.403% | 8.399% | 8.395% | 8.39% | 8.386% | 8.382% | 8.375% | 8.359% | 8.358% | 8.349% | 8.347% | 8.344%
June | 8.858% | 9.042% | 9.046% | 9.052% | 9.166% | 9.079% | 9.084% | 8.879% | 8.915% | 8.843% | 8.737% | 8.677% | 8.656% | 8.641% | 8.628% | 8.611% | 8.596% | 8.582% | 8.566% | 8.55% | 8.526% | 8.514% | 8.501% | 8.489% | 8.478% | 8.466% | 8.449% | 8.405% | 8.4% | 8.377% | 8.371% | 8.362%
July | 8.869% | 9.057% | 9.061% | 9.067% | 9.184% | 9.095% | 9.099% | 8.891% | 8.927% | 8.854% | 8.745% | 8.685% | 8.663% | 8.647% | 8.634% | 8.617% | 8.602% | 8.587% | 8.571% | 8.555% | 8.53% | 8.518% | 8.505% | 8.492% | 8.481% | 8.468% | 8.451% | 8.407% | 8.401% | 8.378% | 8.371% | 8.363%
August | 8.723% | 8.859% | 8.862% | 8.867% | 8.952% | 8.887% | 8.89% | 8.739% | 8.765% | 8.712% | 8.633% | 8.589% | 8.573% | 8.562% | 8.552% | 8.539% | 8.529% | 8.518% | 8.506% | 8.494% | 8.476% | 8.467% | 8.458% | 8.449% | 8.44% | 8.432% | 8.419% | 8.387% | 8.383% | 8.366% | 8.361% | 8.355%
September | 8.39% | 8.41% | 8.41% | 8.411% | 8.423% | 8.414% | 8.414% | 8.392% | 8.396% | 8.388% | 8.377% | 8.37% | 8.368% | 8.367% | 8.365% | 8.363% | 8.362% | 8.36% | 8.358% | 8.357% | 8.354% | 8.353% | 8.351% | 8.35% | 8.349% | 8.348% | 8.346% | 8.341% | 8.341% | 8.338% | 8.337% | 8.336%
October | 8.235% | 8.2% | 8.199% | 8.198% | 8.177% | 8.193% | 8.192% | 8.231% | 8.224% | 8.238% | 8.258% | 8.269% | 8.273% | 8.276% | 8.278% | 8.281% | 8.284% | 8.287% | 8.29% | 8.293% | 8.297% | 8.299% | 8.302% | 8.304% | 8.306% | 8.308% | 8.312% | 8.32% | 8.321% | 8.325% | 8.326% | 8.328%
November | 8.079% | 7.989% | 7.987% | 7.984% | 7.929% | 7.971% | 7.969% | 8.068% | 8.051% | 8.086% | 8.138% | 8.166% | 8.177% | 8.184% | 8.19% | 8.199% | 8.206% | 8.213% | 8.22% | 8.228% | 8.24% | 8.246% | 8.252% | 8.258% | 8.263% | 8.269% | 8.277% | 8.299% | 8.301% | 8.312% | 8.315% | 8.319%
December | 7.984% | 7.862% | 7.86% | 7.855% | 7.779% | 7.838% | 7.835% | 7.97% | 7.947% | 7.995% | 8.065% | 8.105% | 8.119% | 8.129% | 8.138% | 8.149% | 8.158% | 8.168% | 8.179% | 8.189% | 8.205% | 8.213% | 8.222% | 8.23% | 8.237% | 8.245% | 8.257% | 8.286% | 8.289% | 8.304% | 8.309% | 8.314%
Step Change
NEM | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
January | 8.017% | 7.97% | 7.748% | 7.521% | 7.467% | 7.496% | 7.492% | 7.921% | 8.022% | 8.09% | 8.157% | 8.196% | 8.224% | 8.244% | 8.254% | 8.264% | 8.273% | 8.284% | 8.291% | 8.298% | 8.304% | 8.308% | 8.313% | 8.317% | 8.32% | 8.323% | 8.324% | 8.326% | 8.326% | 8.327% | 8.328% | 8.328%
February | 8.032% | 7.988% | 7.777% | 7.561% | 7.509% | 7.537% | 7.533% | 7.942% | 8.037% | 8.102% | 8.166% | 8.202% | 8.229% | 8.248% | 8.258% | 8.267% | 8.276% | 8.286% | 8.293% | 8.3% | 8.305% | 8.309% | 8.314% | 8.317% | 8.32% | 8.323% | 8.325% | 8.326% | 8.326% | 8.327% | 8.328% | 8.329%
March | 8.075% | 8.037% | 7.857% | 7.672% | 7.628% | 7.651% | 7.648% | 7.998% | 8.08% | 8.135% | 8.19% | 8.221% | 8.244% | 8.26% | 8.269% | 8.277% | 8.285% | 8.293% | 8.299% | 8.305% | 8.309% | 8.313% | 8.317% | 8.32% | 8.322% | 8.325% | 8.326% | 8.327% | 8.327% | 8.328% | 8.329% | 8.329%
April | 8.166% | 8.141% | 8.024% | 7.903% | 7.875% | 7.89% | 7.888% | 8.115% | 8.169% | 8.205% | 8.24% | 8.261% | 8.275% | 8.286% | 8.291% | 8.296% | 8.302% | 8.307% | 8.311% | 8.315% | 8.318% | 8.32% | 8.323% | 8.325% | 8.326% | 8.328% | 8.329% | 8.329% | 8.329% | 8.33% | 8.33% | 8.331%
May | 8.534% | 8.563% | 8.704% | 8.847% | 8.882% | 8.863% | 8.866% | 8.594% | 8.53% | 8.487% | 8.445% | 8.42% | 8.403% | 8.39% | 8.384% | 8.377% | 8.371% | 8.365% | 8.36% | 8.356% | 8.352% | 8.349% | 8.346% | 8.344% | 8.342% | 8.34% | 8.339% | 8.338% | 8.338% | 8.338% | 8.337% | 8.336%
June | 8.883% | 8.964% | 9.35% | 9.744% | 9.838% | 9.787% | 9.794% | 9.048% | 8.874% | 8.756% | 8.64% | 8.572% | 8.523% | 8.489% | 8.471% | 8.454% | 8.437% | 8.42% | 8.407% | 8.394% | 8.385% | 8.377% | 8.368% | 8.362% | 8.357% | 8.352% | 8.349% | 8.347% | 8.346% | 8.345% | 8.343% | 8.342%
July | 8.895% | 8.978% | 9.371% | 9.773% | 9.869% | 9.817% | 9.824% | 9.063% | 8.885% | 8.765% | 8.646% | 8.577% | 8.527% | 8.492% | 8.474% | 8.457% | 8.439% | 8.421% | 8.409% | 8.396% | 8.386% | 8.378% | 8.369% | 8.363% | 8.358% | 8.352% | 8.349% | 8.347% | 8.346% | 8.345% | 8.344% | 8.342%
August | 8.742% | 8.802% | 9.088% | 9.381% | 9.45% | 9.413% | 9.418% | 8.864% | 8.735% | 8.647% | 8.561% | 8.511% | 8.474% | 8.449% | 8.436% | 8.423% | 8.41% | 8.397% | 8.388% | 8.379% | 8.372% | 8.366% | 8.359% | 8.355% | 8.351% | 8.347% | 8.345% | 8.343% | 8.343% | 8.342% | 8.341% | 8.34%
September | 8.393% | 8.401% | 8.443% | 8.486% | 8.496% | 8.49% | 8.491% | 8.41% | 8.392% | 8.379% | 8.366% | 8.359% | 8.354% | 8.35% | 8.348% | 8.346% | 8.345% | 8.343% | 8.341% | 8.34% | 8.339% | 8.338% | 8.337% | 8.336% | 8.336% | 8.335% | 8.335% | 8.335% | 8.335% | 8.335% | 8.334% | 8.334%
October | 8.23% | 8.215% | 8.142% | 8.068% | 8.051% | 8.06% | 8.059% | 8.199% | 8.232% | 8.254% | 8.276% | 8.288% | 8.298% | 8.304% | 8.307% | 8.311% | 8.314% | 8.317% | 8.319% | 8.322% | 8.324% | 8.325% | 8.327% | 8.328% | 8.329% | 8.33% | 8.33% | 8.331% | 8.331% | 8.331% | 8.331% | 8.332%
November | 8.066% | 8.027% | 7.84% | 7.649% | 7.603% | 7.628% | 7.624% | 7.986% | 8.071% | 8.128% | 8.185% | 8.217% | 8.241% | 8.258% | 8.266% | 8.275% | 8.283% | 8.291% | 8.297% | 8.304% | 8.308% | 8.312% | 8.316% | 8.319% | 8.322% | 8.324% | 8.326% | 8.327% | 8.327% | 8.328% | 8.328% | 8.329%
December | 7.968% | 7.914% | 7.658% | 7.396% | 7.333% | 7.367% | 7.362% | 7.858% | 7.974% | 8.052% | 8.13% | 8.175% | 8.207% | 8.23% | 8.242% | 8.253% | 8.264% | 8.276% | 8.284% | 8.293% | 8.299% | 8.304% | 8.31% | 8.314% | 8.317% | 8.321% | 8.323% | 8.324% | 8.325% | 8.325% | 8.327% | 8.328%
Green Energy Exports
NEM | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
January | 8.333% | 8.333% | 8.178% | 8.177% | 8.179% | 8.247% | 8.244% | 8.267% | 8.204% | 8.148% | 8.106% | 8.085% | 8.06% | 8.056% | 8.063% | 8.046% | 8.03% | 8.038% | 8.045% | 8.051% | 8.056% | 8.053% | 8.054% | 8.062% | 8.068% | 8.065% | 8.054% | 8.03% | 8.017% | 8.018% | 8.019% | 8.005%
February | 8.333% | 8.333% | 8.186% | 8.185% | 8.187% | 8.251% | 8.248% | 8.271% | 8.211% | 8.157% | 8.117% | 8.098% | 8.074% | 8.07% | 8.076% | 8.06% | 8.045% | 8.052% | 8.059% | 8.065% | 8.07% | 8.067% | 8.068% | 8.075% | 8.081% | 8.078% | 8.068% | 8.045% | 8.032% | 8.033% | 8.034% | 8.021%
March | 8.333% | 8.333% | 8.207% | 8.206% | 8.208% | 8.263% | 8.261% | 8.28% | 8.228% | 8.182% | 8.148% | 8.131% | 8.111% | 8.108% | 8.113% | 8.1% | 8.087% | 8.093% | 8.098% | 8.103% | 8.108% | 8.105% | 8.106% | 8.112% | 8.117% | 8.115% | 8.106% | 8.086% | 8.076% | 8.076% | 8.077% | 8.066%
April | 8.333% | 8.333% | 8.251% | 8.251% | 8.252% | 8.288% | 8.286% | 8.298% | 8.265% | 8.235% | 8.213% | 8.202% | 8.189% | 8.187% | 8.19% | 8.181% | 8.173% | 8.177% | 8.181% | 8.184% | 8.187% | 8.185% | 8.186% | 8.19% | 8.193% | 8.191% | 8.185% | 8.173% | 8.166% | 8.166% | 8.167% | 8.16%
May | 8.333% | 8.333% | 8.432% | 8.432% | 8.431% | 8.388% | 8.39% | 8.375% | 8.415% | 8.451% | 8.477% | 8.49% | 8.506% | 8.509% | 8.505% | 8.515% | 8.525% | 8.52% | 8.516% | 8.512% | 8.509% | 8.511% | 8.51% | 8.505% | 8.501% | 8.503% | 8.51% | 8.525% | 8.534% | 8.533% | 8.533% | 8.541%
June | 8.333% | 8.333% | 8.603% | 8.604% | 8.601% | 8.483% | 8.488% | 8.448% | 8.557% | 8.656% | 8.727% | 8.764% | 8.808% | 8.814% | 8.803% | 8.832% | 8.859% | 8.846% | 8.835% | 8.824% | 8.814% | 8.82% | 8.817% | 8.805% | 8.794% | 8.799% | 8.818% | 8.86% | 8.883% | 8.881% | 8.88% | 8.903%
July | 8.333% | 8.333% | 8.609% | 8.61% | 8.606% | 8.486% | 8.492% | 8.45% | 8.562% | 8.662% | 8.736% | 8.773% | 8.818% | 8.824% | 8.813% | 8.842% | 8.87% | 8.857% | 8.845% | 8.834% | 8.825% | 8.83% | 8.827% | 8.815% | 8.804% | 8.809% | 8.829% | 8.871% | 8.894% | 8.892% | 8.891% | 8.915%
August | 8.333% | 8.333% | 8.534% | 8.534% | 8.532% | 8.445% | 8.448% | 8.418% | 8.5% | 8.573% | 8.626% | 8.653% | 8.686% | 8.69% | 8.682% | 8.703% | 8.724% | 8.714% | 8.705% | 8.697% | 8.691% | 8.694% | 8.693% | 8.684% | 8.676% | 8.679% | 8.694% | 8.724% | 8.741% | 8.74% | 8.739% | 8.757%
September | 8.333% | 8.333% | 8.362% | 8.363% | 8.362% | 8.35% | 8.35% | 8.346% | 8.358% | 8.368% | 8.376% | 8.38% | 8.385% | 8.385% | 8.384% | 8.387% | 8.39% | 8.389% | 8.387% | 8.386% | 8.385% | 8.386% | 8.386% | 8.384% | 8.383% | 8.384% | 8.386% | 8.39% | 8.393% | 8.392% | 8.392% | 8.395%
October | 8.333% | 8.333% | 8.283% | 8.282% | 8.283% | 8.305% | 8.304% | 8.312% | 8.291% | 8.273% | 8.259% | 8.252% | 8.244% | 8.243% | 8.245% | 8.24% | 8.235% | 8.237% | 8.239% | 8.241% | 8.243% | 8.242% | 8.242% | 8.245% | 8.247% | 8.246% | 8.242% | 8.234% | 8.23% | 8.23% | 8.231% | 8.226%
November | 8.333% | 8.333% | 8.202% | 8.202% | 8.204% | 8.261% | 8.258% | 8.278% | 8.225% | 8.177% | 8.142% | 8.124% | 8.103% | 8.1% | 8.105% | 8.091% | 8.078% | 8.084% | 8.09% | 8.095% | 8.1% | 8.097% | 8.098% | 8.104% | 8.11% | 8.107% | 8.098% | 8.078% | 8.067% | 8.068% | 8.068% | 8.057%
December | 8.333% | 8.333% | 8.154% | 8.153% | 8.156% | 8.234% | 8.23% | 8.257% | 8.184% | 8.119% | 8.071% | 8.047% | 8.018% | 8.014% | 8.021% | 8.002% | 7.984% | 7.992% | 8% | 8.007% | 8.013% | 8.01% | 8.012% | 8.02% | 8.027% | 8.024% | 8.011% | 7.983% | 7.968% | 7.969% | 7.97% | 7.954%

## Hydrogen export ports
Go to Assumptions Summary
These assumptions are applicable to all scenarios except Progressive Change.
Export Ports |  | Candidate hydrogen export ports and REZs
Hydrogen export ports were selected from 30 hydrogen hubs identified in Arup's 2019 report. (ARUP, 2019, 'Australian Hydrogen Hubs Study')
An additional candidate port was added at Mackay in Queensland, to align with the recent Queensland Government report into hydrogen export opportunities and provide sufficient granularity across the state to reflect the ISP model sub-regions. (Queensland Govt, Oct 2022, ‘Enabling Queensland’s hydrogen production and export opportunities’.)
The ten candidate ports used in the ISP model are illustrated in the figure and table below.
NEM Region | Potential port location
New South Wales | Newcastle, Port Kembla
Queensland | Gladstone, Townsville, Mackay
South Australia | Port Bonython, Cape Hardy/Port Spencer
Tasmania | Bell Bay
Victoria | Geelong, Portland
Distances from REZs to the ports for and costs for scenarios with hydrogen exports are shown in the 'Build limits' tab, columns S and T.
Note: This map shows the proposed North East Tasmania boundary change by the Federal Government.

## Other hydrogen assumptions
Go to Assumptions Summary
Hydrogen heat content (GJ/t)
To convert to or from GJ to tonnes (the two commonly used mesaures of hydrogen)
GJ/t
Hydrogen heat content | 142
Electrolysers electricity consumption rate (kWh/kg H2)
Sourced from CSIRO, Multisector Modelling 2022 input assumptions
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Proton Exchange Membrane (PEM) | 63.8089 | 62.3861 | 60.995 | 59.635 | 58.3052 | 57.0052 | 55.7341 | 54.4913 | 53.2763 | 52.0883 | 50.9269 | 49.7913 | 48.6811 | 47.5956 | 46.5343 | 45.4967 | 44.4822 | 43.4903 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43
Electricity consumption rate adjustments to include conversion to ammonia (kWh/kg H2)
Conversion to ammonia is only assumed for export purposes. This is in addition to the hydrogen electricity demand identified in the Hydrogen demand sheets.
| 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52 | 2052-53 | 2053-54
Inflexible load additional to the PEM consumption above | 6.9444 | 6.8926 | 6.8411 | 6.7901 | 6.7394 | 6.6891 | 6.6391 | 6.5895 | 6.5404 | 6.4915 | 6.4431 | 6.395 | 6.3472 | 6.2998 | 6.2528 | 6.2061 | 6.1598 | 6.1138 | 6.0681 | 6.0228 | 5.9779 | 5.9332 | 5.8889 | 5.845 | 5.8013 | 5.758 | 5.715 | 5.6724 | 5.63 | 5.588 | 5.5463 | 5.5049
Adopted from Aurecon 2022 Costs and Technical Parameter Review
Electrolysers baseload (%)
Baseload consumption from Kopp et el. (2017) and stakeholders feedback. This is in addition to the hydrogen electricity demand identified in the Hydrogen demand sheets.
% of capacity
% of total electrolysers capacity in MW - Domestic applications | 2022-23: 4.5%
% of total electrolysers capacity in MW - Export applications | bar: 2022-23
PEM Electrolyser technical parameters
Sourced from Aurecon 2022 Costs and Technical Parameter Review
Technology | 2022-23: Lead time for development (years)1; 2023-24: Lead time (years)2; 2024-25: Construction time (years)3; 2025-26: Total lead time (years); 2026-27: Economic Life (years)4; 2027-28: Technical Life (years)5
Proton Exchange Membrane (PEM) | 2022-23: 2; 2023-24: 2; 2024-25: 0.5; 2025-26: 5; 2026-27: 10; 2027-28: 25
Notes:
1. Aurecon has assumed that lead time for development is the time to undertake feasibility studies, procurement and contract negotiations, obtain permits and approvals, secure land agreements, fuel supply and obtain financing.
2. Aurecon has assumed lead time as the time from issue of Notice to Proceed (NTP) to the EPC contractor up to the delivery of all major equipment to site.
3. Aurecon has provided some components of lead time in weeks or fractions of years. AEMO has rounded the total lead time to the nearest whole number of years for capacity planning.
4. Period of time required for the project to recover build costs.
5. Period of time the project is operational before life extension refurbishment or retirement.
6. Electrolysers Variable O&M costs are assumed to be included in the Fixed O&M costs as per Aurecon's report.

## Summary Mapping
Go to Assumptions Summary
Summary Mapping
Existing generator | Technology type | Region | Sub-region | REZ location | Status | Regional build cost zone | Fuel type | Fuel cost mapping | Summer rating (MW) | Winter rating (MW) | Forced outage rate |  |  |  | Mean time to repair |  |  |  | Maintenance duration (%) | Minimum load (MW) | Maximum capacity factor (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate | MLF | Auxiliary load (%) | Connection cost |  | Build limit |  | Total lead time
[11 empty] | Full outage (% of time) |  | Partial outage (% of time) |  | Full outage |  | Partial outage
[11 empty] | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | [8 empty] | Technology | Region | Technology | Region
Bayswater | Steam Sub Critical | NSW | CNSW | N/A | Existing | N/A | Black Coal | Bayswater | Bayswater | Bayswater | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal | BW01 | NSW Coal | Bayswater | Bayswater | Bayswater | Bayswater | Black Coal NSW
Eraring | Steam Sub Critical | NSW | SNW | N/A | Existing | N/A | Black Coal | Eraring | Eraring | Eraring | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal | ER01 | NSW Coal | Eraring | Eraring | Eraring | Eraring | Black Coal NSW
Mt Piper | Steam Sub Critical | NSW | CNSW | N/A | Existing | N/A | Black Coal | Mt Piper | Mt Piper | Mt Piper | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal | MP1 | NSW Coal | Mt Piper | Mt Piper | Mt Piper | Mt Piper | Black Coal NSW
Vales Point B | Steam Sub Critical | NSW | SNW | N/A | Existing | N/A | Black Coal | Vales Point B | Vales Point B | Vales Point B | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal NSW | Black Coal | VP5 | NSW Coal | Vales Point B | Vales Point B | Vales Point B | Vales Point B | Black Coal NSW
Callide B | Steam Sub Critical | QLD | CQ | N/A | Existing | N/A | Black Coal | Callide B | Callide B | Callide B | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal | CALL_B_1 |  | Callide B | Callide B | Callide B | Callide B | Black Coal QLD
Callide C | Steam Super Critical | QLD | CQ | N/A | Existing | N/A | Black Coal | Callide C | Callide C | Callide C | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal | CPP_3 |  | Callide C | Callide C | Callide C | Callide C | Black Coal QLD
Gladstone | Steam Sub Critical | QLD | GG | N/A | Existing | N/A | Black Coal | Gladstone | Gladstone | Gladstone | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal | GSTONE1 |  | Gladstone | Gladstone | Gladstone | Gladstone | Black Coal QLD
Kogan Creek | Steam Super Critical | QLD | SQ | N/A | Existing | N/A | Black Coal | Kogan Creek | Kogan Creek | Kogan Creek | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal | KPP_1 |  | Kogan Creek | Kogan Creek | Kogan Creek | Kogan Creek | Black Coal QLD
Millmerran | Steam Super Critical | QLD | SQ | N/A | Existing | N/A | Black Coal | Millmerran | Millmerran | Millmerran | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal | MPP_1 |  | Millmerran | Millmerran | Millmerran | Millmerran | Black Coal QLD
Stanwell | Steam Sub Critical | QLD | CQ | N/A | Existing | N/A | Black Coal | Stanwell | Stanwell | Stanwell | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal | STAN-1 |  | Stanwell | Stanwell | Stanwell | Stanwell | Black Coal QLD
Tarong | Steam Sub Critical | QLD | SQ | N/A | Existing | N/A | Black Coal | Tarong | Tarong | Tarong | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal | TARONG#1 |  | Tarong | Tarong | Tarong | Tarong | Black Coal QLD
Tarong North | Steam Super Critical | QLD | SQ | N/A | Existing | N/A | Black Coal | Tarong North | Tarong North | Tarong North | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal QLD | Black Coal | TNPS1 |  | Tarong North | Tarong North | Tarong North | Tarong North | Black Coal QLD
Loy Yang A Power Station | Steam Sub Critical | VIC | VIC | N/A | Existing | N/A | Brown Coal | Loy Yang A | Loy Yang A Power Station | Loy Yang A Power Station | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | LYA1 |  | Loy Yang A Power Station | Loy Yang A Power Station | Loy Yang A Power Station | Loy Yang A Power Station | Brown Coal VIC
Loy Yang B | Steam Sub Critical | VIC | VIC | N/A | Existing | N/A | Brown Coal | Loy Yang B | Loy Yang B | Loy Yang B | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | LOYYB1 |  | Loy Yang B | Loy Yang B | Loy Yang B | Loy Yang B | Brown Coal VIC
Yallourn W | Steam Sub Critical | VIC | VIC | N/A | Existing | N/A | Brown Coal | Yallourn W | Yallourn W | Yallourn W | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | Brown Coal | YWPS1 |  | Yallourn W | Yallourn W | Yallourn W | Yallourn W | Brown Coal VIC
Tallawarra | CCGT | NSW | SNW | N/A | Existing | N/A | Gas | Tallawarra | Tallawarra | Tallawarra | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | CCGT |  |  | Tallawarra | Tallawarra | Tallawarra | Tallawarra | CCGT
Condamine A | CCGT | QLD | SQ | N/A | Existing | N/A | Gas | Condamine A | Condamine A | Condamine A | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | CCGT |  |  | Condamine A | Condamine A | Condamine A | Condamine A | CCGT
Darling Downs | CCGT | QLD | SQ | N/A | Existing | N/A | Gas | Darling Downs | Darling Downs | Darling Downs | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | CCGT |  |  | Darling Downs | Darling Downs | Darling Downs | Darling Downs | CCGT
Swanbank E GT | CCGT | QLD | SQ | N/A | Existing | N/A | Gas | Swanbank E GT | Swanbank E GT | Swanbank E GT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | CCGT |  |  | Swanbank E GT | Swanbank E GT | Swanbank E GT | Swanbank E GT | CCGT
Townsville Power Station | CCGT | QLD | NQ | N/A | Existing | N/A | Gas | Townsville Power Station | Townsville Power Station | Townsville Power Station | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | CCGT |  |  | Townsville Power Station | Townsville Power Station | Townsville Power Station | Townsville Power Station | CCGT
Yarwun Cogen | CCGT | QLD | GG | N/A | Existing | N/A | Gas | Yarwun Cogen | Yarwun Cogen | Yarwun Cogen | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | CCGT |  |  | Yarwun Cogen | Yarwun Cogen | Yarwun Cogen | Yarwun Cogen | CCGT
Osborne | CCGT | SA | CSA | N/A | Existing | N/A | Gas | Osborne | Osborne | Osborne | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | CCGT |  |  | Osborne | Osborne | Osborne | Osborne | CCGT
Pelican Point | CCGT | SA | CSA | N/A | Existing | N/A | Gas | Pelican Point | Pelican Point | Pelican Point | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | CCGT |  |  | Pelican Point | Pelican Point | Pelican Point | Pelican Point | CCGT
Tamar Valley Combined Cycle | CCGT | TAS | TAS | N/A | Existing | N/A | Gas | Tamar Valley Combined Cycle | Tamar Valley Combined Cycle | Tamar Valley Combined Cycle | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | CCGT |  |  | Tamar Valley Combined Cycle | Tamar Valley Combined Cycle | Tamar Valley Combined Cycle | Tamar Valley Combined Cycle | CCGT
Colongra | OCGT | NSW | SNW | N/A | Existing | N/A | Gas | Colongra | Colongra | Colongra | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Colongra | Colongra | Colongra | Colongra | OCGT
Smithfield Energy Facility | OCGT | NSW | SNW | N/A | Existing | N/A | Gas | Smithfield Energy Facility | Smithfield Energy Facility | Smithfield Energy Facility | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Smithfield Energy Facility | Smithfield Energy Facility | Smithfield Energy Facility3 | Smithfield Energy Facility | OCGT
Uranquinty | OCGT | NSW | SNSW | N/A | Existing | N/A | Gas | Uranquinty | Uranquinty | Uranquinty | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Uranquinty | Uranquinty | Uranquinty | Uranquinty | OCGT
Barcaldine Power Station | OCGT | QLD | CQ | N/A | Existing | N/A | Gas | Barcaldine Power Station | Barcaldine Power Station | Barcaldine Power Station | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Barcaldine Power Station | Barcaldine Power Station | Barcaldine Power Station | Barcaldine Power Station | OCGT
Braemar | OCGT | QLD | SQ | N/A | Existing | N/A | Gas | Braemar | Braemar | Braemar | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Braemar | Braemar | Braemar | Braemar | OCGT
Braemar 2 Power Station | OCGT | QLD | SQ | N/A | Existing | N/A | Gas | Braemar 2 Power Station | Braemar 2 Power Station | Braemar 2 Power Station | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Braemar 2 Power Station | Braemar 2 Power Station | Braemar 2 Power Station | Braemar 2 Power Station | OCGT
Mt Stuart | OCGT | QLD | NQ | N/A | Existing | N/A | Liquid Fuel | Liquid Fuel | Mt Stuart | Mt Stuart | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Mt Stuart | Mt Stuart | Mt Stuart | Mt Stuart | Liquid Fuel
Oakey Power Station | OCGT | QLD | SQ | N/A | Existing | N/A | Gas | Oakey Power Station | Oakey Power Station | Oakey Power Station | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Oakey Power Station | Oakey Power Station | Oakey Power Station | Oakey Power Station | OCGT
Roma | OCGT | QLD | SQ | N/A | Existing | N/A | Gas | Roma | Roma | Roma | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Roma | Roma | Roma | Roma | OCGT
Bolivar Power Station | OCGT | SA | CSA | N/A | Existing | N/A | Gas | Bolivar Power Station | Bolivar Power Station | Bolivar Power Station | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Bolivar Power Station | Bolivar Power Station | Bolivar Power Station1 | Bolivar Power Station | OCGT
Dry Creek GT | OCGT | SA | CSA | N/A | Existing | N/A | Gas | Dry Creek GT | Dry Creek GT | Dry Creek GT | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Dry Creek GT | Dry Creek GT | Dry Creek GT | Dry Creek GT | OCGT
Hallett GT | OCGT | SA | CSA | N/A | Existing | N/A | Gas | Hallett GT | Hallett GT | Hallett GT | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Hallett GT | Hallett GT | Hallett GT | Hallett GT | OCGT
Ladbroke Grove | OCGT | SA | SESA | N/A | Existing | N/A | Gas | Ladbroke Grove | Ladbroke Grove | Ladbroke Grove | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Ladbroke Grove | Ladbroke Grove | Ladbroke Grove | Ladbroke Grove | OCGT
Mintaro GT | OCGT | SA | CSA | N/A | Existing | N/A | Gas | Mintaro GT | Mintaro GT | Mintaro GT | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Mintaro GT | Mintaro GT | Mintaro GT | Mintaro GT | OCGT
Port Lincoln GT | OCGT | SA | CSA | N/A | Existing | N/A | Liquid Fuel | Liquid Fuel | Port Lincoln Gt | Port Lincoln Gt | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Port Lincoln GT | Port Lincoln GT | Port Lincoln GT | Port Lincoln GT | Liquid Fuel
Quarantine | OCGT | SA | CSA | N/A | Existing | N/A | Gas | Quarantine | Quarantine | Quarantine | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Quarantine | Quarantine | Quarantine | Quarantine | OCGT
Snapper Point Power Station | OCGT | SA | CSA | N/A | Existing | N/A | Gas | SA new OCGT | Snapper Point Power Station | Snapper Point Power Station | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Snapper Point Power Station | Snapper Point Power Station | Snapper Point Power Station1 | Snapper Point Power Station | OCGT
Snuggery | OCGT | SA | SESA | N/A | Existing | N/A | Liquid Fuel | Liquid Fuel | Snuggery | Snuggery | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Snuggery | Snuggery | Snuggery | Snuggery | Liquid Fuel
Bell Bay Three | OCGT | TAS | TAS | N/A | Existing | N/A | Gas | Bell Bay Three | Bell Bay Three | Bell Bay Three | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Bell Bay Three | Bell Bay Three | Bell Bay Three | Bell Bay Three | OCGT
Tamar Valley Peaking | OCGT | TAS | TAS | N/A | Existing | N/A | Gas | Tamar Valley Peaking | Tamar Valley Peaking | Tamar Valley Peaking | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Tamar Valley Peaking | Tamar Valley Peaking | Tamar Valley Peaking | Tamar Valley Peaking | OCGT
Bairnsdale | OCGT | VIC | VIC | N/A | Existing | N/A | Gas | Bairnsdale | Bairnsdale | Bairnsdale | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Bairnsdale | Bairnsdale | Bairnsdale | Bairnsdale | OCGT
Jeeralang A | OCGT | VIC | VIC | N/A | Existing | N/A | Gas | Jeeralang A | Jeeralang A | Jeeralang A | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Jeeralang A | Jeeralang A | Jeeralang A | Jeeralang A | OCGT
Jeeralang B | OCGT | VIC | VIC | N/A | Existing | N/A | Gas | Jeeralang B | Jeeralang B | Jeeralang B | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Jeeralang B | Jeeralang B | Jeeralang B | Jeeralang B | OCGT
Laverton North | OCGT | VIC | VIC | N/A | Existing | N/A | Gas | Laverton North | Laverton North | Laverton North | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Laverton North | Laverton North | Laverton North | Laverton North | OCGT
Mortlake | OCGT | VIC | VIC | N/A | Existing | N/A | Gas | Mortlake | Mortlake | Mortlake | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Mortlake | Mortlake | Mortlake | Mortlake | OCGT
Somerton | OCGT | VIC | VIC | N/A | Existing | N/A | Gas | Somerton | Somerton | Somerton | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Somerton | Somerton | Somerton | Somerton | OCGT
Valley Power | OCGT | VIC | VIC | N/A | Existing | N/A | Gas | Valley Power | Valley Power | Valley Power | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT |  |  | Valley Power | Valley Power | Valley Power | Valley Power | OCGT
Torrens Island B | Gas-powered steam turbine | SA | CSA | N/A | Existing | N/A | Gas | Torrens Island B | Torrens Island B | Torrens Island B | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Gas-powered steam turbine |  |  | Torrens Island B | Torrens Island B | Torrens Island B | Torrens Island B | Gas-powered steam turbine
Newport | Gas-powered steam turbine | VIC | VIC | N/A | Existing | N/A | Gas | Newport | Newport | Newport | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Steam Turbine & CCGT | Gas-powered steam turbine |  |  | Newport | Newport | Newport | Newport | Gas-powered steam turbine
Angaston | Reciprocating Engine | SA | CSA | N/A | Existing | N/A | Liquid Fuel | Liquid Fuel | Angaston | Angaston | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | Reciprocating Engine |  |  | Angaston | Angaston | Angaston | Angaston | Liquid Fuel
Barker Inlet Power Station | Reciprocating Engine | SA | CSA | N/A | Existing | N/A | Gas | Barker Inlet Power Station | Barker Inlet Power Station | Barker Inlet Power Station | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | Reciprocating Engine |  |  | Barker Inlet Power Station | Barker Inlet Power Station | Barker Inlet Power Station | Barker Inlet Power Station | OCGT
Lonsdale | Reciprocating Engine | SA | CSA | N/A | Existing | N/A | Liquid Fuel | Liquid Fuel | Lonsdale | Lonsdale | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | Reciprocating Engine |  |  | Lonsdale | Lonsdale | Lonsdale | Lonsdale | Liquid Fuel
Port Stanvac 1 | Reciprocating Engine | SA | CSA | N/A | Existing | N/A | Liquid Fuel | Liquid Fuel | Port Stanvac 1 | Port Stanvac 1 | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | OCGT Small | Reciprocating Engine |  |  | Port Stanvac 1 | Port Stanvac 1 | Port Stanvac 1 | Port Stanvac 1 | Liquid Fuel
Blowering | Hydro | NSW | SNSW | N/A | Existing | N/A | Water | Hydro | Blowering | Blowering | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Blowering | Hydro
Guthega | Hydro | NSW | SNSW | N/A | Existing | N/A | Water | Hydro | Guthega | Guthega | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Guthega | Hydro
Hume Dam NSW | Hydro | NSW | SNSW | N/A | Existing | N/A | Water | Hydro | Hume Dam NSW | Hume Dam NSW | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Hume Dam NSW | Hydro
Shoalhaven | Hydro | NSW | CNSW | N/A | Existing | N/A | Water | Hydro | Shoalhaven | Shoalhaven | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Shoalhaven | Hydro
Tumut 3 | Hydro | NSW | SNSW | N/A | Existing | N/A | Water | Hydro | Tumut 3 | Tumut 3 | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Tumut 3 | Hydro
Upper Tumut | Hydro | NSW | SNSW | N/A | Existing | N/A | Water | Hydro | Upper Tumut | Upper Tumut | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Upper Tumut | Hydro
Barron Gorge | Hydro | QLD | NQ | N/A | Existing | N/A | Water | Hydro | Barron Gorge | Barron Gorge | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Barron Gorge | Hydro
Kareeya | Hydro | QLD | NQ | N/A | Existing | N/A | Water | Hydro | Kareeya | Kareeya | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Kareeya | Hydro
Wivenhoe | Hydro | QLD | SQ | N/A | Existing | N/A | Water | Hydro | Wivenhoe | Wivenhoe | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Wivenhoe | Hydro
Bastyan | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Bastyan | Bastyan | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Bastyan | Hydro
Catagunya / Liapootah / Wayatinah | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Catagunya / Liapootah / Wayatinah | Catagunya / Liapootah / Wayatinah | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Catagunya / Liapootah / Wayatinah | Hydro
Cethana | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Cethana | Cethana | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Cethana | Hydro
Devils Gate | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Devils Gate | Devils Gate | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Devils Gate | Hydro
Fisher | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Fisher | Fisher | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Fisher | Hydro
Gordon | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Gordon | Gordon | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Gordon | Hydro
John Butters | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | John Butters | John Butters | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | John Butters | Hydro
Lake Echo | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Lake Echo | Lake Echo | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Lake Echo | Hydro
Lemonthyme / Wilmot | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Lemonthyme / Wilmot | Lemonthyme / Wilmot | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Lemonthyme / Wilmot | Hydro
Mackintosh | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Mackintosh | Mackintosh | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Mackintosh | Hydro
Meadowbank | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Meadowbank | Meadowbank | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Meadowbank | Hydro
Poatina | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Poatina | Poatina | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Poatina | Hydro
Reece | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Reece | Reece | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Reece | Hydro
Tarraleah | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Tarraleah | Tarraleah | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Tarraleah | Hydro
Trevallyn | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Trevallyn | Trevallyn | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Trevallyn | Hydro
Tribute | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Tribute | Tribute | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Tribute | Hydro
Tungatinah | Hydro | TAS | TAS | N/A | Existing | N/A | Water | Hydro | Tungatinah | Tungatinah | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Tungatinah | Hydro
Bogong / MacKay | Hydro | VIC | VIC | N/A | Existing | N/A | Water | Hydro | Bogong / Mackay | Bogong / Mackay | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Bogong / MacKay | Hydro
Dartmouth | Hydro | VIC | VIC | N/A | Existing | N/A | Water | Hydro | Dartmouth | Dartmouth | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Dartmouth | Hydro
Eildon | Hydro | VIC | VIC | N/A | Existing | N/A | Water | Hydro | Eildon | Eildon | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Eildon | Hydro
Hume Dam VIC | Hydro | VIC | VIC | N/A | Existing | N/A | Water | Hydro | Hume Dam VIC | Hume Dam VIC | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Hume Dam VIC | Hydro
Murray 1 | Hydro | VIC | VIC | N/A | Existing | N/A | Water | Hydro | Murray 1 | Murray 1 | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Murray 1 | Hydro
Murray 2 | Hydro | VIC | VIC | N/A | Existing | N/A | Water | Hydro | Murray 2 | Murray 2 | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Murray 2 | Hydro
West Kiewa | Hydro | VIC | VIC | N/A | Existing | N/A | Water | Hydro | West Kiewa | West Kiewa | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | West Kiewa | Hydro
Avonlie Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Existing | N/A | Solar | Solar | Avonlie Solar Farm | Avonlie Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Avonlie Solar Farm | Solar
Beryl Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Existing | N/A | Solar | Solar | Beryl Solar Farm | Beryl Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Beryl Solar Farm | Solar
Bomen Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Existing | N/A | Solar | Solar | Bomen Solar Farm | Bomen Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Bomen Solar Farm | Solar
Broken Hill Solar Farm | Large scale Solar PV | NSW | SNSW | Broken Hill | Existing | N/A | Solar | Solar | Broken Hill Solar Plant | Broken Hill Solar Plant | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Broken Hill Solar Farm | Solar
Coleambally Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Existing | N/A | Solar | Solar | Coleambally Solar Farm | Coleambally Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Coleambally Solar Farm | Solar
Corowa Solar Farm | Large scale Solar PV | NSW | SNSW | South West NSW | Existing | N/A | Solar | Solar | Corowa Solar Farm | Corowa Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Corowa Solar Farm | Solar
Darlington Point Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Existing | N/A | Solar | Solar | Darlington Point Solar Farm | Darlington Point Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Darlington Point Solar Farm | Solar
Finley Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Existing | N/A | Solar | Solar | Finley Solar Farm | Finley Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Finley Solar Farm | Solar
Goonumbla Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Existing | N/A | Solar | Solar | Goonumbla Solar Farm | Goonumbla Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Goonumbla Solar Farm | Solar
Gullen Range Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Existing | N/A | Solar | Solar | Gullen Range Solar Farm | Gullen Range Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Gullen Range Solar Farm | Solar
Gunnedah Solar Farm | Large scale Solar PV | NSW | NNSW | North West NSW | Existing | N/A | Solar | Solar | Gunnedah Solar Farm | Gunnedah Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Gunnedah Solar Farm | Solar
Hillston Sun Farm | Large scale Solar PV | NSW | SNSW | N/A | Existing | N/A | Solar | Solar | Hillston Sun Farm | Hillston Sun Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Hillston Sun Farm | Solar
Jemalong Solar | Large scale Solar PV | NSW | CNSW | N/A | Existing | N/A | Solar | Solar | Jemalong Solar | Jemalong Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Jemalong Solar | Solar
Junee Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Existing | N/A | Solar | Solar | Junee Solar Farm | Junee Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Junee Solar Farm | Solar
Limondale Solar Farm 1 | Large scale Solar PV | NSW | SNSW | South West NSW | Existing | N/A | Solar | Solar | Limondale Solar Farm 1 | Limondale Solar Farm 1 | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Limondale Solar Farm 1 | Solar
Limondale Solar Farm 2 | Large scale Solar PV | NSW | SNSW | South West NSW | Existing | N/A | Solar | Solar | Limondale Solar Farm 2 | Limondale Solar Farm 2 | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Limondale Solar Farm 2 | Solar
Manildra Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Existing | N/A | Solar | Solar | Manildra Solar Farm | Manildra Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Manildra Solar Farm | Solar
Molong Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Existing | N/A | Solar | Solar | Molong Solar Farm | Molong Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Molong Solar Farm | Solar
Moree Solar Farm | Large scale Solar PV | NSW | NNSW | North West NSW | Existing | N/A | Solar | Solar | Moree Solar Farm | Moree Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Moree Solar Farm | Solar
Nevertire Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Existing | N/A | Solar | Solar | Nevertire Solar Farm | Nevertire Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Nevertire Solar Farm | Solar
New England Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Existing | N/A | Solar | Solar | New England Solar Farm | New England Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | New England Solar Farm | Solar
Nyngan Solar Plant | Large scale Solar PV | NSW | CNSW | Central-West Orana | Existing | N/A | Solar | Solar | Nyngan Solar Plant | Nyngan Solar Plant | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Nyngan Solar Plant | Solar
Parkes Solar Farm | Large scale Solar PV | NSW | CNSW | N/A | Existing | N/A | Solar | Solar | Parkes Solar Farm | Parkes Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Parkes Solar Farm | Solar
Sunraysia Solar Farm | Large scale Solar PV | NSW | SNSW | South West NSW | Existing | N/A | Solar | Solar | Sunraysia Solar Farm | Sunraysia Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Sunraysia Solar Farm | Solar
Suntop Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Existing | N/A | Solar | Solar | Suntop Solar Farm | Suntop Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Suntop Solar Farm | Solar
Wagga North Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Existing | N/A | Solar | Solar | Wagga North Solar Farm | Wagga North Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Wagga North Solar Farm | Solar
Wellington Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Existing | N/A | Solar | Solar | Wellington Solar Farm | Wellington Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Wellington Solar Farm | Solar
West Wyalong Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Existing | N/A | Solar | Solar | West Wyalong Solar Farm | West Wyalong Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | West Wyalong Solar Farm | Solar
White Rock Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Existing | N/A | Solar | Solar | White Rock Solar Farm | White Rock Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | White Rock Solar Farm | Solar
Bluegrass Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Bluegrass Solar Farm | Bluegrass Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Bluegrass Solar Farm | Solar
Childers Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Existing | N/A | Solar | Solar | Childers Solar Farm | Childers Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Childers Solar Farm | Solar
Clare Solar Farm | Large scale Solar PV | QLD | NQ | Northern Qld | Existing | N/A | Solar | Solar | Clare Solar Farm | Clare Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Clare Solar Farm | Solar
Clermont Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Existing | N/A | Solar | Solar | Clermont Solar Farm | Clermont Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Clermont Solar Farm | Solar
Collinsville Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Existing | N/A | Solar | Solar | Collinsville PV | Collinsville PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Collinsville Solar Farm | Solar
Columboola Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Columboola Solar Farm | Columboola Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Columboola Solar Farm | Solar
Darling Downs Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Darling Downs Solar Farm | Darling Downs Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Darling Downs Solar Farm | Solar
Daydream Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Existing | N/A | Solar | Solar | Daydream Solar Farm | Daydream Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Daydream Solar Farm | Solar
Edenvale Solar Park | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Edenvale Solar Park | Edenvale Solar Park | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Edenvale Solar Park | Solar
Emerald Solar Farm | Large scale Solar PV | QLD | CQ | N/A | Existing | N/A | Solar | Solar | Emerald Solar Park | Emerald Solar Park | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Emerald Solar Farm | Solar
Gangarri Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Gangarri Solar Farm | Gangarri Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Gangarri Solar Farm | Solar
Hamilton Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Existing | N/A | Solar | Solar | Hamilton Solar Farm | Hamilton Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Hamilton Solar Farm | Solar
Haughton Solar Farm | Large scale Solar PV | QLD | NQ | Northern Qld | Existing | N/A | Solar | Solar | Haughton Solar Farm | Haughton Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Haughton Solar Farm | Solar
Hayman Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Existing | N/A | Solar | Solar | Hayman Solar Farm | Hayman Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Hayman Solar Farm | Solar
Hughenden Solar Farm | Large scale Solar PV | QLD | NQ | North Qld Clean Energy Hub | Existing | N/A | Solar | Solar | Hughenden Solar Farm | Hughenden Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Hughenden Solar Farm | Solar
Kennedy Energy Park Solar Farm | Large scale Solar PV | QLD | NQ | North Qld Clean Energy Hub | Existing | N/A | Solar | Solar | Kennedy Energy Park Solar Farm | Kennedy Energy Park Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Kennedy Energy Park Solar Farm | Solar
Kidston Solar Farm | Large scale Solar PV | QLD | NQ | North Qld Clean Energy Hub | Existing | N/A | Solar | Solar | Kidston Solar Project Phase One 50MW | Kidston Solar Project Phase One 50MW | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Kidston Solar Farm | Solar
Lilyvale Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Existing | N/A | Solar | Solar | Lilyvale Solar Farm | Lilyvale Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Lilyvale Solar Farm | Solar
Longreach Solar Farm | Large scale Solar PV | QLD | CQ | Barcaldine | Existing | N/A | Solar | Solar | Longreach Solar Farm | Longreach Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Longreach Solar Farm | Solar
Maryrorough Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Maryrorough Solar Farm | Maryrorough Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Maryrorough Solar Farm | Solar
Middlemount Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Existing | N/A | Solar | Solar | Middlemount Sun Farm | Middlemount Sun Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Middlemount Solar Farm | Solar
Moura Solar Farm | Large scale Solar PV | QLD | CQ | Fitzroy | Existing | N/A | Solar | Solar | Moura Solar Farm | Moura Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Moura Solar Farm | Solar
Oakey 1 Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Oakey 1 Solar Farm | Oakey 1 Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Oakey 1 Solar Farm | Solar
Oakey 2 Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Oakey 2 Solar Farm | Oakey 2 Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Oakey 2 Solar Farm | Solar
Ross River Solar Farm | Large scale Solar PV | QLD | NQ | Northern Qld | Existing | N/A | Solar | Solar | Ross River Solar Farm | Ross River Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Ross River Solar Farm | Solar
Rugby Run Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Existing | N/A | Solar | Solar | Rugby Run Solar Farm | Rugby Run Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Rugby Run Solar Farm | Solar
Sun Metals Corporation Solar Farm | Large scale Solar PV | QLD | NQ | Northern Qld | Existing | N/A | Solar | Solar | Sun Metals Corporation Solar Farm | Sun Metals Corporation Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Sun Metals Corporation Solar Farm | Solar
Susan River Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Existing | N/A | Solar | Solar | Susan River Solar Farm | Susan River Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Susan River Solar Farm | Solar
Warwick Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Warwick Solar Farm | Warwick Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Warwick Solar Farm | Solar
Western Downs Green Power Hub | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Western Downs Green Power Hub | Western Downs Green Power Hub | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Western Downs Green Power Hub | Solar
Whitsunday Solar Farm | Large scale Solar PV | QLD | CQ | Isaac | Existing | N/A | Solar | Solar | Whitsunday Solar Farm | Whitsunday Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Whitsunday Solar Farm | Solar
Yarranlea Solar Farm | Large scale Solar PV | QLD | SQ | Darling Downs | Existing | N/A | Solar | Solar | Yarranlea Solar Farm | Yarranlea Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Yarranlea Solar Farm | Solar
Adelaide Desalination Plant Solar Farm | Large scale Solar PV | SA | CSA | N/A | Existing | N/A | Solar | Solar | Adelaide Desalination Plant | Adelaide Desalination Plant | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Adelaide Desalination Plant Solar Farm | Solar
Bolivar Waste Water Treatment Solar Farm | Large scale Solar PV | SA | CSA | N/A | Existing | N/A | Solar | Solar | Bolivar Waste Water Treatment | Bolivar Waste Water Treatment | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Bolivar Waste Water Treatment Solar Farm | Solar
Bungala One Solar Farm | Large scale Solar PV | SA | CSA | Northern SA | Existing | N/A | Solar | Solar | Bungala One Solar Farm | Bungala One Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Bungala One Solar Farm | Solar
Bungala Two Solar Farm | Large scale Solar PV | SA | CSA | Northern SA | Existing | N/A | Solar | Solar | Bungala Two Solar Farm | Bungala Two Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Bungala Two Solar Farm | Solar
Happy Valley Reservoir | Large scale Solar PV | SA | CSA | N/A | Existing | N/A | Solar | Solar | Happy Valley Reservoir | Happy Valley Reservoir | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Happy Valley Reservoir | Solar
Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | Large scale Solar PV | SA | SESA | South East SA | Existing | N/A | Solar | Solar | Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Mannum Adelaide Pumping Station No 2 - MAPL2 (Palmer) | Solar
Mannum Adelaide Pumping Station No 3 - MAPL3 (Tungkillo) | Large scale Solar PV | SA | SESA | South East SA | Existing | N/A | Solar | Solar | Mannum Adelaide Pumping Station No 3 - MAPL3 (Kanmantoo) | Mannum Adelaide Pumping Station No 3 - MAPL3 (Kanmantoo) | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Mannum Adelaide Pumping Station No 3 - MAPL3 (Tungkillo) | Solar
Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | Large scale Solar PV | SA | CSA | Riverland | Existing | N/A | Solar | Solar | Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Morgan To Whyalla Pipeline No 1 PS And Water Filtration Plant | Solar
Morgan To Whyalla Pipeline No 2 PS | Large scale Solar PV | SA | CSA | Riverland | Existing | N/A | Solar | Solar | Morgan To Whyalla Pipeline No 2 PS | Morgan To Whyalla Pipeline No 2 PS | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Morgan To Whyalla Pipeline No 2 PS | Solar
Morgan To Whyalla Pipeline No 3 PS | Large scale Solar PV | SA | CSA | Riverland | Existing | N/A | Solar | Solar | Morgan To Whyalla Pipeline No 3 PS | Morgan To Whyalla Pipeline No 3 PS | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Morgan To Whyalla Pipeline No 3 PS | Solar
Morgan To Whyalla Pipeline No 4 PS | Large scale Solar PV | SA | CSA | Riverland | Existing | N/A | Solar | Solar | Morgan To Whyalla Pipeline No 4 PS | Morgan To Whyalla Pipeline No 4 PS | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Morgan To Whyalla Pipeline No 4 PS | Solar
Murray Bridge - Onkaparinga Pipeline Pump 2 | Large scale Solar PV | SA | SESA | South East SA | Existing | N/A | Solar | Solar | Murray Bridge - Onkaparinga Pipeline Pump 2 | Murray Bridge - Onkaparinga Pipeline Pump 2 | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Murray Bridge - Onkaparinga Pipeline Pump 2 | Solar
Port Augusta Renewable Energy Park - Solar | Large scale Solar PV | SA | CSA | Northern SA | Existing | N/A | Solar | Solar | Port Augusta Renewable Energy Park - Solar | Port Augusta Renewable Energy Park - Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Port Augusta Renewable Energy Park - Solar | Solar
Tailem Bend Solar Farm | Large scale Solar PV | SA | CSA | N/A | Existing | N/A | Solar | Solar | Tailem Bend Solar Farm | Tailem Bend Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Tailem Bend Solar Farm | Solar
Tailem Bend Solar Farm - stage 2 | Large scale Solar PV | SA | CSA | N/A | Existing | N/A | Solar | Solar | Tailem Bend Solar Farm - stage 2 | Tailem Bend Solar Farm - stage 2 | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Tailem Bend Solar Farm - stage 2 | Solar
Bannerton Solar Park | Large scale Solar PV | VIC | VIC | Murray River | Existing | N/A | Solar | Solar | Bannerton Solar Park | Bannerton Solar Park | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Bannerton Solar Park | Solar
Cohuna Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Existing | N/A | Solar | Solar | Cohuna Solar Farm | Cohuna Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Cohuna Solar Farm | Solar
Gannawarra Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Existing | N/A | Solar | Solar | Gannawarra Solar Farm | Gannawarra Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Gannawarra Solar Farm | Solar
Glenrowan West Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Existing | N/A | Solar | Solar | Glenrowan West Sun Farm | Glenrowan West Sun Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Glenrowan West Solar Farm | Solar
Karadoc Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Existing | N/A | Solar | Solar | Karadoc Solar Farm | Karadoc Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Karadoc Solar Farm | Solar
Kiamal Solar Farm stage 1 | Large scale Solar PV | VIC | VIC | Murray River | Existing | N/A | Solar | Solar | Kiamal Solar Farm stage 1 | Kiamal Solar Farm stage 1 | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Kiamal Solar Farm stage 1 | Solar
Numurkah Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Existing | N/A | Solar | Solar | Numurkah Solar Farm | Numurkah Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Numurkah Solar Farm | Solar
Wemen Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Existing | N/A | Solar | Solar | Wemen Solar Farm | Wemen Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Wemen Solar Farm | Solar
Winton Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Existing | N/A | Solar | Solar | Winton Solar Farm | Winton Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Winton Solar Farm | Solar
Wyalong Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Existing | N/A | Solar | Solar | Wyalong Solar Farm | Wyalong Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Wyalong Solar Farm | Solar
Yatpool Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Existing | N/A | Solar | Solar | Yatpool Solar Farm | Yatpool Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Yatpool Solar Farm | Solar
Bango 973 Wind Farm | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Bango 973 Wind Farm | Bango 973 Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Bango 973 Wind Farm | Wind
Bango 999 Wind Farm | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Bango 999 Wind Farm | Bango 999 Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Bango 999 Wind Farm | Wind
Boco Rock Wind Farm | Wind | NSW | SNSW | Cooma-Monaro | Existing | N/A | Wind | Wind | Boco Rock Wind Farm | Boco Rock Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Boco Rock Wind Farm | Wind
Bodangora Wind Farm | Wind | NSW | CNSW | Central-West Orana | Existing | N/A | Wind | Wind | Bodangora Wind Farm | Bodangora Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Bodangora Wind Farm | Wind
Capital Wind Farm | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Capital Wind Farm | Capital Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Capital Wind Farm | Wind
Collector Wind Farm | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Collector Wind Farm | Collector Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Collector Wind Farm | Wind
Crookwell 2 Wind Farm | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Crookwell 2 Wind Farm | Crookwell 2 Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Crookwell 2 Wind Farm | Wind
Crudine Ridge Wind Farm | Wind | NSW | CNSW | N/A | Existing | N/A | Wind | Wind | Crudine Ridge Wind Farm | Crudine Ridge Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Crudine Ridge Wind Farm | Wind
Cullerin Range Wind Farm | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Cullerin Range Wind Farm | Cullerin Range Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Cullerin Range Wind Farm | Wind
Gullen Range Wind Farm | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Gullen Range Wind Farm | Gullen Range Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Gullen Range Wind Farm | Wind
Gullen Range Wind Farm 2 | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Gullen Range Wind Farm 2 | Gullen Range Wind Farm 2 | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Gullen Range Wind Farm 2 | Wind
Gunning Wind Farm | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Gunning Wind Farm | Gunning Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Gunning Wind Farm | Wind
Sapphire Wind Farm | Wind | NSW | NNSW | New England | Existing | N/A | Wind | Wind | Sapphire Wind Farm | Sapphire Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Sapphire Wind Farm | Wind
Silverton Wind Farm | Wind | NSW | SNSW | Broken Hill | Existing | N/A | Wind | Wind | Silverton Wind Farm | Silverton Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Silverton Wind Farm | Wind
Taralga Wind Farm | Wind | NSW | CNSW | N/A | Existing | N/A | Wind | Wind | Taralga Wind Farm | Taralga Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Taralga Wind Farm | Wind
White Rock Wind Farm - Stage 1 | Wind | NSW | NNSW | New England | Existing | N/A | Wind | Wind | White Rock Wind Farm - Stage 1 | White Rock Wind Farm - Stage 1 | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | White Rock Wind Farm - Stage 1 | Wind
Woodlawn Wind Farm | Wind | NSW | SNSW | N/A | Existing | N/A | Wind | Wind | Woodlawn Wind Farm | Woodlawn Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Woodlawn Wind Farm | Wind
Coopers Gap Wind Farm | Wind | QLD | SQ | Darling Downs | Existing | N/A | Wind | Wind | Coopers Gap Wind Farm | Coopers Gap Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Coopers Gap Wind Farm | Wind
Kaban Green Power Hub - Wind Farm | Wind | QLD | NQ | Far North QLD | Existing | N/A | Wind | Wind | Kaban Green Power Hub - Wind Farm | Kaban Green Power Hub - Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Kaban Green Power Hub - Wind Farm | Wind
Kennedy Energy Park Wind Farm | Wind | QLD | NQ | North Qld Clean Energy Hub | Existing | N/A | Wind | Wind | Kennedy Energy Park Wind Farm | Kennedy Energy Park Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Kennedy Energy Park Wind Farm | Wind
Mount Emerald Wind Farm | Wind | QLD | NQ | Far North QLD | Existing | N/A | Wind | Wind | Mount Emerald Wind Farm | Mount Emerald Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Mount Emerald Wind Farm | Wind
Canunda Wind Farm | Wind | SA | SESA | South East SA | Existing | N/A | Wind | Wind | Canunda Wind Farm | Canunda Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Canunda Wind Farm | Wind
Cathedral Rocks Wind Farm | Wind | SA | CSA | Eastern Eyre Peninsula | Existing | N/A | Wind | Wind | Cathedral Rocks Wind Farm | Cathedral Rocks Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Cathedral Rocks Wind Farm | Wind
Clements Gap Wind Farm | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Clements Gap Wind Farm | Clements Gap Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Clements Gap Wind Farm | Wind
Hallett 4 North Brown Hill Wind Farm | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Hallett 4 North Brown Hill Wind Farm | Hallett 4 North Brown Hill Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Hallett 4 North Brown Hill Wind Farm | Wind
Hallett 5 The Bluff Wind Farm | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Hallett 5 The Bluff Wind Farm | Hallett 5 The Bluff Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Hallett 5 The Bluff Wind Farm | Wind
Hallett Stage 1 Brown Hill Wind Farm | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Hallett Stage 1 Brown Hill Wind Farm | Hallett Stage 1 Brown Hill Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Hallett Stage 1 Brown Hill Wind Farm | Wind
Hallett Stage 2 Hallett Hill Wind Farm | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Hallett Stage 2 Hallett Hill Wind Farm | Hallett Stage 2 Hallett Hill Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Hallett Stage 2 Hallett Hill Wind Farm | Wind
Hornsdale Wind Farm Stage 1 | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Hornsdale Wind Farm Stage 1 | Hornsdale Wind Farm Stage 1 | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Hornsdale Wind Farm Stage 1 | Wind
Hornsdale Wind Farm Stage 2 | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Hornsdale Wind Farm Stage 2 | Hornsdale Wind Farm Stage 2 | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Hornsdale Wind Farm Stage 2 | Wind
Hornsdale Wind Farm Stage 3 | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Hornsdale Wind Farm Stage 3 | Hornsdale Wind Farm Stage 3 | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Hornsdale Wind Farm Stage 3 | Wind
Lake Bonney 1 Wind Farm | Wind | SA | SESA | South East SA | Existing | N/A | Wind | Wind | Lake Bonney 1 Wind Farm | Lake Bonney 1 Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Lake Bonney 1 Wind Farm | Wind
Lake Bonney 2 Wind Farm | Wind | SA | SESA | South East SA | Existing | N/A | Wind | Wind | Lake Bonney 2 Wind Farm | Lake Bonney 2 Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Lake Bonney 2 Wind Farm | Wind
Lake Bonney 3 Wind Farm | Wind | SA | SESA | South East SA | Existing | N/A | Wind | Wind | Lake Bonney 3 Wind Farm | Lake Bonney 3 Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Lake Bonney 3 Wind Farm | Wind
Lincoln Gap Wind Farm - stage 1 | Wind | SA | CSA | Northern SA | Existing | N/A | Wind | Wind | Lincoln Gap Wind Farm - stage 1 | Lincoln Gap Wind Farm - stage 1 | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Lincoln Gap Wind Farm - stage 1 | Wind
Lincoln Gap Wind Farm - stage 2 | Wind | SA | CSA | Northern SA | Existing | N/A | Wind | Wind | Lincoln Gap Wind Farm - stage 2 | Lincoln Gap Wind Farm - stage 2 | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Lincoln Gap Wind Farm - stage 2 | Wind
Mount Millar Wind Farm | Wind | SA | CSA | Eastern Eyre Peninsula | Existing | N/A | Wind | Wind | Mount Millar Wind Farm | Mount Millar Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Mount Millar Wind Farm | Wind
Port Augusta Renewable Energy Park - Wind | Wind | SA | CSA | Northern SA | Existing | N/A | Wind | Wind | Port Augusta Renewable Energy Park - Wind | Port Augusta Renewable Energy Park - Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Port Augusta Renewable Energy Park - Wind | Wind
Snowtown S2 Wind Farm | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Snowtown S2 Wind Farm | Snowtown S2 Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Snowtown S2 Wind Farm | Wind
Snowtown Wind Farm | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Snowtown Wind Farm | Snowtown Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Snowtown Wind Farm | Wind
Starfish Hill Wind Farm | Wind | SA | CSA | N/A | Existing | N/A | Wind | Wind | Starfish Hill Wind Farm | Starfish Hill Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Starfish Hill Wind Farm | Wind
Waterloo Wind Farm | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Waterloo Wind Farm | Waterloo Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Waterloo Wind Farm | Wind
Wattle Point Wind Farm | Wind | SA | CSA | Yorke Peninsula | Existing | N/A | Wind | Wind | Wattle Point Wind Farm | Wattle Point Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Wattle Point Wind Farm | Wind
Willogoleche Wind Farm | Wind | SA | CSA | Mid-North SA | Existing | N/A | Wind | Wind | Willogoleche Wind Farm | Willogoleche Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Willogoleche Wind Farm | Wind
Cattle Hill Wind Farm | Wind | TAS | TAS | Central Highlands | Existing | N/A | Wind | Wind | Cattle Hill Wind Farm | Cattle Hill Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Cattle Hill Wind Farm | Wind
Granville Harbour Wind Farm | Wind | TAS | TAS | North West Tasmania | Existing | N/A | Wind | Wind | Granville Harbour Wind Farm | Granville Harbour Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Granville Harbour Wind Farm | Wind
Musselroe Wind Farm | Wind | TAS | TAS | N/A | Existing | N/A | Wind | Wind | Musselroe Wind Farm | Musselroe Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Musselroe Wind Farm | Wind
Woolnorth Wind Farm | Wind | TAS | TAS | N/A | Existing | N/A | Wind | Wind | Woolnorth Wind Farm | Woolnorth Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Woolnorth Wind Farm | Wind
Ararat Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Ararat Wind Farm | Ararat Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Ararat Wind Farm | Wind
Bald Hills Wind Farm | Wind | VIC | VIC | N/A | Existing | N/A | Wind | Wind | Bald Hills Wind Farm | Bald Hills Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Bald Hills Wind Farm | Wind
Berrybank Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Berrybank Wind Farm | Berrybank Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Berrybank Wind Farm | Wind
Bulgana Green Power Hub - Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Bulgana Green Power Hub - Wind Farm | Bulgana Green Power Hub - Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Bulgana Green Power Hub - Wind Farm | Wind
Challicum Hills Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Challicum Hills Wind Farm | Challicum Hills Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Challicum Hills Wind Farm | Wind
Cherry Tree Wind Farm | Wind | VIC | VIC | N/A | Existing | N/A | Wind | Wind | Cherry Tree Wind Farm | Cherry Tree Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Cherry Tree Wind Farm | Wind
Crowlands Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Crowlands Wind Farm | Crowlands Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Crowlands Wind Farm | Wind
Dulacca Wind Farm | Wind | QLD | SQ | Darling Downs | Existing | N/A | Wind | Wind | Dulacca Wind Farm | Dulacca Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Dulacca Wind Farm | Wind
Dundonnell Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Dundonnell Wind Farm | Dundonnell Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Dundonnell Wind Farm | Wind
Elaine Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Elaine Wind Farm | Elaine Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Elaine Wind Farm | Wind
Kiata Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Kiata Wind Farm | Kiata Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Kiata Wind Farm | Wind
Macarthur Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Macarthur Wind Farm | Macarthur Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Macarthur Wind Farm | Wind
Moorabool Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Moorabool Wind Farm | Moorabool Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Moorabool Wind Farm | Wind
Mortlake South Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Mortlake South Wind Farm | Mortlake South Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Mortlake South Wind Farm | Wind
Mortons Lane Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Mortons Lane Wind Farm | Mortons Lane Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Mortons Lane Wind Farm | Wind
Mt Gellibrand Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Mt Gellibrand Wind Farm | Mt Gellibrand Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Mt Gellibrand Wind Farm | Wind
Mt Mercer Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Mt Mercer Wind Farm | Mt Mercer Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Mt Mercer Wind Farm | Wind
Murra Warra Wind Farm - stage 1 | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Murra Warra Wind Farm - stage 1 | Murra Warra Wind Farm - stage 1 | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Murra Warra Wind Farm - stage 1 | Wind
Murra Warra Wind Farm - stage 2 | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Murra Warra Wind Farm - Stage 2 | Murra Warra Wind Farm - Stage 2 | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Murra Warra Wind Farm - stage 2 | Wind
Oaklands Hill Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Oaklands Hill Wind Farm | Oaklands Hill Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Oaklands Hill Wind Farm | Wind
Portland Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Portland Wind Farm | Portland Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Portland Wind Farm | Wind
Salt Creek Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Salt Creek Wind Farm | Salt Creek Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Salt Creek Wind Farm | Wind
Stockyard Hill Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Stockyard Hill Wind Farm | Stockyard Hill Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Stockyard Hill Wind Farm | Wind
Waubra Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Waubra Wind Farm | Waubra Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Waubra Wind Farm | Wind
Yaloak South Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Yaloak South Wind Farm | Yaloak South Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Yaloak South Wind Farm | Wind
Yambuk Wind Farm | Wind | VIC | VIC | South West Victoria | Existing | N/A | Wind | Wind | Yambuk Wind Farm | Yambuk Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Yambuk Wind Farm | Wind
Yendon Wind Farm | Wind | VIC | VIC | Western Victoria | Existing | N/A | Wind | Wind | Yendon Wind Farm | Yendon Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Yendon Wind Farm | Wind
Committed generator | Technology type | Region | Sub-region | REZ location | Status | Regional build cost zone | Fuel type | Fuel cost mapping | Summer rating (MW) | Winter rating (MW) | Forced outage rate |  |  |  | Mean time to repair |  |  |  | Maintenance duration (%) | Minimum load (MW) | Maximum capacity factor (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate | MLF | Auxiliary load (%) | Connection cost |  | Build limit |  | Total lead time
[11 empty] | Full outage (% of time) |  | Partial outage (% of time) |  | Full outage |  | Partial outage
[11 empty] | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | [8 empty] | Technology | Region | Technology | Region
Kurri Kurri OCGT | OCGT | NSW | SNW | N/A | Committed | N/A | Gas | Kurri Kurri | Kurri Kurri OCGT | Kurri Kurri OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Kurri Kurri OCGT | Kurri Kurri OCGT | Kurri Kurri OCGT2 | Kurri Kurri OCGT | OCGT
Tallawarra B* | OCGT | NSW | SNW | N/A | Committed | N/A | Gas | Tallawarra B | Tallawarra B* | Tallawarra B* | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT | OCGT |  |  | Tallawarra B | Tallawarra B | Tallawarra B | Tallawarra B* | OCGT
Kidston | Pumped Hydro | QLD | NQ | N/A | Committed | N/A | Water | Hydro | Kidston | Kidston | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Kidston | Hydro
Snowy 2.0 | Pumped Hydro | NSW | SNSW | Tumut | Committed | N/A | Water | Hydro | Snowy 2.0 | Snowy 2.0 | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Snowy 2.0 | Hydro
Girgarre Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Committed | N/A | Solar | Solar | Girgarre Solar Farm | Girgarre Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Girgarre Solar Farm | Solar
Glenrowan Solar Farm | Large scale Solar PV | VIC | VIC | Central North Vic | Committed | N/A | Solar | Solar | Glenrowan Solar Farm | Glenrowan Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Glenrowan Solar Farm | Solar
Mannum Solar Farm 2* | Large scale Solar PV | SA | CSA | Riverland | Committed | N/A | Solar | Solar | Mannum Solar Farm 2* | Mannum Solar Farm 2* | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Mannum Solar Farm 2* | Solar
Metz Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Committed | N/A | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Metz Solar Farm | Solar
Riverina Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Committed | N/A | Solar | Solar | Riverina Solar Farm | Riverina Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Riverina Solar Farm | Solar
Sebastopol Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Committed | N/A | Solar | Solar | Sebastopol Solar Farm | Sebastopol Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Sebastopol Solar Farm | Solar
Stubbo Solar Farm | Large scale Solar PV | NSW | CNSW | Central-West Orana | Committed | N/A | Solar | Solar | Stubbo Solar Farm | Stubbo Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Stubbo Solar Farm | Solar
Walla Walla Solar Farm | Large scale Solar PV | NSW | SNSW | N/A | Committed | N/A | Solar | Solar | Walla Walla Solar Farm | Walla Walla Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Walla Walla Solar Farm | Solar
Wandoan South Solar Farm - stage 1 | Large scale Solar PV | QLD | SQ | Darling Downs | Committed | N/A | Solar | Solar | Wandoan South Solar Farm - stage 1 | Wandoan South Solar Farm - stage 1 | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Wandoan South Solar Farm - stage 1 | Solar
Wellington North Solar Farm (Lightsource) | Large scale Solar PV | NSW | CNSW | Central-West Orana | Committed | N/A | Solar | Solar | Wellington North Solar Farm (Lightsource) | Wellington North Solar Farm (Lightsource) | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Wellington North Solar Farm (Lightsource) | Solar
Wollar Solar Farm | Large scale Solar PV | NSW | CNSW | N/A | Committed | N/A | Solar | Solar | Wollar Solar Farm | Wollar Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Wollar Solar Farm | Solar
Woolooga Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Committed | N/A | Solar | Solar | Woolooga Solar Farm | Woolooga Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Woolooga Solar Farm | Solar
Wunghnu Solar Farm | Large scale Solar PV | VIC | VIC | N/A | Committed | N/A | Solar | Solar | Wunghnu Solar Farm | Wunghnu Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Wunghnu Solar Farm | Solar
Clarke Creek Wind Farm | Wind | QLD | CQ | Isaac | Committed | N/A | Wind | Wind | Clarke Creek Wind Farm | Clarke Creek Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Clarke Creek Wind Farm | Wind
Crookwell 3 Wind Farm | Wind | NSW | SNSW | N/A | Committed | N/A | Wind | Wind | Crookwell 3 Wind Farm | Crookwell 3 Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Crookwell 3 Wind Farm | Wind
Flyers Creek Wind Farm | Wind | NSW | CNSW | Central-West Orana | Committed | N/A | Wind | Wind | Flyers Creek Wind Farm | Flyers Creek Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Flyers Creek Wind Farm | Wind
Golden Plains Wind Farm East | Wind | VIC | VIC | South West Victoria | Committed | N/A | Wind | Wind | Golden Plains Wind Farm East | Golden Plains Wind Farm East | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Golden Plains Wind Farm East | Wind
Goyder South Wind Farm 1A | Wind | SA | CSA | Mid-North SA | Committed | N/A | Wind | Wind | Goyder South Wind Farm 1A | Goyder South Wind Farm 1A | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Goyder South Wind Farm 1A | Wind
Goyder South Wind Farm 1B | Wind | SA | CSA | Mid-North SA | Committed | N/A | Wind | Wind | Goyder South Wind Farm 1B | Goyder South Wind Farm 1B | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Goyder South Wind Farm 1B | Wind
Hawkesdale Wind Farm | Wind | VIC | VIC | South West Victoria | Committed | N/A | Wind | Wind | Hawkesdale Wind Farm | Hawkesdale Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Hawkesdale Wind Farm | Wind
Ryan Corner Wind Farm | Wind | VIC | VIC | South West Victoria | Committed | N/A | Wind | Wind | Ryan Corner Wind Farm | Ryan Corner Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Ryan Corner Wind Farm | Wind
Rye Park Wind Farm | Wind | NSW | SNSW | N/A | Committed | N/A | Wind | Wind | Rye Park Wind Farm | Rye Park Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Rye Park Wind Farm | Wind
Wambo Wind Farm | Wind | QLD | SQ | Darling Downs | Committed | N/A | Wind | Wind | Wambo Wind Farm | Wambo Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Wambo Wind Farm | Wind
Anticipated projects | Technology type | Region | Sub-region | REZ location | Status | Regional build cost zone | Fuel type | Fuel cost mapping | Summer rating (MW) | Winter rating (MW) | Forced outage rate |  |  |  | Mean time to repair |  |  |  | Maintenance duration (%) | Minimum load (MW) | Maximum capacity factor (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate | MLF | Auxiliary load (%) | Connection cost |  | Build limit |  | Total lead time
[11 empty] | Full outage (% of time) |  | Partial outage (% of time) |  | Full outage |  | Partial outage
[11 empty] | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | [8 empty] | Technology | Region | Technology | Region
SA Hydrogen Turbine | Hydrogen-based gas turbines | SA | CSA | N/A | Anticipated | SA Low | Hyblend | SA new OCGT | SA Hydrogen Turbine | SA Hydrogen Turbine | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines |  |  | SA Hydrogen Turbine | SA Hydrogen Turbine | SA Hydrogen Turbine | SA Hydrogen Turbine | Hydrogen-based gas turbines
Borumba | Pumped Hydro | QLD | SQ | Banana | Anticipated | N/A | Water | Hydro | Borumba | Borumba | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro |  |  | All Hydro | All Hydro |  | Borumba | Hydro
Aramara Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Anticipated | N/A | Solar | Solar | Aramara Solar Farm | Aramara Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Aramara Solar Farm | Solar
Banksia Solar Farm | Large scale Solar PV | QLD | SQ | Wide Bay | Anticipated | N/A | Solar | Solar | Banksia Solar Farm | Banksia Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Banksia Solar Farm | Solar
Culcairn Solar Farm | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Anticipated | N/A | Solar | Solar | Culcairn Solar Farm | Culcairn Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Culcairn Solar Farm | Solar
Cultana Solar Farm | Large scale Solar PV | SA | CSA | Northern SA | Anticipated | N/A | Solar | Solar | Cultana Solar Farm | Cultana Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Cultana Solar Farm | Solar
Derby Solar Farm | Large scale Solar PV | VIC | VIC | Murray River | Anticipated | N/A | Solar | Solar | Derby Solar Farm | Derby Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Derby Solar Farm | Solar
Frasers Solar Farm | Large scale Solar PV | VIC | VIC | Gippsland | Anticipated | N/A | Solar | Solar | Frasers Solar Farm | Frasers Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Frasers Solar Farm | Solar
Horsham Solar Farm | Large scale Solar PV | VIC | VIC | Western Victoria | Anticipated | N/A | Solar | Solar | Frasers Solar Farm | Frasers Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Horsham Solar Farm | Solar
Lockhart Hybrid Facility - Solar | Large scale Solar PV | NSW | SNSW | Wagga Wagga | Anticipated | N/A | Solar | Solar | Lockhart Hybrid Facility - Solar | Lockhart Hybrid Facility - Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Lockhart Hybrid Facility - Solar | Solar
Quorn Park Solar Farm | Large scale Solar PV | NSW | CNSW | N/A | Anticipated | N/A | Solar | Solar | Quorn Park Solar Farm | Quorn Park Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Quorn Park Solar Farm | Solar
Tamworth Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Anticipated | N/A | Solar | Solar | Tamworth Solar Farm | Tamworth Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Tamworth Solar Farm | Solar
Tilbuster Solar Farm | Large scale Solar PV | NSW | NNSW | New England | Anticipated | N/A | Solar | Solar | Tilbuster Solar Farm | Tilbuster Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Tilbuster Solar Farm | Solar
MacIntyre Wind Farm | Wind | QLD | SQ | Darling Downs | Anticipated | N/A | Wind | Wind | MacIntyre Wind Farm | MacIntyre Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | MacIntyre Wind Farm | Wind
Uungula Wind Farm | Wind | NSW | CNSW | Central-West Orana | Anticipated | N/A | Wind | Wind | Uungula Wind Farm | Uungula Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Uungula Wind Farm | Wind
Woolsthorpe Wind Farm | Wind | VIC | VIC | South West Victoria | Anticipated | N/A | Wind | Wind | Woolsthorpe Wind Farm | Woolsthorpe Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Woolsthorpe Wind Farm | Wind
Batteries | Technology type | Region | Sub-region | REZ location | Status | Regional build cost zone | Fuel type | Fuel cost mapping | Summer rating (MW) | Winter rating (MW) | Forced outage rate |  |  |  | Mean time to repair |  |  |  | Maintenance duration (%) | Minimum load (MW) | Maximum capacity factor (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate | MLF | Auxiliary load (%) | Connection cost |  | Build limit |  | Total lead time
[11 empty] | Full outage (% of time) |  | Partial outage (% of time) |  | Full outage |  | Partial outage
[11 empty] | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | [8 empty] | Technology | Region | Technology | Region
Adelaide Desalination Plant BESS | Battery Storage | SA | CSA | N/A | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Adelaide Desalination Plant BESS | Battery Storage
Aldoga BESS Stage 1 | Battery Storage | QLD | GG | N/A | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Aldoga BESS Stage 1 | Battery Storage
Ballarat Energy Storage System | Battery Storage | VIC | VIC | Western Victoria | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Ballarat Energy Storage System | Battery Storage
Blyth BESS | Battery Storage | SA | CSA | Mid-North SA | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Blyth BESS | Battery Storage
Bolivar Waste Water Treatment BESS | Battery Storage | SA | CSA | N/A | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Bolivar Waste Water Treatment BESS | Battery Storage
Bouldercombe Battery project | Battery Storage | QLD | CQ | Fitzroy | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Bouldercombe Battery project | Battery Storage
Broken Hill BESS | Battery Storage | NSW | SNSW | Broken Hill | Committed* | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Broken Hill BESS | Battery Storage
Bulgana Green Power Hub BESS | Battery Storage | VIC | VIC | Western Victoria | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Bulgana Green Power Hub BESS | Battery Storage
Bungama Solar BESS | Battery Storage | SA | CSA | Mid-North SA | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Bungama Solar BESS | Battery Storage
Capital Battery | Battery Storage | NSW | SNSW | Tumut | Committed | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Capital Battery | Battery Storage
Chinchilla BESS | Battery Storage | QLD | SQ | Darling Downs | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Chinchilla BESS | Battery Storage
Christies Beach Wastewater Treatment Plant BESS | Battery Storage | SA | CSA | N/A | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Christies Beach Wastewater Treatment Plant BESS | Battery Storage
Dalrymple BESS | Battery Storage | SA | CSA | Yorke Peninsula | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Dalrymple BESS | Battery Storage
Darlington Point Energy Storage System | Battery Storage | NSW | SNSW | N/A | Committed | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Darlington Point Energy Storage System | Battery Storage
Eraring Big Battery | Battery Storage | NSW | SNW | Hunter Central Coast | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Eraring Big Battery | Battery Storage
Gannawarra Energy Storage System | Battery Storage | VIC | VIC | Murray River | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Gannawarra Energy Storage System | Battery Storage
Gnarwarre BESS | Battery Storage | VIC | VIC | South West Victoria | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Gnarwarre BESS | Battery Storage
Happy Valley Reservoir BESS | Battery Storage | SA | CSA | N/A | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Happy Valley Reservoir BESS | Battery Storage
Hazelwood BESS | Battery Storage | VIC | VIC | Gippsland | Committed | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Hazelwood BESS | Battery Storage
Hornsdale Power Reserve Unit 1 | Battery Storage | SA | CSA | Mid-North SA | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Hornsdale Power Reserve Unit 1 | Battery Storage
Koorangie Energy Storage System | Battery Storage | VIC | VIC | Murray River | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Koorangie Energy Storage System | Battery Storage
Lake Bonney BESS | Battery Storage | SA | SESA | South East SA | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Lake Bonney BESS | Battery Storage
Liddell BESS | Battery Storage | NSW | CNSW | Hunter-Central Coast | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (4hrs storage) | All Battery storage (4hrs storage) |  | Liddell BESS | Battery Storage
Lincoln Gap Wind Farm BESS | Battery Storage | SA | CSA | Northern SA | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Lincoln Gap Wind Farm BESS | Battery Storage
Lockhart Hybrid Facility - Battery | Battery Storage | NSW | SNSW | Wagga Wagga | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Lockhart Hybrid Facility - Battery | Battery Storage
Melbourne Renewable Energy Hub - Side A | Battery Storage | VIC | VIC | N/A | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Melbourne Renewable Energy Hub - Side A | Battery Storage
Mornington BESS | Battery Storage | VIC | VIC | N/A | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Mornington BESS | Battery Storage
Mortlake Battery | Battery Storage | VIC | VIC | South West Victoria | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Mortlake Battery | Battery Storage
Mt Fox BESS | Battery Storage | QLD | NQ | Northern Qld | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Mt Fox BESS | Battery Storage
New England Solar Farm BESS | Battery Storage | NSW | NNSW | New England | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | New England Solar Farm BESS | Battery Storage
Orana BESS | Battery Storage | NSW | CNSW | Central-West Orana | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Orana BESS | Battery Storage
Philip Island BESS | Battery Storage | VIC | VIC | N/A | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Philip Island BESS | Battery Storage
Queanbeyan BESS | Battery Storage | NSW | SNSW | Tumut | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Queanbeyan BESS | Battery Storage
Quorn Park BESS | Battery Storage | NSW | CNSW | N/A | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Quorn Park BESS | Battery Storage
Rangebank BESS | Battery Storage | VIC | VIC | N/A | Committed | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Rangebank BESS | Battery Storage
Richmond Valley BESS | Battery Storage | NSW | NNSW | N/A | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (8hrs storage) | All Battery storage (8hrs storage) |  | Richmond Valley BESS | Battery Storage
Riverina Energy Storage System 1 | Battery Storage | NSW | SNSW | N/A | Committed | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Riverina Energy Storage System 1 | Battery Storage
Riverina Energy Storage System 2 | Battery Storage | NSW | SNSW | N/A | Committed | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Riverina Energy Storage System 2 | Battery Storage
Sapphire Wind Farm BESS | Battery Storage | NSW | NNSW | New England | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Sapphire Wind Farm BESS | Battery Storage
Stanwell BESS | Battery Storage | QLD | CQ | Fitzroy | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Stanwell BESS | Battery Storage
Swanbank BESS | Battery Storage | QLD | SQ | N/A | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Swanbank BESS | Battery Storage
Tailem Bend Battery Project | Battery Storage | SA | CSA | N/A | Committed | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Tailem Bend Battery Project | Battery Storage
Tamworth BESS | Battery Storage | NSW | NNSW | N/A | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Tamworth BESS | Battery Storage
Tarong BESS | Battery Storage | QLD | SQ | Darling Downs | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Tarong BESS | Battery Storage
Templers BESS | Battery Storage | SA | CSA | Mid-North SA | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Templers BESS | Battery Storage
Terang BESS | Battery Storage | VIC | VIC | South West Victoria | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Terang BESS | Battery Storage
Torrens Island BESS | Battery Storage | SA | CSA | N/A | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Torrens Island BESS | Battery Storage
Ulinda Park BESS | Battery Storage | QLD | SQ | Darling Downs | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Ulinda Park BESS | Battery Storage
Victorian Big Battery | Battery Storage | VIC | VIC | N/A | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Victorian Big Battery | Battery Storage
Wallgrove Grid Battery project | Battery Storage | NSW | SNW | N/A | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Wallgrove Grid Battery project | Battery Storage
Wandoan South BESS | Battery Storage | QLD | SQ | Darling Downs | Existing | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Wandoan South BESS | Battery Storage
Waratah Super Battery | Battery Storage | NSW | SNW | N/A | Committed* | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Waratah Super Battery | Battery Storage
Western Downs Battery | Battery Storage | QLD | SQ | Darling Downs | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Western Downs Battery | Battery Storage
Wooreen Energy Storage System | Battery Storage | VIC | VIC | Gippsland | Anticipated | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (4hrs storage) | All Battery storage (4hrs storage) |  | Wooreen Energy Storage System | Battery Storage
Additional projects | Technology type | Region | Sub-region | REZ location | Status | Regional build cost zone | Fuel type | Fuel cost mapping | Summer rating (MW) | Winter rating (MW) | Forced outage rate |  |  |  | Mean time to repair |  |  |  | Maintenance duration (%) | Minimum load (MW) | Maximum capacity factor (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate | MLF | Auxiliary load (%) | Connection cost |  | Build limit |  | Total lead time
[11 empty] | Full outage (% of time) |  | Partial outage (% of time) |  | Full outage |  | Partial outage
[11 empty] | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | [8 empty] | Technology | Region | Technology | Region
Coppabella Wind Farm | Wind | NSW | SNSW | Tumut | Additional projects | N/A | Wind | Wind | Mortlake South Wind Farm | Mortlake South Wind Farm | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | All Wind | All Wind |  | Coppabella Wind Farm | Wind
Derby Solar Project BESS | Battery Storage | VIC | VIC | Murray River | Additional projects | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Derby Solar Project BESS | Battery Storage
Fulham Solar Farm | Large scale Solar PV | VIC | VIC | Gippsland | Additional projects | N/A | Solar | Solar | Frasers Solar Farm | Frasers Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Fulham Solar Farm | Solar
Fulham Solar Farm BESS | Battery Storage | VIC | VIC | Gippsland | Additional projects | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (1hr storage) | All Battery storage (1hr storage) |  | Fulham Solar Farm BESS | Battery Storage
Goulburn River BESS | Battery Storage | NSW | CNSW | N/A | Additional projects | N/A | Battery | Battery | Goulburn River BESS | Goulburn River BESS | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (8hrs storage) | All Battery storage (8hrs storage) |  | Goulburn River BESS | Battery Storage
Horsham Solar Farm BESS | Battery Storage | VIC | VIC | Western Victoria | Additional projects | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Horsham Solar Farm BESS | Battery Storage
Kiamal Solar Farm – Stage 2 | Large scale Solar PV | VIC | VIC | Murray River | Additional projects | N/A | Solar | Solar | Frasers Solar Farm | Frasers Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | Kiamal Solar Farm – Stage 2 | Solar
Kiamal Solar Farm – Stage 2 BESS | Battery Storage | VIC | VIC | Murray River | Additional projects | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Kiamal Solar Farm – Stage 2 BESS | Battery Storage
Kogan Gas | Hydrogen-based gas turbines | QLD | SQ | N/A | Additional projects | QLD Low | Hyblend | QLD new OCGT | Kogan Gas | Kogan Gas | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines | Hydrogen-based gas turbines |  |  | Kogan Gas | Kogan Gas | Kogan Gas | Kogan Gas | Hydrogen-based gas turbines
Limondale BESS | Battery Storage | NSW | SNSW | South West NSW | Additional projects | N/A | Battery | Battery | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (8hrs storage) | All Battery storage (8hrs storage) |  | Limondale BESS | Battery Storage
New England Solar Farm - stage 2 | Large scale Solar PV | NSW | NNSW | New England | Additional projects | N/A | Solar | Solar | Frasers Solar Farm | Frasers Solar Farm | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | All Large scale solar PV | All Large scale solar PV |  | New England Solar Farm - stage 2 | Solar
Silver City Energy Storage | Battery Storage | NSW | SNSW | Broken Hill | Additional projects | N/A | Battery | Battery | Silver City Energy Storage | Silver City Energy Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (8hrs storage) | All Battery storage (8hrs storage) |  | Silver City Energy Storage | Battery Storage
Smithfield BESS | Battery Storage | NSW | SNW | N/A | Additional projects | N/A | Battery | Battery | Smithfield BESS | Smithfield BESS | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage | Battery Storage |  |  | All Battery storage (2hrs storage) | All Battery storage (2hrs storage) |  | Smithfield BESS | Battery Storage
New entrants | Technology type | Region | Sub-region | REZ location | Status | Regional build cost zone | Fuel type | Fuel cost mapping | Summer rating (MW) | Winter rating (MW) | Forced outage rate |  |  |  | Mean time to repair |  |  |  | Maintenance duration (%) | Minimum load (MW) | Maximum capacity factor (%) | FOM ($/kW/annum) | VOM ($/MWh sent-out) | Heat rate | MLF | Auxiliary load (%) | Connection cost |  | Build limit |  | Total lead time
[11 empty] | Full outage (% of time) |  | Partial outage (% of time) |  | Full outage |  | Partial outage
[11 empty] | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | Until 2022 | Post 2022 | [8 empty] | Technology | REZ/Region | Technology | Region
OCGT (small GT) | OCGT (small GT) | QLD | NQ | N/A | New Entrant | QLD Low | Gas | QLD new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | QLD Low | QLD Low | OCGT (small GT) | NE_NQ | OCGT (small GT) | Small OCGT2 | QLD | OCGT (small GT) | QLD | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | QLD | CQ | N/A | New Entrant | QLD Low | Gas | QLD new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | QLD Low | QLD Low | OCGT (small GT) | NE_CQ | OCGT (small GT) | Small OCGT2 | QLD | OCGT (small GT) | QLD | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | QLD | GG | N/A | New Entrant | QLD Low | Gas | QLD new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | QLD Low | QLD Low | OCGT (small GT) | NE_GG | OCGT (small GT) | Small OCGT2 | QLD | OCGT (small GT) | QLD | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | QLD | SQ | N/A | New Entrant | QLD Low | Gas | QLD new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | QLD Low | QLD Low | OCGT (small GT) | NE_SQ | OCGT (small GT) | Small OCGT2 | QLD | OCGT (small GT) | QLD | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | NSW | NNSW | N/A | New Entrant | NSW Low | Gas | NSW new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | NSW Low | NSW Low | OCGT (small GT) | NE_NNSW | OCGT (small GT) | Small OCGT2 | NSW | OCGT (small GT) | NSW | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | NSW | CNSW | N/A | New Entrant | NSW Low | Gas | NSW new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | NSW Low | NSW Low | OCGT (small GT) | NE_CNSW | OCGT (small GT) | Small OCGT2 | NSW | OCGT (small GT) | NSW | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | NSW | SNW | N/A | New Entrant | NSW Low | Gas | NSW new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | NSW Low | NSW Low | OCGT (small GT) | NE_SNW | OCGT (small GT) | Small OCGT2 | NSW | OCGT (small GT) | NSW | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | NSW | SNSW | N/A | New Entrant | NSW Medium | Gas | NSW new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | NSW Medium | NSW Medium | OCGT (small GT) | NE_SNSW | OCGT (small GT) | Small OCGT2 | NSW | OCGT (small GT) | NSW | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | VIC | VIC | N/A | New Entrant | VIC Low | Gas | VIC new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | VIC Low | VIC Low | OCGT (small GT) | NE_VIC1 | OCGT (small GT) | Small OCGT2 | VIC | OCGT (small GT) | VIC | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | SA | CSA | N/A | New Entrant | SA Low | Gas | SA new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | SA Low | SA Low | OCGT (small GT) | NE_CSA | OCGT (small GT) | Small OCGT2 | SA | OCGT (small GT) | SA | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | SA | SESA | N/A | New Entrant | SA Medium | Gas | SA new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | SA Medium | SA Medium | OCGT (small GT) | NE_SESA | OCGT (small GT) | Small OCGT2 | SA | OCGT (small GT) | SA | OCGT (small GT)
OCGT (small GT) | OCGT (small GT) | TAS | TAS | N/A | New Entrant | TAS Low | Gas | TAS new OCGT | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) | OCGT (small GT) |  |  | TAS Low | TAS Low | OCGT (small GT) | NE_TAS1 | OCGT (small GT) | Small OCGT2 | TAS | OCGT (small GT) | TAS | OCGT (small GT)
OCGT (large GT) | OCGT (large GT) | QLD | NQ | N/A | New Entrant | QLD Low | Gas | QLD new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | QLD Low | QLD Low | OCGT (large GT) | NE_NQ | OCGT (large GT) | Large OCGT | QLD | OCGT (large GT) | QLD | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | QLD | CQ | N/A | New Entrant | QLD Low | Gas | QLD new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | QLD Low | QLD Low | OCGT (large GT) | NE_CQ | OCGT (large GT) | Large OCGT | QLD | OCGT (large GT) | QLD | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | QLD | GG | N/A | New Entrant | QLD Low | Gas | QLD new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | QLD Low | QLD Low | OCGT (large GT) | NE_GG | OCGT (large GT) | Large OCGT | QLD | OCGT (large GT) | QLD | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | QLD | SQ | N/A | New Entrant | QLD Low | Gas | QLD new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | QLD Low | QLD Low | OCGT (large GT) | NE_SQ | OCGT (large GT) | Large OCGT | QLD | OCGT (large GT) | QLD | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | NSW | NNSW | N/A | New Entrant | NSW Low | Gas | NSW new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | NSW Low | NSW Low | OCGT (large GT) | NE_NNSW | OCGT (large GT) | Large OCGT | NSW | OCGT (large GT) | NSW | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | NSW | CNSW | N/A | New Entrant | NSW Low | Gas | NSW new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | NSW Low | NSW Low | OCGT (large GT) | NE_CNSW | OCGT (large GT) | Large OCGT | NSW | OCGT (large GT) | NSW | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | NSW | SNW | N/A | New Entrant | NSW Low | Gas | NSW new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | NSW Low | NSW Low | OCGT (large GT) | NE_SNW | OCGT (large GT) | Large OCGT | NSW | OCGT (large GT) | NSW | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | NSW | SNSW | N/A | New Entrant | NSW Medium | Gas | NSW new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | NSW Medium | NSW Medium | OCGT (large GT) | NE_SNSW | OCGT (large GT) | Large OCGT | NSW | OCGT (large GT) | NSW | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | VIC | VIC | N/A | New Entrant | VIC Low | Gas | VIC new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | VIC Low | VIC Low | OCGT (large GT) | NE_VIC1 | OCGT (large GT) | Large OCGT | VIC | OCGT (large GT) | VIC | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | SA | CSA | N/A | New Entrant | SA Low | Gas | SA new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | SA Low | SA Low | OCGT (large GT) | NE_CSA | OCGT (large GT) | Large OCGT | SA | OCGT (large GT) | SA | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | SA | SESA | N/A | New Entrant | SA Medium | Gas | SA new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | SA Medium | SA Medium | OCGT (large GT) | NE_SESA | OCGT (large GT) | Large OCGT | SA | OCGT (large GT) | SA | OCGT (large GT)
OCGT (large GT) | OCGT (large GT) | TAS | TAS | N/A | New Entrant | TAS Low | Gas | TAS new OCGT | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) | OCGT (large GT) |  |  | TAS Low | TAS Low | OCGT (large GT) | NE_TAS1 | OCGT (large GT) | Large OCGT | TAS | OCGT (large GT) | TAS | OCGT (large GT)
CCGT | CCGT | QLD | NQ | N/A | New Entrant | QLD Low | Gas | QLD new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | QLD Low | QLD Low | CCGT | NE_NQ | CCGT | CCGT2 | QLD | CCGT | QLD | CCGT
CCGT | CCGT | QLD | CQ | N/A | New Entrant | QLD Low | Gas | QLD new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | QLD Low | QLD Low | CCGT | NE_CQ | CCGT | CCGT2 | QLD | CCGT | QLD | CCGT
CCGT | CCGT | QLD | GG | N/A | New Entrant | QLD Low | Gas | QLD new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | QLD Low | QLD Low | CCGT | NE_GG | CCGT | CCGT2 | QLD | CCGT | QLD | CCGT
CCGT | CCGT | QLD | SQ | N/A | New Entrant | QLD Low | Gas | QLD new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | QLD Low | QLD Low | CCGT | NE_SQ | CCGT | CCGT2 | QLD | CCGT | QLD | CCGT
CCGT | CCGT | NSW | NNSW | N/A | New Entrant | NSW Low | Gas | NSW new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | NSW Low | NSW Low | CCGT | NE_NNSW | CCGT | CCGT2 | NSW | CCGT | NSW | CCGT
CCGT | CCGT | NSW | CNSW | N/A | New Entrant | NSW Low | Gas | NSW new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | NSW Low | NSW Low | CCGT | NE_CNSW | CCGT | CCGT2 | NSW | CCGT | NSW | CCGT
CCGT | CCGT | NSW | SNW | N/A | New Entrant | NSW Low | Gas | NSW new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | NSW Low | NSW Low | CCGT | NE_SNW | CCGT | CCGT2 | NSW | CCGT | NSW | CCGT
CCGT | CCGT | NSW | SNSW | N/A | New Entrant | NSW Medium | Gas | NSW new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | NSW Medium | NSW Medium | CCGT | NE_SNSW | CCGT | CCGT2 | NSW | CCGT | NSW | CCGT
CCGT | CCGT | VIC | VIC | N/A | New Entrant | VIC Low | Gas | VIC new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | VIC Low | VIC Low | CCGT | NE_VIC1 | CCGT | CCGT2 | VIC | CCGT | VIC | CCGT
CCGT | CCGT | SA | CSA | N/A | New Entrant | SA Low | Gas | SA new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | SA Low | SA Low | CCGT | NE_CSA | CCGT | CCGT2 | SA | CCGT | SA | CCGT
CCGT | CCGT | SA | SESA | N/A | New Entrant | SA Medium | Gas | SA new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | SA Medium | SA Medium | CCGT | NE_SESA | CCGT | CCGT2 | SA | CCGT | SA | CCGT
CCGT | CCGT | TAS | TAS | N/A | New Entrant | TAS Low | Gas | TAS new CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT | CCGT |  |  | TAS Low | TAS Low | CCGT | NE_TAS1 | CCGT | CCGT2 | TAS | CCGT | TAS | CCGT
CCGT with CCS | CCGT with CCS | QLD | NQ | N/A | New Entrant | QLD Low | Gas | QLD new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | QLD Low | QLD Low | CCGT with CCS | NE_NQ | CCGT with CCS | CCGT with CCS | QLD | CCGT with CCS | QLD | CCGT with CCS
CCGT with CCS | CCGT with CCS | QLD | CQ | N/A | New Entrant | QLD Low | Gas | QLD new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | QLD Low | QLD Low | CCGT with CCS | NE_CQ | CCGT with CCS | CCGT with CCS | QLD | CCGT with CCS | QLD | CCGT with CCS
CCGT with CCS | CCGT with CCS | QLD | GG | N/A | New Entrant | QLD Low | Gas | QLD new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | QLD Low | QLD Low | CCGT with CCS | NE_GG | CCGT with CCS | CCGT with CCS | QLD | CCGT with CCS | QLD | CCGT with CCS
CCGT with CCS | CCGT with CCS | QLD | SQ | N/A | New Entrant | QLD Low | Gas | QLD new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | QLD Low | QLD Low | CCGT with CCS | NE_SQ | CCGT with CCS | CCGT with CCS | QLD | CCGT with CCS | QLD | CCGT with CCS
CCGT with CCS | CCGT with CCS | NSW | NNSW | N/A | New Entrant | NSW Low | Gas | NSW new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | NSW Low | NSW Low | CCGT with CCS | NE_NNSW | CCGT with CCS | CCGT with CCS | NSW | CCGT with CCS | NSW | CCGT with CCS
CCGT with CCS | CCGT with CCS | NSW | CNSW | N/A | New Entrant | NSW Low | Gas | NSW new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | NSW Low | NSW Low | CCGT with CCS | NE_CNSW | CCGT with CCS | CCGT with CCS | NSW | CCGT with CCS | NSW | CCGT with CCS
CCGT with CCS | CCGT with CCS | NSW | SNW | N/A | New Entrant | NSW Low | Gas | NSW new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | NSW Low | NSW Low | CCGT with CCS | NE_SNW | CCGT with CCS | CCGT with CCS | NSW | CCGT with CCS | NSW | CCGT with CCS
CCGT with CCS | CCGT with CCS | NSW | SNSW | N/A | New Entrant | NSW Medium | Gas | NSW new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | NSW Medium | NSW Medium | CCGT with CCS | NE_SNSW | CCGT with CCS | CCGT with CCS | NSW | CCGT with CCS | NSW | CCGT with CCS
CCGT with CCS | CCGT with CCS | VIC | VIC | N/A | New Entrant | VIC Low | Gas | VIC new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | VIC Low | VIC Low | CCGT with CCS | NE_VIC1 | CCGT with CCS | CCGT with CCS | VIC | CCGT with CCS | VIC | CCGT with CCS
CCGT with CCS | CCGT with CCS | SA | CSA | N/A | New Entrant | SA Low | Gas | SA new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | SA Low | SA Low | CCGT with CCS | NE_CSA | CCGT with CCS | CCGT with CCS | SA | CCGT with CCS | SA | CCGT with CCS
CCGT with CCS | CCGT with CCS | SA | SESA | N/A | New Entrant | SA Medium | Gas | SA new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | SA Medium | SA Medium | CCGT with CCS | NE_SESA | CCGT with CCS | CCGT with CCS | SA | CCGT with CCS | SA | CCGT with CCS
CCGT with CCS | CCGT with CCS | TAS | TAS | N/A | New Entrant | TAS Low | Gas | TAS new CCGT | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS | CCGT with CCS |  |  | TAS Low | TAS Low | CCGT with CCS | NE_TAS1 | CCGT with CCS | CCGT with CCS | TAS | CCGT with CCS | TAS | CCGT with CCS
Biomass | Biomass | QLD | NQ | N/A | New Entrant | QLD Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | QLD Low | QLD Low | Biomass | NE_NQ | Biomass | Biomass | QLD | Biomass | QLD | Biomass
Biomass | Biomass | QLD | CQ | N/A | New Entrant | QLD Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | QLD Low | QLD Low | Biomass | NE_CQ | Biomass | Biomass | QLD | Biomass | QLD | Biomass
Biomass | Biomass | QLD | GG | N/A | New Entrant | QLD Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | QLD Low | QLD Low | Biomass | NE_GG | Biomass | Biomass | QLD | Biomass | QLD | Biomass
Biomass | Biomass | QLD | SQ | N/A | New Entrant | QLD Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | QLD Low | QLD Low | Biomass | NE_SQ | Biomass | Biomass | QLD | Biomass | QLD | Biomass
Biomass | Biomass | NSW | NNSW | N/A | New Entrant | NSW Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | NSW Low | NSW Low | Biomass | NE_NNSW | Biomass | Biomass | NSW | Biomass | NSW | Biomass
Biomass | Biomass | NSW | CNSW | N/A | New Entrant | NSW Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | NSW Low | NSW Low | Biomass | NE_CNSW | Biomass | Biomass | NSW | Biomass | NSW | Biomass
Biomass | Biomass | NSW | SNW | N/A | New Entrant | NSW Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | NSW Low | NSW Low | Biomass | NE_SNW | Biomass | Biomass | NSW | Biomass | NSW | Biomass
Biomass | Biomass | NSW | SNSW | N/A | New Entrant | NSW Medium | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | NSW Medium | NSW Medium | Biomass | NE_SNSW | Biomass | Biomass | NSW | Biomass | NSW | Biomass
Biomass | Biomass | VIC | VIC | N/A | New Entrant | VIC Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | VIC Low | VIC Low | Biomass | NE_VIC1 | Biomass | Biomass | VIC | Biomass | VIC | Biomass
Biomass | Biomass | SA | CSA | N/A | New Entrant | SA Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | SA Low | SA Low | Biomass | NE_CSA | Biomass | Biomass | SA | Biomass | SA | Biomass
Biomass | Biomass | SA | SESA | N/A | New Entrant | SA Medium | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | SA Medium | SA Medium | Biomass | NE_SESA | Biomass | Biomass | SA | Biomass | SA | Biomass
Biomass | Biomass | TAS | TAS | N/A | New Entrant | TAS Low | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass | Biomass |  |  | TAS Low | TAS Low | Biomass | NE_TAS1 | Biomass | Biomass | TAS | Biomass | TAS | Biomass
Large scale Solar PV | Large scale Solar PV | QLD | NQ | Far North QLD | New Entrant | QLD Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | QLD Low | QLD Low | Large scale Solar PV | REZ_Q1_Solar | Large scale Solar PV | Large scale Solar PV | Far North Queensland | Large scale Solar PV | Far North QLD | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | QLD | NQ | North Qld Clean Energy Hub | New Entrant | QLD Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | QLD Low | QLD Low | Large scale Solar PV | REZ_Q2_Solar | Large scale Solar PV | Large scale Solar PV | North Queensland Clean Energy Hub | Large scale Solar PV | North Qld Clean Energy Hub | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | QLD | NQ | Northern Qld | New Entrant | QLD Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | QLD Low | QLD Low | Large scale Solar PV | REZ_Q3_Solar | Large scale Solar PV | Large scale Solar PV | Northern Queensland | Large scale Solar PV | Northern Qld | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | QLD | CQ | Isaac | New Entrant | QLD Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | QLD Low | QLD Low | Large scale Solar PV | REZ_Q4_Solar | Large scale Solar PV | Large scale Solar PV | Isaac | Large scale Solar PV | Isaac | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | QLD | CQ | Barcaldine | New Entrant | QLD Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | QLD Medium | QLD Medium | Large scale Solar PV | REZ_Q5_Solar | Large scale Solar PV | Large scale Solar PV | Barcaldine | Large scale Solar PV | Barcaldine | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | QLD | CQ | Fitzroy | New Entrant | QLD Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | QLD Low | QLD Low | Large scale Solar PV | REZ_Q6_Solar | Large scale Solar PV | Large scale Solar PV | Fitzroy | Large scale Solar PV | Fitzroy | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | QLD | SQ | Wide Bay | New Entrant | QLD Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | QLD Low | QLD Low | Large scale Solar PV | REZ_Q7_Solar | Large scale Solar PV | Large scale Solar PV | Wide Bay | Large scale Solar PV | Wide Bay | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | QLD | SQ | Darling Downs | New Entrant | QLD Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | QLD Low | QLD Low | Large scale Solar PV | REZ_Q8_Solar | Large scale Solar PV | Large scale Solar PV | Darling Downs | Large scale Solar PV | Darling Downs | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | QLD | SQ | Banana | New Entrant | QLD Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | QLD Medium | QLD Medium | Large scale Solar PV | REZ_Q9_Solar | Large scale Solar PV | Large scale Solar PV | Banana | Large scale Solar PV | Banana | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | NNSW | North West NSW | New Entrant | NSW Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW Medium | NSW Medium | Large scale Solar PV | REZ_N1_Solar | Large scale Solar PV | Large scale Solar PV | North West New South Wales | Large scale Solar PV | North West NSW | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | NNSW | New England | New Entrant | NSW Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW Low | NSW Low | Large scale Solar PV | REZ_N2_Solar | Large scale Solar PV | Large scale Solar PV | New England | Large scale Solar PV | New England | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | CNSW | Central-West Orana | New Entrant | NSW Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW Medium | NSW Medium | Large scale Solar PV | REZ_N3_Solar | Large scale Solar PV | Large scale Solar PV | Central-West Orana | Large scale Solar PV | Central-West Orana | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | SNSW | Broken Hill | New Entrant | NSW High | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW High | NSW High | Large scale Solar PV | REZ_N4_Solar | Large scale Solar PV | Large scale Solar PV | Broken Hill | Large scale Solar PV | Broken Hill | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | SNSW | South West NSW | New Entrant | NSW High | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW High | NSW High | Large scale Solar PV | REZ_N5_Solar | Large scale Solar PV | Large scale Solar PV | South West New South Wales | Large scale Solar PV | South West NSW | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | SNSW | Wagga Wagga | New Entrant | NSW Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW Medium | NSW Medium | Large scale Solar PV | REZ_N6_Solar | Large scale Solar PV | Large scale Solar PV | Wagga Wagga | Large scale Solar PV | Wagga Wagga | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | SNSW | Tumut | New Entrant | NSW Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW Medium | NSW Medium | Large scale Solar PV | REZ_N7_Solar | Large scale Solar PV | Large scale Solar PV | Tumut | Large scale Solar PV | Tumut | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | SNSW | Cooma-Monaro | New Entrant | NSW Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW Medium | NSW Medium | Large scale Solar PV | REZ_N8_Solar | Large scale Solar PV | Large scale Solar PV | Cooma-Monaro | Large scale Solar PV | Cooma-Monaro | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | CNSW | Hunter-Central Coast | New Entrant | NSW Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW Low | NSW Low | Large scale Solar PV | REZ_N9_Solar | Large scale Solar PV | Large scale Solar PV | Hunter-Central Coast | Large scale Solar PV | Hunter-Central Coast | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | SNW | Illawarra | New Entrant | NSW Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW Low | NSW Low | Large scale Solar PV | REZ_N12_Solar | Large scale Solar PV | Large scale Solar PV | Illawarra | Large scale Solar PV | Illawarra | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | VIC | VIC | Ovens Murray | New Entrant | VIC Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | VIC Medium | VIC Medium | Large scale Solar PV | REZ_V1_Solar | Large scale Solar PV | Large scale Solar PV | Ovens Murray | Large scale Solar PV | Ovens Murray | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | VIC | VIC | Murray River | New Entrant | VIC Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | VIC Medium | VIC Medium | Large scale Solar PV | REZ_V2_Solar | Large scale Solar PV | Large scale Solar PV | Murray River | Large scale Solar PV | Murray River | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | VIC | VIC | Western Victoria | New Entrant | VIC Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | VIC Medium | VIC Medium | Large scale Solar PV | REZ_V3_Solar | Large scale Solar PV | Large scale Solar PV | Western Victoria | Large scale Solar PV | Western Victoria | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | VIC | VIC | South West Victoria | New Entrant | VIC Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | VIC Medium | VIC Medium | Large scale Solar PV | REZ_V4_Solar | Large scale Solar PV | Large scale Solar PV | South West Victoria | Large scale Solar PV | South West Victoria | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | VIC | VIC | Gippsland | New Entrant | VIC Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | VIC Low | VIC Low | Large scale Solar PV | REZ_V5_Solar | Large scale Solar PV | Large scale Solar PV | Gippsland | Large scale Solar PV | Gippsland | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | VIC | VIC | Central North Vic | New Entrant | VIC High | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | VIC High | VIC High | Large scale Solar PV | REZ_V6_Solar | Large scale Solar PV | Large scale Solar PV | Central North Victoria | Large scale Solar PV | Central North Vic | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | SA | SESA | South East SA | New Entrant | SA Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | SA Low | SA Low | Large scale Solar PV | REZ_S1_Solar | Large scale Solar PV | Large scale Solar PV | South East South Australia | Large scale Solar PV | South East SA | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | SA | CSA | Riverland | New Entrant | SA Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | SA Low | SA Low | Large scale Solar PV | REZ_S2_Solar | Large scale Solar PV | Large scale Solar PV | Riverland | Large scale Solar PV | Riverland | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | SA | CSA | Mid-North SA | New Entrant | SA Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | SA Low | SA Low | Large scale Solar PV | REZ_S3_Solar | Large scale Solar PV | Large scale Solar PV | Mid-North South Australia | Large scale Solar PV | Mid-North SA | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | SA | CSA | Yorke Peninsula | New Entrant | SA Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | SA Low | SA Low | Large scale Solar PV | REZ_S4_Solar | Large scale Solar PV | Large scale Solar PV | Yorke Peninsula | Large scale Solar PV | Yorke Peninsula | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | SA | CSA | Northern SA | New Entrant | SA Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | SA Medium | SA Medium | Large scale Solar PV | REZ_S5_Solar | Large scale Solar PV | Large scale Solar PV | Northern South Australia | Large scale Solar PV | Northern SA | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | SA | CSA | Leigh Creek | New Entrant | SA Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | SA Medium | SA Medium | Large scale Solar PV | REZ_S6_Solar | Large scale Solar PV | Large scale Solar PV | Leigh Creek | Large scale Solar PV | Leigh Creek | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | SA | CSA | Roxby Downs | New Entrant | SA Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | SA Medium | SA Medium | Large scale Solar PV | REZ_S7_Solar | Large scale Solar PV | Large scale Solar PV | Roxby Downs | Large scale Solar PV | Roxby Downs | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | SA | CSA | Eastern Eyre Peninsula | New Entrant | SA Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | SA Medium | SA Medium | Large scale Solar PV | REZ_S8_Solar | Large scale Solar PV | Large scale Solar PV | Eastern Eyre Peninsula | Large scale Solar PV | Eastern Eyre Peninsula | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | SA | CSA | Western Eyre Peninsula | New Entrant | SA Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | SA Medium | SA Medium | Large scale Solar PV | REZ_S9_Solar | Large scale Solar PV | Large scale Solar PV | Western Eyre Peninsula | Large scale Solar PV | Western Eyre Peninsula | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | TAS | TAS | North East Tasmania | New Entrant | TAS Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | TAS Low | TAS Low | Large scale Solar PV | REZ_T1_Solar | Large scale Solar PV | Large scale Solar PV | North East Tasmania | Large scale Solar PV | North East Tasmania | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | TAS | TAS | North West Tasmania | New Entrant | TAS Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | TAS Medium | TAS Medium | Large scale Solar PV | REZ_T2_Solar | Large scale Solar PV | Large scale Solar PV | North West Tasmania | Large scale Solar PV | North West Tasmania | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | TAS | TAS | Central Highlands | New Entrant | TAS Low | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | TAS Low | TAS Low | Large scale Solar PV | REZ_T3_Solar | Large scale Solar PV | Large scale Solar PV | Central Highlands | Large scale Solar PV | Central Highlands | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | NSW | CNSW | New South Wales Non-REZ | New Entrant | NSW Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | NSW Medium | NSW Medium | Large scale Solar PV | N0_Solar | Large scale Solar PV | Large scale Solar PV | New South Wales Non-REZ | Large scale Solar PV | New South Wales Non-REZ | Large scale Solar PV
Large scale Solar PV | Large scale Solar PV | VIC | VIC | Victoria Non-REZ | New Entrant | VIC Medium | Solar | Solar | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV | Large scale Solar PV |  |  | VIC Medium | VIC Medium | Large scale Solar PV | V0_Solar | Large scale Solar PV | Large scale Solar PV | Victoria Non-REZ | Large scale Solar PV | Victoria Non-REZ | Large scale Solar PV
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | QLD | NQ | Far North QLD | New Entrant | QLD Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | QLD Low | QLD Low | Solar Thermal (15hrs storage) | REZ_Q1_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Far North Queensland | Solar Thermal (15hrs storage) | Far North QLD | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | QLD | NQ | North Qld Clean Energy Hub | New Entrant | QLD Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | QLD Low | QLD Low | Solar Thermal (15hrs storage) | REZ_Q2_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | North Queensland Clean Energy Hub | Solar Thermal (15hrs storage) | North Qld Clean Energy Hub | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | QLD | NQ | Northern Qld | New Entrant | QLD Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | QLD Low | QLD Low | Solar Thermal (15hrs storage) | REZ_Q3_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Northern Queensland | Solar Thermal (15hrs storage) | Northern Qld | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | QLD | CQ | Isaac | New Entrant | QLD Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | QLD Low | QLD Low | Solar Thermal (15hrs storage) | REZ_Q4_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Isaac | Solar Thermal (15hrs storage) | Isaac | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | QLD | CQ | Barcaldine | New Entrant | QLD Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | QLD Medium | QLD Medium | Solar Thermal (15hrs storage) | REZ_Q5_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Barcaldine | Solar Thermal (15hrs storage) | Barcaldine | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | QLD | CQ | Fitzroy | New Entrant | QLD Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | QLD Low | QLD Low | Solar Thermal (15hrs storage) | REZ_Q6_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Fitzroy | Solar Thermal (15hrs storage) | Fitzroy | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | QLD | SQ | Wide Bay | New Entrant | QLD Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | QLD Low | QLD Low | Solar Thermal (15hrs storage) | REZ_Q7_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Wide Bay | Solar Thermal (15hrs storage) | Wide Bay | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | QLD | SQ | Darling Downs | New Entrant | QLD Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | QLD Low | QLD Low | Solar Thermal (15hrs storage) | REZ_Q8_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Darling Downs | Solar Thermal (15hrs storage) | Darling Downs | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | QLD | SQ | Banana | New Entrant | QLD Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | QLD Medium | QLD Medium | Solar Thermal (15hrs storage) | REZ_Q9_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Banana | Solar Thermal (15hrs storage) | Banana | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | NNSW | North West NSW | New Entrant | NSW Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW Medium | NSW Medium | Solar Thermal (15hrs storage) | REZ_N1_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | North West New South Wales | Solar Thermal (15hrs storage) | North West NSW | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | NNSW | New England | New Entrant | NSW Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW Low | NSW Low | Solar Thermal (15hrs storage) | REZ_N2_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | New England | Solar Thermal (15hrs storage) | New England | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | CNSW | Central-West Orana | New Entrant | NSW Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW Medium | NSW Medium | Solar Thermal (15hrs storage) | REZ_N3_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Central-West Orana | Solar Thermal (15hrs storage) | Central-West Orana | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | SNSW | Broken Hill | New Entrant | NSW High | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW High | NSW High | Solar Thermal (15hrs storage) | REZ_N4_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Broken Hill | Solar Thermal (15hrs storage) | Broken Hill | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | SNSW | South West NSW | New Entrant | NSW High | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW High | NSW High | Solar Thermal (15hrs storage) | REZ_N5_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | South West New South Wales | Solar Thermal (15hrs storage) | South West NSW | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | SNSW | Wagga Wagga | New Entrant | NSW Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW Medium | NSW Medium | Solar Thermal (15hrs storage) | REZ_N6_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Wagga Wagga | Solar Thermal (15hrs storage) | Wagga Wagga | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | SNSW | Tumut | New Entrant | NSW Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW Medium | NSW Medium | Solar Thermal (15hrs storage) | REZ_N7_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Tumut | Solar Thermal (15hrs storage) | Tumut | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | SNSW | Cooma-Monaro | New Entrant | NSW Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW Medium | NSW Medium | Solar Thermal (15hrs storage) | REZ_N8_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Cooma-Monaro | Solar Thermal (15hrs storage) | Cooma-Monaro | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | CNSW | Hunter-Central Coast | New Entrant | NSW Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW Low | NSW Low | Solar Thermal (15hrs storage) | REZ_N9_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Hunter-Central Coast | Solar Thermal (15hrs storage) | Hunter-Central Coast | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | SNW | Illawarra | New Entrant | NSW Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW Low | NSW Low | Solar Thermal (15hrs storage) | REZ_N12_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Illawarra | Solar Thermal (15hrs storage) | Illawarra | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | VIC | VIC | Ovens Murray | New Entrant | VIC Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | VIC Medium | VIC Medium | Solar Thermal (15hrs storage) | REZ_V1_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Ovens Murray | Solar Thermal (15hrs storage) | Ovens Murray | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | VIC | VIC | Murray River | New Entrant | VIC Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | VIC Medium | VIC Medium | Solar Thermal (15hrs storage) | REZ_V2_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Murray River | Solar Thermal (15hrs storage) | Murray River | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | VIC | VIC | Western Victoria | New Entrant | VIC Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | VIC Medium | VIC Medium | Solar Thermal (15hrs storage) | REZ_V3_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Western Victoria | Solar Thermal (15hrs storage) | Western Victoria | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | VIC | VIC | South West Victoria | New Entrant | VIC Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | VIC Medium | VIC Medium | Solar Thermal (15hrs storage) | REZ_V4_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | South West Victoria | Solar Thermal (15hrs storage) | South West Victoria | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | VIC | VIC | Gippsland | New Entrant | VIC Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | VIC Low | VIC Low | Solar Thermal (15hrs storage) | REZ_V5_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Gippsland | Solar Thermal (15hrs storage) | Gippsland | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | VIC | VIC | Central North Vic | New Entrant | VIC High | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | VIC High | VIC High | Solar Thermal (15hrs storage) | REZ_V6_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Central North Victoria | Solar Thermal (15hrs storage) | Central North Vic | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | SA | SESA | South East SA | New Entrant | SA Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | SA Low | SA Low | Solar Thermal (15hrs storage) | REZ_S1_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | South East South Australia | Solar Thermal (15hrs storage) | South East SA | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | SA | CSA | Riverland | New Entrant | SA Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | SA Low | SA Low | Solar Thermal (15hrs storage) | REZ_S2_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Riverland | Solar Thermal (15hrs storage) | Riverland | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | SA | CSA | Mid-North SA | New Entrant | SA Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | SA Low | SA Low | Solar Thermal (15hrs storage) | REZ_S3_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Mid-North South Australia | Solar Thermal (15hrs storage) | Mid-North SA | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | SA | CSA | Yorke Peninsula | New Entrant | SA Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | SA Low | SA Low | Solar Thermal (15hrs storage) | REZ_S4_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Yorke Peninsula | Solar Thermal (15hrs storage) | Yorke Peninsula | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | SA | CSA | Northern SA | New Entrant | SA Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | SA Medium | SA Medium | Solar Thermal (15hrs storage) | REZ_S5_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Northern South Australia | Solar Thermal (15hrs storage) | Northern SA | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | SA | CSA | Leigh Creek | New Entrant | SA Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | SA Medium | SA Medium | Solar Thermal (15hrs storage) | REZ_S6_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Leigh Creek | Solar Thermal (15hrs storage) | Leigh Creek | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | SA | CSA | Roxby Downs | New Entrant | SA Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | SA Medium | SA Medium | Solar Thermal (15hrs storage) | REZ_S7_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Roxby Downs | Solar Thermal (15hrs storage) | Roxby Downs | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | SA | CSA | Eastern Eyre Peninsula | New Entrant | SA Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | SA Medium | SA Medium | Solar Thermal (15hrs storage) | REZ_S8_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Eastern Eyre Peninsula | Solar Thermal (15hrs storage) | Eastern Eyre Peninsula | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | SA | CSA | Western Eyre Peninsula | New Entrant | SA Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | SA Medium | SA Medium | Solar Thermal (15hrs storage) | REZ_S9_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Western Eyre Peninsula | Solar Thermal (15hrs storage) | Western Eyre Peninsula | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | TAS | TAS | North East Tasmania | New Entrant | TAS Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | TAS Low | TAS Low | Solar Thermal (15hrs storage) | REZ_T1_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | North East Tasmania | Solar Thermal (15hrs storage) | North East Tasmania | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | TAS | TAS | North West Tasmania | New Entrant | TAS Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | TAS Medium | TAS Medium | Solar Thermal (15hrs storage) | REZ_T2_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | North West Tasmania | Solar Thermal (15hrs storage) | North West Tasmania | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | TAS | TAS | Central Highlands | New Entrant | TAS Low | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | TAS Low | TAS Low | Solar Thermal (15hrs storage) | REZ_T3_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Central Highlands | Solar Thermal (15hrs storage) | Central Highlands | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | NSW | CNSW | New South Wales Non-REZ | New Entrant | NSW Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | NSW Medium | NSW Medium | Solar Thermal (15hrs storage) | N0_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | New South Wales Non-REZ | Solar Thermal (15hrs storage) | New South Wales Non-REZ | Solar Thermal (15hrs storage)
Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | VIC | VIC | Victoria Non-REZ | New Entrant | VIC Medium | Solar | Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) |  |  | VIC Medium | VIC Medium | Solar Thermal (15hrs storage) | V0_Solar | Solar Thermal (15hrs storage) | Solar Thermal (15hrs storage) | Victoria Non-REZ | Solar Thermal (15hrs storage) | Victoria Non-REZ | Solar Thermal (15hrs storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | QLD | NQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | QLD Low | QLD Low | Battery Storage (1hr storage) | NE_NQ | Battery Storage (1hr storage) | 1 hr Battery Storage | QLD | Battery Storage (1hr storage) | QLD | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | QLD | CQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | QLD Low | QLD Low | Battery Storage (1hr storage) | NE_CQ | Battery Storage (1hr storage) | 1 hr Battery Storage | QLD | Battery Storage (1hr storage) | QLD | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | QLD | GG | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | QLD Low | QLD Low | Battery Storage (1hr storage) | NE_GG | Battery Storage (1hr storage) | 1 hr Battery Storage | QLD | Battery Storage (1hr storage) | QLD | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | QLD | SQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | QLD Low | QLD Low | Battery Storage (1hr storage) | NE_SQ | Battery Storage (1hr storage) | 1 hr Battery Storage | QLD | Battery Storage (1hr storage) | QLD | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | NSW | NNSW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | NSW Low | NSW Low | Battery Storage (1hr storage) | NE_NNSW | Battery Storage (1hr storage) | 1 hr Battery Storage | NSW | Battery Storage (1hr storage) | NSW | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | NSW | CNSW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | NSW Low | NSW Low | Battery Storage (1hr storage) | NE_CNSW | Battery Storage (1hr storage) | 1 hr Battery Storage | NSW | Battery Storage (1hr storage) | NSW | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | NSW | SNW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | NSW Low | NSW Low | Battery Storage (1hr storage) | NE_SNW | Battery Storage (1hr storage) | 1 hr Battery Storage | NSW | Battery Storage (1hr storage) | NSW | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | NSW | SNSW | N/A | New Entrant | NSW Medium | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | NSW Medium | NSW Medium | Battery Storage (1hr storage) | NE_SNSW | Battery Storage (1hr storage) | 1 hr Battery Storage | NSW | Battery Storage (1hr storage) | NSW | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | VIC | VIC | N/A | New Entrant | VIC Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | VIC Low | VIC Low | Battery Storage (1hr storage) | NE_VIC1 | Battery Storage (1hr storage) | 1 hr Battery Storage | VIC | Battery Storage (1hr storage) | VIC | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | SA | CSA | N/A | New Entrant | SA Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | SA Low | SA Low | Battery Storage (1hr storage) | NE_CSA | Battery Storage (1hr storage) | 1 hr Battery Storage | SA | Battery Storage (1hr storage) | SA | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | SA | SESA | N/A | New Entrant | SA Medium | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | SA Medium | SA Medium | Battery Storage (1hr storage) | NE_SESA | Battery Storage (1hr storage) | 1 hr Battery Storage | SA | Battery Storage (1hr storage) | SA | Battery Storage (1hr storage)
Battery Storage (1hr storage) | Battery Storage (1hr storage) | TAS | TAS | N/A | New Entrant | TAS Low | Battery | Battery | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) | Battery Storage (1hr storage) |  |  | TAS Low | TAS Low | Battery Storage (1hr storage) | NE_TAS1 | Battery Storage (1hr storage) | 1 hr Battery Storage | TAS | Battery Storage (1hr storage) | TAS | Battery Storage (1hr storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | QLD | NQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (2hrs storage) | NE_NQ | Battery Storage (2hrs storage) | 2 hr Battery Storage | QLD | Battery Storage (2hrs storage) | QLD | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | QLD | CQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (2hrs storage) | NE_CQ | Battery Storage (2hrs storage) | 2 hr Battery Storage | QLD | Battery Storage (2hrs storage) | QLD | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | QLD | GG | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (2hrs storage) | NE_GG | Battery Storage (2hrs storage) | 2 hr Battery Storage | QLD | Battery Storage (2hrs storage) | QLD | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | QLD | SQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (2hrs storage) | NE_SQ | Battery Storage (2hrs storage) | 2 hr Battery Storage | QLD | Battery Storage (2hrs storage) | QLD | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NSW | NNSW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | NSW Low | NSW Low | Battery Storage (2hrs storage) | NE_NNSW | Battery Storage (2hrs storage) | 2 hr Battery Storage | NSW | Battery Storage (2hrs storage) | NSW | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NSW | CNSW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | NSW Low | NSW Low | Battery Storage (2hrs storage) | NE_CNSW | Battery Storage (2hrs storage) | 2 hr Battery Storage | NSW | Battery Storage (2hrs storage) | NSW | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NSW | SNW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | NSW Low | NSW Low | Battery Storage (2hrs storage) | NE_SNW | Battery Storage (2hrs storage) | 2 hr Battery Storage | NSW | Battery Storage (2hrs storage) | NSW | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | NSW | SNSW | N/A | New Entrant | NSW Medium | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | NSW Medium | NSW Medium | Battery Storage (2hrs storage) | NE_SNSW | Battery Storage (2hrs storage) | 2 hr Battery Storage | NSW | Battery Storage (2hrs storage) | NSW | Battery Storage (2hrs storage)
Battery storage (2hrs storage) | Battery Storage (2hrs storage) | VIC | VIC | N/A | New Entrant | VIC Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | VIC Low | VIC Low | Battery Storage (2hrs storage) | NE_VIC1 | Battery Storage (2hrs storage) | 2 hr Battery Storage | VIC | Battery Storage (2hrs storage) | VIC | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | SA | CSA | N/A | New Entrant | SA Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | SA Low | SA Low | Battery Storage (2hrs storage) | NE_CSA | Battery Storage (2hrs storage) | 2 hr Battery Storage | SA | Battery Storage (2hrs storage) | SA | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | SA | SESA | N/A | New Entrant | SA Medium | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | SA Medium | SA Medium | Battery Storage (2hrs storage) | NE_SESA | Battery Storage (2hrs storage) | 2 hr Battery Storage | SA | Battery Storage (2hrs storage) | SA | Battery Storage (2hrs storage)
Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | TAS | TAS | N/A | New Entrant | TAS Low | Battery | Battery | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) | Battery Storage (2hrs storage) |  |  | TAS Low | TAS Low | Battery Storage (2hrs storage) | NE_TAS1 | Battery Storage (2hrs storage) | 2 hr Battery Storage | TAS | Battery Storage (2hrs storage) | TAS | Battery Storage (2hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | QLD | NQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (4hrs storage) | NE_NQ | Battery Storage (4hrs storage) | 4 hr Battery Storage | QLD | Battery Storage (4hrs storage) | QLD | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | QLD | CQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (4hrs storage) | NE_CQ | Battery Storage (4hrs storage) | 4 hr Battery Storage | QLD | Battery Storage (4hrs storage) | QLD | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | QLD | GG | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (4hrs storage) | NE_GG | Battery Storage (4hrs storage) | 4 hr Battery Storage | QLD | Battery Storage (4hrs storage) | QLD | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | QLD | SQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (4hrs storage) | NE_SQ | Battery Storage (4hrs storage) | 4 hr Battery Storage | QLD | Battery Storage (4hrs storage) | QLD | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NSW | NNSW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | NSW Low | NSW Low | Battery Storage (4hrs storage) | NE_NNSW | Battery Storage (4hrs storage) | 4 hr Battery Storage | NSW | Battery Storage (4hrs storage) | NSW | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NSW | CNSW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | NSW Low | NSW Low | Battery Storage (4hrs storage) | NE_CNSW | Battery Storage (4hrs storage) | 4 hr Battery Storage | NSW | Battery Storage (4hrs storage) | NSW | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NSW | SNW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | NSW Low | NSW Low | Battery Storage (4hrs storage) | NE_SNW | Battery Storage (4hrs storage) | 4 hr Battery Storage | NSW | Battery Storage (4hrs storage) | NSW | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | NSW | SNSW | N/A | New Entrant | NSW Medium | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | NSW Medium | NSW Medium | Battery Storage (4hrs storage) | NE_SNSW | Battery Storage (4hrs storage) | 4 hr Battery Storage | NSW | Battery Storage (4hrs storage) | NSW | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | VIC | VIC | N/A | New Entrant | VIC Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | VIC Low | VIC Low | Battery Storage (4hrs storage) | NE_VIC1 | Battery Storage (4hrs storage) | 4 hr Battery Storage | VIC | Battery Storage (4hrs storage) | VIC | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | SA | CSA | N/A | New Entrant | SA Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | SA Low | SA Low | Battery Storage (4hrs storage) | NE_CSA | Battery Storage (4hrs storage) | 4 hr Battery Storage | SA | Battery Storage (4hrs storage) | SA | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | SA | SESA | N/A | New Entrant | SA Medium | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | SA Medium | SA Medium | Battery Storage (4hrs storage) | NE_SESA | Battery Storage (4hrs storage) | 4 hr Battery Storage | SA | Battery Storage (4hrs storage) | SA | Battery Storage (4hrs storage)
Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | TAS | TAS | N/A | New Entrant | TAS Low | Battery | Battery | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) | Battery Storage (4hrs storage) |  |  | TAS Low | TAS Low | Battery Storage (4hrs storage) | NE_TAS1 | Battery Storage (4hrs storage) | 4 hr Battery Storage | TAS | Battery Storage (4hrs storage) | TAS | Battery Storage (4hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | QLD | NQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (8hrs storage) | NE_NQ | Battery Storage (8hrs storage) | 8 hr Battery Storage | QLD | Battery Storage (8hrs storage) | QLD | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | QLD | CQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (8hrs storage) | NE_CQ | Battery Storage (8hrs storage) | 8 hr Battery Storage | QLD | Battery Storage (8hrs storage) | QLD | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | QLD | GG | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (8hrs storage) | NE_GG | Battery Storage (8hrs storage) | 8 hr Battery Storage | QLD | Battery Storage (8hrs storage) | QLD | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | QLD | SQ | N/A | New Entrant | QLD Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | QLD Low | QLD Low | Battery Storage (8hrs storage) | NE_SQ | Battery Storage (8hrs storage) | 8 hr Battery Storage | QLD | Battery Storage (8hrs storage) | QLD | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | NSW | NNSW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | NSW Low | NSW Low | Battery Storage (8hrs storage) | NE_NNSW | Battery Storage (8hrs storage) | 8 hr Battery Storage | NSW | Battery Storage (8hrs storage) | NSW | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | NSW | CNSW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | NSW Low | NSW Low | Battery Storage (8hrs storage) | NE_CNSW | Battery Storage (8hrs storage) | 8 hr Battery Storage | NSW | Battery Storage (8hrs storage) | NSW | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | NSW | SNW | N/A | New Entrant | NSW Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | NSW Low | NSW Low | Battery Storage (8hrs storage) | NE_SNW | Battery Storage (8hrs storage) | 8 hr Battery Storage | NSW | Battery Storage (8hrs storage) | NSW | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | NSW | SNSW | N/A | New Entrant | NSW Medium | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | NSW Medium | NSW Medium | Battery Storage (8hrs storage) | NE_SNSW | Battery Storage (8hrs storage) | 8 hr Battery Storage | NSW | Battery Storage (8hrs storage) | NSW | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | VIC | VIC | N/A | New Entrant | VIC Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | VIC Low | VIC Low | Battery Storage (8hrs storage) | NE_VIC1 | Battery Storage (8hrs storage) | 8 hr Battery Storage | VIC | Battery Storage (8hrs storage) | VIC | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | SA | CSA | N/A | New Entrant | SA Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | SA Low | SA Low | Battery Storage (8hrs storage) | NE_CSA | Battery Storage (8hrs storage) | 8 hr Battery Storage | SA | Battery Storage (8hrs storage) | SA | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | SA | SESA | N/A | New Entrant | SA Medium | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | SA Medium | SA Medium | Battery Storage (8hrs storage) | NE_SESA | Battery Storage (8hrs storage) | 8 hr Battery Storage | SA | Battery Storage (8hrs storage) | SA | Battery Storage (8hrs storage)
Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | TAS | TAS | N/A | New Entrant | TAS Low | Battery | Battery | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) | Battery Storage (8hrs storage) |  |  | TAS Low | TAS Low | Battery Storage (8hrs storage) | NE_TAS1 | Battery Storage (8hrs storage) | 8 hr Battery Storage | TAS | Battery Storage (8hrs storage) | TAS | Battery Storage (8hrs storage)
Wind | Wind | QLD | NQ | Far North QLD | New Entrant | QLD Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | QLD Low | QLD Low | Wind | REZ_Q1_Wind | Wind | Wind | Far North Queensland | Wind | Far North QLD | Wind
Wind | Wind | QLD | NQ | North Qld Clean Energy Hub | New Entrant | QLD Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | QLD Low | QLD Low | Wind | REZ_Q2_Wind | Wind | Wind | North Queensland Clean Energy Hub | Wind | North Qld Clean Energy Hub | Wind
Wind | Wind | QLD | NQ | Northern Qld | New Entrant | QLD Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | QLD Low | QLD Low | Wind | REZ_Q3_Wind | Wind | Wind | Northern Queensland | Wind | Northern Qld | Wind
Wind | Wind | QLD | CQ | Isaac | New Entrant | QLD Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | QLD Low | QLD Low | Wind | REZ_Q4_Wind | Wind | Wind | Isaac | Wind | Isaac | Wind
Wind | Wind | QLD | CQ | Barcaldine | New Entrant | QLD Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | QLD Medium | QLD Medium | Wind | REZ_Q5_Wind | Wind | Wind | Barcaldine | Wind | Barcaldine | Wind
Wind | Wind | QLD | CQ | Fitzroy | New Entrant | QLD Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | QLD Low | QLD Low | Wind | REZ_Q6_Wind | Wind | Wind | Fitzroy | Wind | Fitzroy | Wind
Wind | Wind | QLD | SQ | Wide Bay | New Entrant | QLD Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | QLD Low | QLD Low | Wind | REZ_Q7_Wind | Wind | Wind | Wide Bay | Wind | Wide Bay | Wind
Wind | Wind | QLD | SQ | Darling Downs | New Entrant | QLD Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | QLD Low | QLD Low | Wind | REZ_Q8_Wind | Wind | Wind | Darling Downs | Wind | Darling Downs | Wind
Wind | Wind | QLD | SQ | Banana | New Entrant | QLD Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | QLD Medium | QLD Medium | Wind | REZ_Q9_Wind | Wind | Wind | Banana | Wind | Banana | Wind
Wind | Wind | NSW | NNSW | North West NSW | New Entrant | NSW Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW Medium | NSW Medium | Wind | REZ_N1_Wind | Wind | Wind | North West New South Wales | Wind | North West NSW | Wind
Wind | Wind | NSW | NNSW | New England | New Entrant | NSW Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW Low | NSW Low | Wind | REZ_N2_Wind | Wind | Wind | New England | Wind | New England | Wind
Wind | Wind | NSW | CNSW | Central-West Orana | New Entrant | NSW Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW Medium | NSW Medium | Wind | REZ_N3_Wind | Wind | Wind | Central-West Orana | Wind | Central-West Orana | Wind
Wind | Wind | NSW | SNSW | Broken Hill | New Entrant | NSW High | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW High | NSW High | Wind | REZ_N4_Wind | Wind | Wind | Broken Hill | Wind | Broken Hill | Wind
Wind | Wind | NSW | SNSW | South West NSW | New Entrant | NSW High | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW High | NSW High | Wind | REZ_N5_Wind | Wind | Wind | South West New South Wales | Wind | South West NSW | Wind
Wind | Wind | NSW | SNSW | Wagga Wagga | New Entrant | NSW Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW Medium | NSW Medium | Wind | REZ_N6_Wind | Wind | Wind | Wagga Wagga | Wind | Wagga Wagga | Wind
Wind | Wind | NSW | SNSW | Tumut | New Entrant | NSW Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW Medium | NSW Medium | Wind | REZ_N7_Wind | Wind | Wind | Tumut | Wind | Tumut | Wind
Wind | Wind | NSW | SNSW | Cooma-Monaro | New Entrant | NSW Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW Medium | NSW Medium | Wind | REZ_N8_Wind | Wind | Wind | Cooma-Monaro | Wind | Cooma-Monaro | Wind
Wind | Wind | NSW | CNSW | Hunter-Central Coast | New Entrant | NSW Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW Low | NSW Low | Wind | REZ_N9_Wind | Wind | Wind | Hunter-Central Coast | Wind | Hunter-Central Coast | Wind
Wind | Wind | NSW | SNW | Illawarra | New Entrant | NSW Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW Low | NSW Low | Wind | REZ_N12_Wind | Wind | Wind | Illawarra | Wind | Illawarra | Wind
Wind | Wind | VIC | VIC | Ovens Murray | New Entrant | VIC Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | VIC Medium | VIC Medium | Wind | REZ_V1_Wind | Wind | Wind | Ovens Murray | Wind | Ovens Murray | Wind
Wind | Wind | VIC | VIC | Murray River | New Entrant | VIC Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | VIC Medium | VIC Medium | Wind | REZ_V2_Wind | Wind | Wind | Murray River | Wind | Murray River | Wind
Wind | Wind | VIC | VIC | Western Victoria | New Entrant | VIC Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | VIC Medium | VIC Medium | Wind | REZ_V3_Wind | Wind | Wind | Western Victoria | Wind | Western Victoria | Wind
Wind | Wind | VIC | VIC | South West Victoria | New Entrant | VIC Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | VIC Medium | VIC Medium | Wind | REZ_V4_Wind | Wind | Wind | South West Victoria | Wind | South West Victoria | Wind
Wind | Wind | VIC | VIC | Gippsland | New Entrant | VIC Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | VIC Low | VIC Low | Wind | REZ_V5_Wind | Wind | Wind | Gippsland | Wind | Gippsland | Wind
Wind | Wind | VIC | VIC | Central North Vic | New Entrant | VIC High | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | VIC High | VIC High | Wind | REZ_V6_Wind | Wind | Wind | Central North Victoria | Wind | Central North Vic | Wind
Wind | Wind | SA | SESA | South East SA | New Entrant | SA Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | SA Low | SA Low | Wind | REZ_S1_Wind | Wind | Wind | South East South Australia | Wind | South East SA | Wind
Wind | Wind | SA | CSA | Riverland | New Entrant | SA Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | SA Low | SA Low | Wind | REZ_S2_Wind | Wind | Wind | Riverland | Wind | Riverland | Wind
Wind | Wind | SA | CSA | Mid-North SA | New Entrant | SA Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | SA Low | SA Low | Wind | REZ_S3_Wind | Wind | Wind | Mid-North South Australia | Wind | Mid-North SA | Wind
Wind | Wind | SA | CSA | Yorke Peninsula | New Entrant | SA Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | SA Low | SA Low | Wind | REZ_S4_Wind | Wind | Wind | Yorke Peninsula | Wind | Yorke Peninsula | Wind
Wind | Wind | SA | CSA | Northern SA | New Entrant | SA Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | SA Medium | SA Medium | Wind | REZ_S5_Wind | Wind | Wind | Northern South Australia | Wind | Northern SA | Wind
Wind | Wind | SA | CSA | Leigh Creek | New Entrant | SA Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | SA Medium | SA Medium | Wind | REZ_S6_Wind | Wind | Wind | Leigh Creek | Wind | Leigh Creek | Wind
Wind | Wind | SA | CSA | Roxby Downs | New Entrant | SA Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | SA Medium | SA Medium | Wind | REZ_S7_Wind | Wind | Wind | Roxby Downs | Wind | Roxby Downs | Wind
Wind | Wind | SA | CSA | Eastern Eyre Peninsula | New Entrant | SA Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | SA Medium | SA Medium | Wind | REZ_S8_Wind | Wind | Wind | Eastern Eyre Peninsula | Wind | Eastern Eyre Peninsula | Wind
Wind | Wind | SA | CSA | Western Eyre Peninsula | New Entrant | SA Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | SA Medium | SA Medium | Wind | REZ_S9_Wind | Wind | Wind | Western Eyre Peninsula | Wind | Western Eyre Peninsula | Wind
Wind | Wind | TAS | TAS | North East Tasmania | New Entrant | TAS Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | TAS Low | TAS Low | Wind | REZ_T1_Wind | Wind | Wind | North East Tasmania | Wind | North East Tasmania | Wind
Wind | Wind | TAS | TAS | North West Tasmania | New Entrant | TAS Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | TAS Medium | TAS Medium | Wind | REZ_T2_Wind | Wind | Wind | North West Tasmania | Wind | North West Tasmania | Wind
Wind | Wind | TAS | TAS | Central Highlands | New Entrant | TAS Low | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | TAS Low | TAS Low | Wind | REZ_T3_Wind | Wind | Wind | Central Highlands | Wind | Central Highlands | Wind
Wind | Wind | NSW | CNSW | New South Wales Non-REZ | New Entrant | NSW Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | NSW Medium | NSW Medium | Wind | N0_Wind | Wind | Wind | New South Wales Non-REZ | Wind | New South Wales Non-REZ | Wind
Wind | Wind | VIC | VIC | Victoria Non-REZ | New Entrant | VIC Medium | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind | Wind |  |  | VIC Medium | VIC Medium | Wind | V0_Wind | Wind | Wind | Victoria Non-REZ | Wind | Victoria Non-REZ | Wind
Wind - offshore (fixed) | Wind | NSW | SNW | Hunter Coast | New Entrant | NSW Low | Wind | Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) |  |  | NSW Low | NSW Low | Wind - offshore (fixed) | REZ_N10_Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Hunter Coast | Wind - offshore (fixed) | Hunter Coast | Wind - offshore (fixed)
Wind - offshore (fixed) | Wind | NSW | SNW | Illawarra Coast | New Entrant | NSW Low | Wind | Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) |  |  | NSW Low | NSW Low | Wind - offshore (fixed) | REZ_N11_Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Illawarra Coast | Wind - offshore (fixed) | Illawarra Coast | Wind - offshore (fixed)
Wind - offshore (fixed) | Wind | VIC | VIC | Gippsland Coast | New Entrant | VIC Low | Wind | Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) |  |  | VIC Low | VIC Low | Wind - offshore (fixed) | REZ_V7_Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Gippsland Coast | Wind - offshore (fixed) | Gippsland Coast | Wind - offshore (fixed)
Wind - offshore (fixed) | Wind | VIC | VIC | Portland Coast | New Entrant | VIC Low | Wind | Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) |  |  | VIC Low | VIC Low | Wind - offshore (fixed) | REZ_V8_Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Portland Coast | Wind - offshore (fixed) | Portland Coast | Wind - offshore (fixed)
Wind - offshore (fixed) | Wind | SA | SESA | South East SA Coast | New Entrant | SA Low | Wind | Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) |  |  | SA Low | SA Low | Wind - offshore (fixed) | REZ_S10_Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | South East South Australia Coast | Wind - offshore (fixed) | South East SA Coast | Wind - offshore (fixed)
Wind - offshore (fixed) | Wind | TAS | TAS | North West Tasmania Coast | New Entrant | TAS Low | Wind | Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) |  |  | TAS Low | TAS Low | Wind - offshore (fixed) | REZ_T4_Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | North-West Tasmania Coast | Wind - offshore (fixed) | North West Tasmania Coast | Wind - offshore (fixed)
Wind - offshore (fixed) | Wind | TAS | TAS | North East Tasmania Coast | New Entrant | TAS Low | Wind | Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) | Wind - offshore (fixed) |  |  | TAS Low | TAS Low | Wind - offshore (fixed) | REZ_T5_Wind | Wind - offshore (fixed) | Wind - offshore (fixed) | North-East Tasmania Coast | Wind - offshore (fixed) | North East Tasmania Coast | Wind - offshore (fixed)
Wind - offshore (floating) | Wind | NSW | SNW | Hunter Coast | New Entrant | NSW Low | Wind | Wind | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) |  |  | NSW Low | NSW Low | Wind - offshore (floating) | REZ_N10_Wind | Wind - offshore (floating) | Wind - offshore (floating) | Hunter Coast | Wind - offshore (floating) | Hunter Coast | Wind - offshore (floating)
Wind - offshore (floating) | Wind | NSW | SNW | Illawarra Coast | New Entrant | NSW Low | Wind | Wind | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) |  |  | NSW Low | NSW Low | Wind - offshore (floating) | REZ_N11_Wind | Wind - offshore (floating) | Wind - offshore (floating) | Illawarra Coast | Wind - offshore (floating) | Illawarra Coast | Wind - offshore (floating)
Wind - offshore (floating) | Wind | VIC | VIC | Gippsland Coast | New Entrant | VIC Low | Wind | Wind | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) |  |  | VIC Low | VIC Low | Wind - offshore (floating) | REZ_V7_Wind | Wind - offshore (floating) | Wind - offshore (floating) | Gippsland Coast | Wind - offshore (floating) | Gippsland Coast | Wind - offshore (floating)
Wind - offshore (floating) | Wind | VIC | VIC | Portland Coast | New Entrant | VIC Low | Wind | Wind | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) |  |  | VIC Low | VIC Low | Wind - offshore (floating) | REZ_V8_Wind | Wind - offshore (floating) | Wind - offshore (floating) | Portland Coast | Wind - offshore (floating) | Portland Coast | Wind - offshore (floating)
Wind - offshore (floating) | Wind | SA | SESA | South East SA Coast | New Entrant | SA Low | Wind | Wind | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) |  |  | SA Low | SA Low | Wind - offshore (floating) | REZ_S10_Wind | Wind - offshore (floating) | Wind - offshore (floating) | South East South Australia Coast | Wind - offshore (floating) | South East SA Coast | Wind - offshore (floating)
Wind - offshore (floating) | Wind | TAS | TAS | North West Tasmania Coast | New Entrant | TAS Low | Wind | Wind | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) |  |  | TAS Low | TAS Low | Wind - offshore (floating) | REZ_T4_Wind | Wind - offshore (floating) | Wind - offshore (floating) | North-West Tasmania Coast | Wind - offshore (floating) | North West Tasmania Coast | Wind - offshore (floating)
Wind - offshore (floating) | Wind | TAS | TAS | North East Tasmania Coast | New Entrant | TAS Low | Wind | Wind | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) | Wind - offshore (floating) |  |  | TAS Low | TAS Low | Wind - offshore (floating) | REZ_T5_Wind | Wind - offshore (floating) | Wind - offshore (floating) | North-East Tasmania Coast | Wind - offshore (floating) | North East Tasmania Coast | Wind - offshore (floating)
Pumped Hydro (8hrs storage) | Pumped Hydro | QLD | NQ | N/A | New Entrant | NQ | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (8hrs storage) | NE_NQ | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | QLD | 8hr storage | QLD | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | QLD | CQ | N/A | New Entrant | CQ | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (8hrs storage) | NE_CQ | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | QLD | 8hr storage | QLD | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | QLD | GG | N/A | New Entrant | GG | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (8hrs storage) | NE_GG | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | QLD | 8hr storage | QLD | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | QLD | SQ | N/A | New Entrant | SQ | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (8hrs storage) | NE_SQ | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | QLD | 8hr storage | QLD | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | NSW | NNSW | N/A | New Entrant | NNSW | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (8hrs storage) | NE_NNSW | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | NSW | 8hr storage | NSW | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | NSW | CNSW | N/A | New Entrant | CNSW | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (8hrs storage) | NE_CNSW | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | NSW | 8hr storage | NSW | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | NSW | SNW | N/A | New Entrant | SNW | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (8hrs storage) | NE_SNW | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | NSW | 8hr storage | NSW | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | NSW | SNSW | N/A | New Entrant | SNSW | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (8hrs storage) | NE_SNSW | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | NSW | 8hr storage | NSW | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | VIC | VIC | N/A | New Entrant | VIC | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | VIC Low | VIC Low | Pumped Hydro (8hrs storage) | NE_VIC1 | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | VIC | 8hr storage | VIC | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | SA | CSA | N/A | New Entrant | CSA | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | SA Low | SA Low | Pumped Hydro (8hrs storage) | NE_CSA | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | SA | 8hr storage | SA | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | SA | SESA | N/A | New Entrant | SESA | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | SA Low | SA Low | Pumped Hydro (8hrs storage) | NE_SESA | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | SA | 8hr storage | SA | Pumped Hydro (8hrs storage)
Pumped Hydro (8hrs storage) | Pumped Hydro | TAS | TAS | N/A | New Entrant | TAS | Water | Hydro | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) | Pumped Hydro (8hrs storage) |  |  | TAS Low | TAS Low | Pumped Hydro (8hrs storage) | NE_TAS1 | Pumped Hydro (8hrs storage) | Pumped Hydro3 (8 hrs storage) | TAS | 8hr storage | TAS | Pumped Hydro (8hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | QLD | NQ | N/A | New Entrant | NQ | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (24hrs storage) | NE_NQ | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | QLD | 24hrs storage | QLD | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | QLD | CQ | N/A | New Entrant | CQ | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (24hrs storage) | NE_CQ | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | QLD | 24hrs storage | QLD | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | QLD | GG | N/A | New Entrant | GG | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (24hrs storage) | NE_GG | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | QLD | 24hrs storage | QLD | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | QLD | SQ | N/A | New Entrant | SQ | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (24hrs storage) | NE_SQ | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | QLD | 24hrs storage | QLD | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | NSW | NNSW | N/A | New Entrant | NNSW | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (24hrs storage) | NE_NNSW | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | NSW | 24hrs storage | NSW | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | NSW | CNSW | N/A | New Entrant | CNSW | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (24hrs storage) | NE_CNSW | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | NSW | 24hrs storage | NSW | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | NSW | SNW | N/A | New Entrant | SNW | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (24hrs storage) | NE_SNW | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | NSW | 24hrs storage | NSW | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | NSW | SNSW | N/A | New Entrant | SNSW | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (24hrs storage) | NE_SNSW | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | NSW | 24hrs storage | NSW | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | VIC | VIC | N/A | New Entrant | VIC | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | VIC Low | VIC Low | Pumped Hydro (24hrs storage) | NE_VIC1 | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | VIC | 24hrs storage | VIC | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | SA | CSA | N/A | New Entrant | CSA | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | SA Low | SA Low | Pumped Hydro (24hrs storage) | NE_CSA | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | SA | 24hrs storage | SA | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | SA | SESA | N/A | New Entrant | SESA | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | SA Low | SA Low | Pumped Hydro (24hrs storage) | NE_SESA | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | SA | 24hrs storage | SA | Pumped Hydro (24hrs storage)
Pumped Hydro (24hrs storage) | Pumped Hydro | TAS | TAS | N/A | New Entrant | TAS | Water | Hydro | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | TAS Low | TAS Low | Pumped Hydro (24hrs storage) | NE_TAS1 | Pumped Hydro (24hrs storage) | Pumped Hydro (24 hrs storage) | TAS | 24hrs storage | TAS | Pumped Hydro (24hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | QLD | NQ | N/A | New Entrant | NQ | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (48hrs storage) | NE_NQ | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | QLD | 48hrs storage | QLD | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | QLD | CQ | N/A | New Entrant | CQ | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (48hrs storage) | NE_CQ | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | QLD | 48hrs storage | QLD | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | QLD | GG | N/A | New Entrant | GG | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (48hrs storage) | NE_GG | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | QLD | 48hrs storage | QLD | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | QLD | SQ | N/A | New Entrant | SQ | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | QLD Low | QLD Low | Pumped Hydro (48hrs storage) | NE_SQ | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | QLD | 48hrs storage | QLD | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | NSW | NNSW | N/A | New Entrant | NNSW | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (48hrs storage) | NE_NNSW | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | NSW | 48hrs storage | NSW | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | NSW | CNSW | N/A | New Entrant | CNSW | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (48hrs storage) | NE_CNSW | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | NSW | 48hrs storage | NSW | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | NSW | SNW | N/A | New Entrant | SNW | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (48hrs storage) | NE_SNW | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | NSW | 48hrs storage | NSW | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | NSW | SNSW | N/A | New Entrant | SNSW | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | NSW Low | NSW Low | Pumped Hydro (48hrs storage) | NE_SNSW | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | NSW | 48hrs storage | NSW | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | VIC | VIC | N/A | New Entrant | VIC | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | VIC Low | VIC Low | Pumped Hydro (48hrs storage) | NE_VIC1 | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | VIC | 48hrs storage | VIC | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | SA | CSA | N/A | New Entrant | CSA | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | SA Low | SA Low | Pumped Hydro (48hrs storage) | NE_CSA | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | SA | 48hrs storage | SA | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | SA | SESA | N/A | New Entrant | SESA | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | SA Low | SA Low | Pumped Hydro (48hrs storage) | NE_SESA | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | SA | 48hrs storage | SA | Pumped Hydro (48hrs storage)
Pumped Hydro (48hrs storage) | Pumped Hydro | TAS | TAS | N/A | New Entrant | TAS | Water | Hydro | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) | Pumped Hydro (48hrs storage) |  |  | TAS Low | TAS Low | Pumped Hydro (48hrs storage) | NE_TAS1 | Pumped Hydro (48hrs storage) | Pumped Hydro (48 hrs storage) | TAS | 48hrs storage | TAS | Pumped Hydro (48hrs storage)
BOTN - Cethana | Pumped Hydro | TAS | TAS | N/A | New Entrant | TAS | Water | Hydro | BOTN - Cethana | BOTN - Cethana | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) | Pumped Hydro (24hrs storage) |  |  | TAS Medium | TAS Medium | Pumped Hydro (24hrs storage) | NE_TAS1 | Pumped Hydro (24hrs storage) | BOTN- Cethana | TAS | 24hrs storage | TAS | Pumped Hydro (24hrs storage)
Hydrogen reciprocating engines | Hydrogen reciprocating engines | QLD | NQ | N/A | New Entrant | QLD Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | QLD Low | QLD Low | Hydrogen reciprocating engines | NE_NQ | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | QLD | Hydrogen reciprocating engines | QLD | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | QLD | CQ | N/A | New Entrant | QLD Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | QLD Low | QLD Low | Hydrogen reciprocating engines | NE_CQ | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | QLD | Hydrogen reciprocating engines | QLD | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | QLD | GG | N/A | New Entrant | QLD Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | QLD Low | QLD Low | Hydrogen reciprocating engines | NE_GG | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | QLD | Hydrogen reciprocating engines | QLD | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | QLD | SQ | N/A | New Entrant | QLD Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | QLD Low | QLD Low | Hydrogen reciprocating engines | NE_SQ | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | QLD | Hydrogen reciprocating engines | QLD | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | NSW | NNSW | N/A | New Entrant | NSW Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | NSW Low | NSW Low | Hydrogen reciprocating engines | NE_NNSW | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | NSW | Hydrogen reciprocating engines | NSW | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | NSW | CNSW | N/A | New Entrant | NSW Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | NSW Low | NSW Low | Hydrogen reciprocating engines | NE_CNSW | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | NSW | Hydrogen reciprocating engines | NSW | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | NSW | SNW | N/A | New Entrant | NSW Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | NSW Low | NSW Low | Hydrogen reciprocating engines | NE_SNW | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | NSW | Hydrogen reciprocating engines | NSW | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | NSW | SNSW | N/A | New Entrant | NSW Medium | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | NSW Medium | NSW Medium | Hydrogen reciprocating engines | NE_SNSW | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | NSW | Hydrogen reciprocating engines | NSW | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | VIC | VIC | N/A | New Entrant | VIC Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | VIC Low | VIC Low | Hydrogen reciprocating engines | NE_VIC1 | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | VIC | Hydrogen reciprocating engines | VIC | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | SA | CSA | N/A | New Entrant | SA Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | SA Low | SA Low | Hydrogen reciprocating engines | NE_CSA | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | SA | Hydrogen reciprocating engines | SA | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | SA | SESA | N/A | New Entrant | SA Medium | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | SA Medium | SA Medium | Hydrogen reciprocating engines | NE_SESA | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | SA | Hydrogen reciprocating engines | SA | Hydrogen reciprocating engines
Hydrogen reciprocating engines | Hydrogen reciprocating engines | TAS | TAS | N/A | New Entrant | TAS Low | Hydrogen | Hydrogen | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines4 | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines | Hydrogen reciprocating engines |  |  | TAS Low | TAS Low | Hydrogen reciprocating engines | NE_TAS1 | Hydrogen reciprocating engines | Hydrogen Reciprocating engines | TAS | Hydrogen reciprocating engines | TAS | Hydrogen reciprocating engines