## Capacity_Factors
Technology | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50 | 2050-51 | 2051-52
Data type | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float
Solar PV - Single axis tracking (AC basis with DC:AC ~1.2+) | 29% | 29.2% | 29.4% | 29.6% | 29.8% | 30% | 30.2% | 30.4% | 30.6% | 30.8% | 31% | 31.2% | 31.4% | 31.6% | 31.8% | 32% | 32.2% | 32.4% | 32.6% | 32.8% | 33% | 33.2% | 33.4% | 33.6% | 33.8% | 34% | 34.2%
Wind - onshore | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35% | 35%
Wind - offshore | 50% | 50.5% | 51% | 51.5% | 52% | 52.5% | 53% | 53.5% | 54% | 54.5% | 55% | 55.5% | 56% | 56.5% | 57% | 57.5% | 58% | 58.5% | 59% | 59.5% | 59.5% | 59.5% | 59.5% | 59.5% | 59.5% | 59.5% | 59.5%
Wave | 35% | 35.1% | 35.2% | 35.3% | 35.4% | 35.5% | 35.6% | 35.7% | 35.8% | 35.9% | 36% | 36.1% | 36.2% | 36.3% | 36.4% | 36.5% | 36.6% | 36.7% | 36.8% | 36.9% | 37% | 37.1% | 37.2% | 37.3% | 37.4% | 37.5% | 37.6%
Tidal stream | 34% | 34.1% | 34.2% | 34.3% | 34.4% | 34.5% | 34.6% | 34.7% | 34.8% | 34.9% | 35% | 35.1% | 35.2% | 35.3% | 35.4% | 35.5% | 35.6% | 35.7% | 35.8% | 35.9% | 36% | 36.1% | 36.2% | 36.3% | 36.4% | 36.5% | 36.6%

## Generation_Storages_Electrolyse
General Details | [8 empty] | Technical Parameter | [46 empty] | Economic Parameter | [23 empty] | Refurbishment |  |  | Impact of refurbishment on:
Technology | Generation type | Fuel type | First year assumed commercially viable for construction | Total plant size (gross) | Plant net power output | Seasonal ratings: summer peak (Not Required) | Seasonal ratings: summer typical (Net) | Seasonal ratings: not summer (Net) | Technical life | Economic life | Lead time for development | Lead time | Construction time | Min stable generation | Auxiliary load | Auxiliary load for generators operating in synchronous condenser mode | Full forced outage rate | Frequency of full forced outage per annum | Full outage mean time to repair | Partial forced outage rate | Frequency of partial forced outages | Partial outage derating factor | Partial outage mean time to repair | Equivalent forced outage rate | Maintenance frequency | Average planned maintenance | Minimum load required for synchronous condensers | Ramp up rate | Ramp down rate | Heat rate at minimum operation (HHV Net) | Heat rate at maximum operation (HHV Net) | Combustion emissions | Efficiency | CHP efficiency | Hydrogen production | Hydrogen consumption | Hydrogen gas turbines | Hydrogen compressors | Hydrogen transport | Hydrogen storages | Energy consumption | Water consumption | Plant output | Gas compressors | Gas storages (Fixed) | Storage Maximum Charging/Pumping load | Storage cycle efficiency | Storage: charge efficiency | Storage: discharge efficiency | Storage: allowable max state of charge | Storage: allowable min state of charge | Storage: maximum number of cycles | Storage: depth of discharge | Unit size (nominal) | Number of units | Total capex: net | Total capex: gross | Total capex: storage depth | Total capex | Total capex with land costs | Equipment costs | Fuel connection costs (Fixed) | Fuel connection costs (Variable) | Cost of land and development | Installation costs | Carbon capture equipment and installation costs $ | Carbon storage costs | Carbon transportation costs | Decommissioning, demolition & rehabilitation costs | Disposal costs | Recycling costs | Total retirement costs | Decommissioning, demolition & rehabilitation costs | Disposal costs | Recycling costs | Total retirement costs | Fixed operating cost | Extended warranties | Variable operating cost | Refurbishment cost (costs for components for major types of refurbishment) | Duration of refurbishment | Net Output | Thermal efficiency (HHV sent-out) | Variable operation and maintenance cost | Fixed operation and maintenance cost | Fugitive emissions | Combustion emissions | Cold start-up notification time | Warm start-up notification time | Hot start-up notification time | Cold start up costs | Warm start up costs | Hot start up costs
|  |  |  | MW | MW | MW | MW | MW | years | years | years | years | weeks | % | % | % | % |  | hour | % |  | % | hour | % | events per year | days/year | MW | MW/min | MW/min | GJ/MWh | GJ/MWh | kg CO2-e/GJ of fuel | % | % | kg/h | kg/h |  |  |  |  | MWh/t(NH3) | m3/t(NH3) | tpd |  | $/GJ/day | MW | % | % | % | % | % |  |  | MW |  | $/kW | $/kW | $/kWh | $ | $ | $ | $ | $/km | $ | $ |  | $/t CO2 | $/tCO2/km | $/MW net | $/MW net | $/MW net | $/MW net | $/MW gross | $/MW gross | $/MW gross | $/MW gross | $/MW Net/year | $/MW Net/year | $/MWh Net | $/kW | Weeks | kW | % | $/MWh | $/kW/annum | kg CO2e/GJ | tonnes CO2e/GJ | Hr | Hr | Hr | $/MW | $/MW | $/MW
Data type | str | str | date | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float |  | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float
CCGT - Without CCS | str: Thermal; str: Natural Gas; date: 2025; MW float: 380; MW float: 370; MW float: 348; MW float: 389; % float: 3%; % float: 3.5%; % float: 12.8; % float: 7.47; % float: 6.38; % float: 2227.6; % float: 824901338; % float: 923889498.56; % float: 577430936.6; % float: 23000000 | 1600000 | 98988160.56 | 247470401.4 |  |  |  | 111000 | 17500 | -23000 | 105500 |  |  |  |  | 36000 |  | 5
CCGT - With CCS (90%) | str: Thermal; str: Natural Gas; date: 2025; MW float: 352; MW float: 320; MW float: 301; MW float: 334; % float: 9%; % float: 3.5%; % float: 12.8; % float: 8.29; % float: 7.41; % float: 6105.3; % float: 1989255559; % float: 2227966226.08; % float: 577430936.6; % float: 23000000 | 1600000 | 238710667.08 | 247470401.4 | 1164354221 | 18.5 | 0.1096 | 127500 | 20000 | -26500 | 121000 |  |  |  |  | 46000 |  | 8
CCGT - With CCS (50%) | str: Thermal; str: Natural Gas; date: 2025; MW float: 365; MW float: 338; MW float: 318; MW float: 354; % float: 7%; % float: 3.5%; % float: 12.8; % float: 7.76; % float: 7; % float: 5206.1; % float: 1786472973; % float: 2000849729.76; % float: 577430936.6; % float: 23000000 | 1600000 | 214376756.76 | 247470401.4 | 961571635 | 18.5 | 0.1096 | 121000 | 19000 | -24500 | 115500 |  |  |  |  | 44000 |  | 7
OCGT - Small Aero-derivative, hydrogen ready (35%) | str: Thermal; str: Natural Gas/Diesel; date: 2025; MW float: 191; MW float: 186; MW float: 175; MW float: 197; years float: 40; years float: 25; years float: 1.5; % float: 50%; % float: 2%; % float: 2.3%; % float: 7; % float: 20; % float: 20; % float: 10.6; % float: 10.6; % float: 2578.6; % float: 479266678; % float: 536778679.36; % float: 335486674.6; % float: 23000000 | 1600000 | 57512001.36 | 143780003.4 |  |  |  | 47500 | 7500 | -24000 | 31000 |  |  |  |  | 29000 |  | 10
OCGT - Large Aero-derivative, hydrogen ready (35%) | str: Thermal; str: Natural Gas/Diesel; date: 2025; MW float: 178; MW float: 174; MW float: 163; MW float: 184; years float: 40; years float: 25; years float: 1.5; % float: 50%; % float: 2%; % float: 2.3%; % float: 7; % float: 25; % float: 25; % float: 10.8; % float: 10; % float: 2994.7; % float: 519852754; % float: 582235084.48; % float: 363896927.8; % float: 23000000 | 1600000 | 62382330.48 | 155955826.2 |  |  |  | 47500 | 7500 | -18000 | 37000 |  |  |  |  | 26000 |  | 10
OCGT - Small Industrial, hydrogen ready (10-15%) | str: Thermal; str: Natural Gas/Diesel; date: 2025; MW float: 216; MW float: 211; MW float: 198; MW float: 222; years float: 40; years float: 25; years float: 2; % float: 50%; % float: 2%; % float: 2.3%; % float: 7; % float: 25; % float: 25; % float: 10.8; % float: 10.3; % float: 2022.9; % float: 426705279; % float: 477909912.48; % float: 298693695.3; % float: 23000000 | 1600000 | 51204633.48 | 128011583.7 |  |  |  | 43000 | 7000 | -12000 | 38000 |  |  |  |  | 30000 |  | 11
OCGT - Large Industrial, hydrogen ready (10%) | str: Thermal; str: Natural Gas/Diesel; date: 2025; MW float: 251; MW float: 246; MW float: 232; MW float: 259; years float: 40; years float: 25; years float: 2; % float: 50%; % float: 2%; % float: 2.3%; % float: 7; % float: 90; % float: 90; % float: 13.8; % float: 10.8; % float: 1574.5; % float: 387482822; % float: 433980760.64; % float: 271237975.4; % float: 23000000 | 1600000 | 46497938.64 | 116244846.6 |  |  |  | 48000 | 7500 | -18500 | 37000 |  |  |  |  | 23000 |  | 11
Reciprocating Internal Combustion Engines, hydrogen ready (25%) | str: Thermal; str: Natural Gas/Diesel; date: 2025; MW float: 221; MW float: 217; MW float: 217; MW float: 217; years float: 40; years float: 25; years float: 2; years float: 1; weeks float: 80; % float: 40%; % float: 1.8%; % float: 2%; % float: 2.7; % float: 36; % float: 36; % float: 11.356; % float: 8.79; % float: 1283.7351; % float: 2358.7; % float: 512956233; % float: 574510980.96; % float: 359069363.1; % float: 23000000 | 1600000 | 61554747.96 | 153886869.9 |  |  |  | 64500 | 22000 | -28500 | 58000 |  |  |  |  | 36000 |  | 9
Sub-critical - Black Coal, Small without CCS | str: Thermal; str: Black Coal; date: 2025; MW float: 350; MW float: 327; MW float: 320; MW float: 328; years float: 50; years float: 30; years float: 4.5; years float: 2.5; weeks float: 104; % float: 7%; % float: 3.5%; % float: 10; % float: 11.6; % float: 9.3 | [6 empty] | 236000 | 51000 | -32000 | 255000 |  |  |  |  | 38000 |  | 7
Sub-critical - Black Coal, Small with CCS | str: Thermal; str: Black Coal; date: 2025; MW float: 350; MW float: 283; MW float: 277; MW float: 285; years float: 50; years float: 30; years float: 4.5; years float: 2.5; weeks float: 104; % float: 19%; % float: 3.5%; % float: 10; % float: 9.3; % float: 13 | [6 empty] | 379000 | 82000 | -42000 | 419000 |  |  |  |  | 65000 |  | 18
Sub-critical - Black Coal, Large without CCS | str: Thermal; str: Black Coal; date: 2025; MW float: 660; MW float: 617; MW float: 604; MW float: 620; years float: 50; years float: 30; years float: 4.5; years float: 2.5; weeks float: 104; % float: 7%; % float: 3.5%; % float: 10; % float: 10.9; % float: 9.5 | [6 empty] | 236000 | 50000 | -32000 | 254000 |  |  |  |  | 28000 |  | 8
Sub-critical - Black Coal, Large with CCS | str: Thermal; str: Black Coal; date: 2025; MW float: 660; MW float: 537; MW float: 525; MW float: 540; years float: 50; years float: 30; years float: 4.5; years float: 2.5; weeks float: 104; % float: 19%; % float: 3.5%; % float: 10; % float: 13.4; % float: 12.8 | [6 empty] | 378000 | 80000 | -38000 | 420000 |  |  |  |  | 46000 |  | 18
Super-critical - Black Coal, Small without CCS | str: Thermal; str: Black Coal; date: 2025; MW float: 400; MW float: 374; MW float: 366; MW float: 377; years float: 50; years float: 30; years float: 5.5; years float: 2.5; weeks float: 104; % float: 7%; % float: 3.5%; % float: 10; % float: 11.1; % float: 9.2 | [6 empty] | 236000 | 51000 | -37000 | 250000 |  |  |  |  | 49000 |  | 8
Super-critical - Black Coal, Small with CCS | str: Thermal; str: Black Coal; date: 2025; MW float: 400; MW float: 328; MW float: 322; MW float: 330; years float: 50; years float: 30; years float: 5.5; years float: 2.5; weeks float: 104; % float: 18%; % float: 3.5%; % float: 10; % float: 12.7; % float: 12.2 | [6 empty] | 374000 | 81000 | -50000 | 405000 |  |  |  |  | 72000 |  | 18
Super-critical - Black Coal, Large without CCS | str: Thermal; str: Black Coal; date: 2025; MW float: 700; MW float: 656; MW float: 643; MW float: 660; years float: 50; years float: 30; years float: 5.5; years float: 2.5; weeks float: 104; % float: 6%; % float: 3.5%; % float: 10; % float: 11.3; % float: 9 | [6 empty] | 236000 | 50000 | -39000 | 247000 |  |  |  |  | 52000 |  | 8
Super-critical - Black Coal, Large with CCS | str: Thermal; str: Black Coal; date: 2025; MW float: 700; MW float: 573; MW float: 564; MW float: 577; years float: 50; years float: 30; years float: 5.5; years float: 2.5; weeks float: 104; % float: 18%; % float: 3.5%; % float: 10; % float: 12.5; % float: 12.1 | [6 empty] | 375000 | 80000 | -55000 | 400000 |  |  |  |  | 72000 |  | 18
Sub-critical - Brown Coal, Small without CCS | str: Thermal; str: Brown Coal; date: 2025; MW float: 350; MW float: 318; MW float: 311; MW float: 319; years float: 50; years float: 30; years float: 6.5; years float: 2.5; weeks float: 104; % float: 9%; % float: 4.5%; % float: 12; % float: 12.2; % float: 11.6 | [6 empty] | 314000 | 68000 | -32000 | 350000 |  |  |  |  | 33000 |  | 8
Sub-critical - Brown Coal, Small with CCS | str: Thermal; str: Brown Coal; date: 2025; MW float: 350; MW float: 258; MW float: 525; MW float: 259; years float: 50; years float: 30; years float: 6.5; years float: 2.5; weeks float: 104; % float: 26%; % float: 4.5%; % float: 12; % float: 17.2; % float: 17.4 | [6 empty] | 408000 | 87000 | -32000 | 463000 |  |  |  |  | 56000 |  | 19
Sub-critical - Brown Coal, Large without CCS | str: Thermal; str: Brown Coal; date: 2025; MW float: 580; MW float: 527; MW float: 515; MW float: 531; years float: 50; years float: 30; years float: 6.5; years float: 2.5; weeks float: 104; % float: 9%; % float: 4.5%; % float: 12; % float: 12; % float: 11.4 | [6 empty] | 323000 | 69000 | -37000 | 355000 |  |  |  |  | 45000 |  | 8
Sub-critical - Brown Coal, Large with CCS | str: Thermal; str: Brown Coal; date: 2025; MW float: 580; MW float: 489; MW float: 476; MW float: 489; years float: 50; years float: 30; years float: 6.5; years float: 2.5; weeks float: 104; % float: 16%; % float: 4.5%; % float: 12; % float: 17.1; % float: 17.2 | [6 empty] | 419000 | 90000 | -37000 | 472000 |  |  |  |  | 63000 |  | 19
Ultra Super-critical - Black Coal Without CCS | str: Thermal; str: Black Coal; date: 2025; MW float: 700; MW float: 671; MW float: 658; MW float: 673; years float: 50; years float: 30; years float: 6.5; years float: 2.5; weeks float: 104; % float: 30%; % float: 4.1%; % float: 4%; % float: 10.5; % float: 20; % float: 20; % float: 10.17; % float: 8.55; % float: 6033.623; % float: 4053024028.2656; % float: 4660977632.5055; % float: 1621209611.3062 | 2280000 | 607953604.2398 | 2431814416.9594 |  |  |  | 237000 | 52000 | -40000 | 249000 |  |  |  |  | 66200 |  | 5
Ultra Super-critical - Black Coal With CCS (90%) | str: Thermal; str: Black Coal; date: 2025; MW float: 700; MW float: 577; MW float: 566; MW float: 582; years float: 50; years float: 30; years float: 6.5; years float: 2.5; weeks float: 104; % float: 30%; % float: 17.5%; % float: 4%; % float: 10.5; % float: 20; % float: 20; % float: 11.64; % float: 11.99; % float: 10942.8839; % float: 6492809602.3255; % float: 7466731042.6743; % float: 1621209611.3062 | 2280000 | 973921440.3488 | 2431814416.9594 | 2439785574.0599 | 18.5 | 0.1096 | 382000 | 81000 | -58000 | 405000 |  |  |  |  | 96800 |  | 9
Ultra Super-critical - Black Coal With CCS (50%) | str: Thermal; str: Black Coal; date: 2025; MW float: 700; MW float: 612; MW float: 600; MW float: 616; years float: 50; years float: 30; years float: 6.5; years float: 2.5; weeks float: 104; % float: 30%; % float: 12.5%; % float: 4%; % float: 10.5; % float: 20; % float: 20; % float: 10.11; % float: 9.89; % float: 9235.0131; % float: 5792351373.1632; % float: 6661204079.1377; % float: 1621209611.3062 | 2280000 | 868852705.9745 | 2431814416.9594 | 1739327344.8976 | 18.5 | 0.1096 | 364000 | 76000 | -58000 | 382000 |  |  |  |  | 86500 |  | 8
Conventional hydro | str: Conventional hydro; str: N/A; date: 2025; MW float: 190; MW float: 188; MW float: 188; MW float: 188; years float: 100; years float: 50; years float: 4; years float: 0.5; weeks float: 208; % float: 25%; % float: 1%; % float: 1%; % float: 1%; % float: 5; % float: 400; % float: 400; % float: 95; % int: 2; % float: 6500; % float: 1960000000; % float: 1960000000; % float: 490000000 |  | 0 | 1470000000 |  |  |  | 9000 | 4000 | -2500 | 10500 |  |  |  |  | 20000
Pumped hydroelectric storage (10 hr) | str: Storage; str: N/A; date: 2025; MW float: 500; MW float: 495; MW float: 495; MW float: 495; years float: 100; years float: 50; years float: 4; years float: 0.5; weeks float: 182; % float: 25%; % float: 1%; % float: 1%; % float: 1%; % float: 5; % float: 400; % float: 400; % float: 550; % float: 77.5%; % float: 88.75%; % float: 88.75%; % int: 182500; % float: 250; % int: 2; % float: 3300; % float: 1650000000; % float: 1750000000; % float: 410000000 |  | 100000000 | 1240000000 |  |  |  | 9000 | 4000 | -2500 | 10500 |  |  |  |  | 20000
Pumped hydroelectric storage (24 hr) | str: Storage; str: N/A; date: 2025; MW float: 1000; MW float: 990; MW float: 990; MW float: 990; years float: 100; years float: 50; years float: 4; years float: 0.5; weeks float: 208; % float: 15%; % float: 1%; % float: 1%; % float: 1%; % float: 5; % float: 400; % float: 400; % float: 1100; % float: 77.5%; % float: 88.75%; % float: 88.75%; % int: 91250; % float: 250; % int: 4; % float: 4080; % float: 4080000000; % float: 4320000000; % float: 1020000000 |  | 240000000 | 3060000000 |  |  |  | 6500 | 2000 | -1500 | 7000 |  |  |  |  | 22500
Pumped hydroelectric storage (48 hr) | str: Storage; str: N/A; date: 2025; MW float: 1000; MW float: 990; MW float: 990; MW float: 990; years float: 100; years float: 50; years float: 4; years float: 0.5; weeks float: 260; % float: 15%; % float: 1%; % float: 1%; % float: 1%; % float: 5; % float: 400; % float: 400; % float: 1100; % float: 77.5%; % float: 88.75%; % float: 88.75%; % int: 45625; % float: 250; % int: 4; % float: 4850; % float: 4850000000; % float: 5140000000; % float: 1210000000 |  | 290000000 | 3640000000 |  |  |  | 6500 | 2000 | -1500 | 7000 |  |  |  |  | 25000
Pumped hydroelectric storage (160 hr) | str: Storage; str: N/A; date: 2025; MW float: 2000; MW float: 1980; MW float: 1980; MW float: 1980; years float: 100; years float: 50; years float: 4; years float: 0.5; weeks float: 312; % float: 8%; % float: 1%; % float: 1%; % float: 1%; % float: 5; % float: 400; % float: 400; % float: 2200; % float: 77.5%; % float: 88.75%; % float: 88.75%; % int: 18250; % float: 250; % int: 8; % float: 8290; % float: 16580000000; % float: 17570000000; % float: 4150000000 |  | 990000000 | 12440000000 |  |  |  | 6500 | 2000 | -1500 | 7000 |  |  |  |  | 30000
Large Scale Li-ion Battery Storage (1hr) | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 198.3; MW float: 198.3; MW float: 198.3; years float: 20; years float: 20; years float: 1-2; years float: 1.5; weeks float: 44; % float: 0.85%; % float: 1-2%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 85%; % float: 92.2%; % float: 92.2%; % float: 100%; % float: 0%; % int: 7300; % float: 100%; % float: 410; % float: 310; % float: 144000000; % float: 154000000; % float: 108000000 |  | 10000000 | 36000000 | [7 empty] | 28000 | 7000 | -4000 | 31000 | 6000 | 2500
Large Scale Li-ion Battery Storage (2hr) | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 198.1; MW float: 198.1; MW float: 198.1; years float: 20; years float: 20; years float: 1-2; years float: 1.5; weeks float: 52; % float: 0.95%; % float: 1-2%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 85%; % float: 92.2%; % float: 92.2%; % float: 100%; % float: 0%; % int: 7300; % float: 100%; % float: 410; % float: 290; % float: 198000000; % float: 208000000; % float: 148500000 |  | 10000000 | 49500000 | [7 empty] | 41000 | 14000 | -6000 | 49000 | 10000 | 5000
Large Scale Li ion Battery Storage (4hr) | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 197.6; MW float: 197.6; MW float: 197.6; years float: 20; years float: 20; years float: 1-2; years float: 1.5; weeks float: 60; % float: 1.2%; % float: 1-2%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 85%; % float: 92.2%; % float: 92.2%; % float: 100%; % float: 0%; % int: 7300; % float: 100%; % float: 410; % float: 265; % float: 294000000; % float: 304000000; % float: 220500000 |  | 10000000 | 73500000 | [7 empty] | 76000 | 27000 | -9000 | 94000 | 16000 | 10000
Large Scale Li ion Battery Storage (8hr) | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 196.5; MW float: 196.5; MW float: 196.5; years float: 20; years float: 20; years float: 1-2; years float: 1.5; weeks float: 68; % float: 1.75%; % float: 1-2%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 85%; % float: 92.2%; % float: 92.2%; % float: 100%; % float: 0%; % int: 7300; % float: 100%; % float: 410; % float: 245; % float: 474000000; % float: 484000000; % float: 355500000 |  | 10000000 | 118500000 | [7 empty] | 128000 | 55000 | -17000 | 166000 | 24000 | 20000
Large Scale Flow Battery Storage (8hr) | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 186.4; MW float: 186.4; MW float: 186.4; years float: 25; years float: 25; years float: 1.5-2; years float: 1.5; weeks float: 78; % float: 6.8%; % float: 3-5%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 70%; % float: 82.7%; % float: 82.7%; % float: 100%; % float: 0%; % int: >10,000; % float: 100%; % float: 910; % float: 1456000000; % float: 1471000000; % float: 1092000000 |  | 15000000 | 364000000 | [7 empty] | 455000 | 410000 | -3003000 | -2138000 | 145600
Large Scale Flow Battery Storage (12hr) | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 186.4; MW float: 186.4; MW float: 186.4; years float: 25; years float: 25; years float: 1.5-2; years float: 1.5; weeks float: 78; % float: 6.8%; % float: 3-5%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 70%; % float: 82.7%; % float: 82.7%; % float: 100%; % float: 0%; % int: >10,000; % float: 100%; % float: 815; % float: 1956000000; % float: 1971000000; % float: 1467000000 |  | 15000000 | 489000000 | [7 empty] | 569000 | 487000 | -4415000 | -3359000 | 195600
Large Scale Battery Storage (1hr) for hybrid generation | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 198.3; MW float: 198.3; MW float: 198.3; years float: 20; years float: 20; years float: 1-2; years float: 1.5; weeks float: 44; % float: 0.85%; % float: 1-2%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 85%; % float: 92.2%; % float: 92.2%; % float: 100%; % float: 0%; % int: 7300; % float: 100%; % float: 369; % float: 310; % float: 135800000; % float: 145800000; % float: 101850000 |  | 10000000 | 33950000 | [7 empty] | 28000 | 7000 | -4000 | 31000 | 6000 | 2500
Large Scale Battery Storage (2hr) for hybrid generation | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 198.1; MW float: 198.1; MW float: 198.1; years float: 20; years float: 20; years float: 1-2; years float: 1.5; weeks float: 52; % float: 0.95%; % float: 1-2%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 85%; % float: 92.2%; % float: 92.2%; % float: 100%; % float: 0%; % int: 7300; % float: 100%; % float: 369; % float: 290; % float: 189800000; % float: 199800000; % float: 142350000 |  | 10000000 | 47450000 | [7 empty] | 41000 | 14000 | -6000 | 49000 | 10000 | 5000
Large Scale Battery Storage (4hr) for hybrid generation | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 197.6; MW float: 197.6; MW float: 197.6; years float: 20; years float: 20; years float: 1-2; years float: 1.5; weeks float: 60; % float: 1.2%; % float: 1-2%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 85%; % float: 92.2%; % float: 92.2%; % float: 100%; % float: 0%; % int: 7300; % float: 100%; % float: 369; % float: 265; % float: 285800000; % float: 295800000; % float: 214350000 |  | 10000000 | 71450000 | [7 empty] | 76000 | 27000 | -9000 | 94000 | 16000 | 10000
Large Scale Battery Storage (8hr) for hybrid generation | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 196.5; MW float: 196.5; MW float: 196.5; years float: 20; years float: 20; years float: 1-2; years float: 1.5; weeks float: 68; % float: 1.75%; % float: 1-2%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 85%; % float: 92.2%; % float: 92.2%; % float: 100%; % float: 0%; % int: 7300; % float: 100%; % float: 369; % float: 245; % float: 465800000; % float: 475800000; % float: 349350000 |  | 10000000 | 116450000 | [7 empty] | 128000 | 55000 | -17000 | 166000 | 24000 | 20000
Large Scale Battery Storage (8hr) for hybrid generation (VRB) | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 186.4; MW float: 186.4; MW float: 186.4; years float: 25; years float: 25; years float: 1.5-2; years float: 1.5; weeks float: 78; % float: 6.8%; % float: 3-5%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 70%; % float: 82.7%; % float: 82.7%; % float: 100%; % float: 0%; % int: >10,000; % float: 100%; % float: 865; % float: 1384000000; % float: 1399000000; % float: 1038000000 |  | 15000000 | 346000000 | [7 empty] | 455000 | 410000 | -3003000 | -2138000 | 145600
Large Scale Battery Storage (12hr) for hybrid generation (VRB) | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 186.4; MW float: 186.4; MW float: 186.4; years float: 25; years float: 25; years float: 1.5-2; years float: 1.5; weeks float: 78; % float: 6.8%; % float: 3-5%; % float: 10,000+; % float: 10,000+; % float: 200; % float: 70%; % float: 82.7%; % float: 82.7%; % float: 100%; % float: 0%; % int: >10,000; % float: 100%; % float: 774; % float: 1857600000; % float: 1872600000; % float: 1393200000 |  | 15000000 | 464400000 | [7 empty] | 569000 | 487000 | -4415000 | -3359000 | 195600
Residential Battery Storage (2hr) | str: Storage; str: N/A; date: 2025; MW float: 0.005; MW float: 0.0495; MW float: 0.0495; MW float: 0.0495; years float: 10; years float: 10; weeks float: 60; % float: 1%; % float: 2-3%; % float: 10,000+; % float: 10,000+; % float: 0.05; % float: 85%; % float: 92.2%; % float: 92.2%; % float: 100%; % float: 0%; % int: 3650; % float: 100%; % float: 11000; % float: 8250 |  |  | 2750 | [8 empty] | 75000 | 200000 | 275000
Compressed Air Energy Storage (12 hr vessel storage) | str: Storage; str: N/A; date: 2025; MW float: 50; MW float: 50; MW float: 50; MW float: 50; MW float: 50; years float: 30-50; years float: 30; years float: 2; years float: 1.5-2; weeks float: 80-100; % float: Negligible; % float: 0.5-2; % float: 2%; % float: 3; % float: 100%; % float: 50; % int: 1; % float: 41480; % float: 2037000000; % float: 2074000000; % float: 1037000000 |  | 37000000 | 1000000000 |  |  |  | 98000 | 154000 | -119000 | -27000 |  |  |  |  | 16000 |  | 2.78
Compressed Air Energy Storage (8 hr cavern storage) | str: Storage; str: N/A; date: 2025; MW float: 200; MW float: 200; MW float: 200; MW float: 200; MW float: 200; years float: 30-50; years float: 30; years float: 2-5; years float: 1.5-2; weeks float: 100-150; % float: Negligible; % float: 0.5-2; % float: 2%; % float: 3; % float: 100%; % float: 0%; % float: 200; % int: 1; % float: 5300; % float: 1055000000; % float: 1065000000; % float: 260000000 |  | 10000000 | 795000000 |  |  |  | 98000 | 20000 | 133000 | 91000 |  |  |  |  | 14400 |  | 2.5
Wave | str: Renewable; str: N/A; date: 2025; MW float: 0.3; MW float: 1.455; MW float: 1.455; MW float: 1.455; MW float: 1.455; years float: 25; years float: 20; years float: 5; years float: 1; weeks float: 52; % float: Near 0; % float: 3%; % float: 20%; % float: 0.3; % int: 5; % float: 14950; % float: 2242240; % float: 2870062; % float: 17937784 |  | 627822 | 4484446 |  |  |  | 1863017.638 | 8598.5429 | -275153.3742 | 1596462.8067 |  |  |  |  | 529900
Tidal Stream | str: Renewable; str: N/A; date: 2025; MW float: 1.5; MW float: 5.82; MW float: 5.82; MW float: 5.82; MW float: 5.82; years float: 20; years float: 20; years float: 4 to 5; years float: 1; weeks float: 52; % float: Near 0; % float: 3%; % float: 5%; % float: 1.5; % int: 4; % float: 12420; % float: 72284400; % float: 74669785; % float: 55919211 |  | 2385385 | 13979803 |  |  |  | 1547737.7301 | 7143.4049 | -228588.9571 | 1326292.1779 |  |  |  |  | 496800
Solar PV - Single axis tracking - Large Scale | str: Renewable; str: N/A; date: 2025; MW float: 200; MW float: 200; MW float: 200; MW float: 140; years float: 30; years float: 30; years float: 2.5; years float: 1; weeks float: 26; % float: 0%; % float: 2.9%; % float: 1.5%; % float: 52; % float: Resource dependent; % float: Resource and system dependent; % float: 1080.8333; % float: 259400000; % float: 324142000; % float: 146900000 |  | 64742000 | 112500000 |  |  |  | 104000 | 1000 | 5000 | 110000 |  |  |  |  | 12000 |  | incl in fixed operation cost | 137 | 8 | Net 10MW (5%) reduction during refurb assuming 2 x 5MW central inverters offline at once |  | incl | 12
Solar PV - Distribution Scale (SAT): 20-40MW | str: Renewable; str: N/A; date: 2025; MW float: 20; MW float: 20; MW float: 20; MW float: 15; years float: 30; years float: 30; years float: 1.5; years float: 0.5; weeks float: 26; % float: 0; % float: 2.9; % float: 1.5; % float: Incl in EFOR; % float: Incl in EFOR; % float: Resource dependent; % float: Resource and system dependent; % float: 1361.5385; % float: 35400000; % float: 42414000; % float: 20000000 |  | 7014000 | 15400000 |  |  |  | 135000 | 1000 | 6000 | 142000 |  |  |  |  | 12500 |  | incl in fixed operation cost | 137 | 2 | Net 5MW (25%) reduction during refurb assuming 1 x 5MW central inverter offline at once |  | incl | 12.5
Solar PV - Distribution Scale (SAT): 5-20MW | str: Renewable; str: N/A; date: 2025; MW float: 5; MW float: 5; MW float: 5; MW float: 3.5; years float: 30; years float: 30; years float: 1; years float: 0.25; weeks float: 12; % float: 0; % float: 2.9; % float: 1.5; % float: Incl in EFOR; % float: Incl in EFOR; % float: Resource dependent; % float: Resource and system dependent; % float: 1506.6667; % float: 11300000; % float: 13323000; % float: 6400000 |  | 2023000 | 4900000 |  |  |  | 200000 | 1000 | 7000 | 208000 |  |  |  |  | 13360 |  | incl in fixed operation cost | 130 | 1 | Minimal reduction during refurb assuming use of string inverters |  | incl | 13.36
Solar PV - Behind the Meter (rooftop): 100kW-5MW | str: Renewable; str: N/A; date: 2025; MW float: 1; MW float: 1; MW float: 1; MW float: 0.75; years float: 25; years float: 25; years float: 0.5; years float: 0.25; weeks float: 12; % float: 0; % float: 2.9; % float: 1.5; % float: Incl in EFOR; % float: Incl in EFOR; % float: Resource dependent; % float: Resource and system dependent; % float: 1225; % float: 1470000; % float: 1470000; % float: 830000 |  | 0 | 640000 |  |  |  | 256000 | 1000 | 13000 | 270000 |  |  |  |  | 15000 |  | incl in fixed operation cost | 130 | 1 | Minimal reduction during refurb assuming use of string inverters |  | incl | 15
Solar Thermal Central Receiver with storage (14hr) | str: Renewable; str: N/A; date: 2025; MW float: 150; MW float: 140; MW float: 140; MW float: 140; years float: 40; years float: 30; years float: 2.5; years float: 1.75; weeks float: 91; % float: 20%; % float: 6.7%; % float: 3%; % float: 7; % float: 360; % float: 360; % float: 6887.1429; % float: 491.9388; % float: 964200000; % float: 1058616000; % float: 433890000 |  | 94416000 | 530310000 |  |  |  | 246000 | 141000 | -3000 | 384000 |  |  |  |  | 137000 |  | incl in fixed operation cost | 2070 - 3100 | 26-40 | NB material refurb only expected at end of operating life - so may be N/A in this instance | Typically ~30% for steam system, expected to improve 1.5-2.5% | Expected to reduce die to less pressure part failures, EFOR to reduce to ~3% |  |  |  | 6 to 8 | 3 to 4 | 1 to 1.5 | Per pump power for start time indicated | Per pump power for start time indicated | Per pump power for start time indicated
Wind - onshore | str: Renewable; str: N/A; date: 2025; MW float: 7.2; MW float: 698.4; MW float: 698.4; MW float: 698.4; MW float: 698.4; years float: 30; years float: 25; years float: 3 to 5; years float: 1; weeks float: 100; % float: Near 0; % float: 3%; % float: 2.5%; % float: 7.2; % int: 100; % float: 3150; % float: 2212900000; % float: 2268225000; % float: 1549000000 |  | 55325000 | 663900000 |  |  |  | 181000 | 4500 | -24500 | 161000 |  |  |  |  | 29000
Wind - offshore (Fixed) | str: Renewable; str: N/A; date: 2025; MW float: 15; MW float: 1152; MW float: 1152; MW float: 1152; MW float: 1152; years float: 30; years float: 25; years float: 5+; years float: 3; weeks float: 156; % float: Near 0; % float: 4%; % float: 5%; % float: 15; % int: 80; % float: 5216; % float: 5963375881; % float: 6259200000; % float: 4085615881 |  | 295824119 | 1877760000 |  |  |  | 650000 | 3000 | -96000 | 557000 |  |  |  |  | 175000
Wind - offshore (Floating) | str: Renewable; str: N/A; date: 2025; MW float: 15; MW float: 418; MW float: 418; MW float: 418; MW float: 418; years float: 30; years float: 25; years float: 5+; years float: 3; weeks float: 156; % float: Near 0; % float: 4%; % float: 5%; % float: 15; % int: 29; % float: 8000; % float: 3378156364.6136; % float: 3479947623.6136; % float: 2435963336.6136 |  | 101791259 | 942193028 |  |  |  | 275000 | 3000 | -96000 | 182000 |  |  |  |  | 201765
Waste to Energy | str: Waste to Energy; str: Municipal waste; date: 2025; MW float: 30; MW float: 26.4; MW float: 25.7; MW float: 26.8; years float: 30; years float: 25; years float: 3; years float: 1.75; weeks float: 165; % float: 40%; % float: 7.3%; % float: 22.8; % float: 72; % float: 72; % float: 25796.5; % float: 681027600; % float: 749130360; % float: 408616560 |  | 68102760 | 272411040 |  |  |  | 150000 | 2000 | 11400 | 140600 |  |  |  |  | 773895 |  | 32.7929
Fuel cells - small (assume PEMFC) | str: Renewable; str: Renewable Hydrogen; date: 2025; MW float: 0.045; MW float: 0.0405; years float: 20; years float: 20; years float: 1 to 2; years float: 1 to 2; weeks float: 20; % float: 25%; % float: 10%; % float: Variable; % float: 7; % float: 0-100% in < 1min; % float: 0-100% in < 1min; % float: 2.8; % float: 0.045; % int: 1; % float: 7000; % float: 315000; % float: 331000; % float: 141750 |  | 16000 | 173250 | [7 empty] | 600000 | 5000 | -103000 | 502000 | 350000 |  | Included in fixed O&M (excludes power, water) | 700 | Dependent on # modules, and parallel vs series refurb, expect low single digit weeks per module | Refurb could be staged to take one module off at a time. Net impact on production dependent on # modules installed |  | Stack replacement, typ ~10% improvement in spec power at stack end of life |  |  |  | <1min | <1min | <1min | minimal | minimal | minimal
Fuel cells - large (assume PEMFC) | str: Renewable; str: Renewable Hydrogen; date: 2025; MW float: 1.2; MW float: 1.08; years float: 20; years float: 20; years float: 1 to 2; years float: 1 to 2; weeks float: 26; % float: 25%; % float: 10%; % float: Variable; % float: 7; % float: 0-100% in < 1min; % float: 0-100% in < 1min; % float: 75; % float: 0.2; % int: 6; % float: 6000; % float: 7200000; % float: 7560000; % float: 3240000 |  | 360000 | 3960000 | [7 empty] | 600000 | 5000 | -103000 | 502000 | 300000 |  | Included in fixed O&M (excludes power, water) | 600 | Dependent on # modules, and parallel vs series refurb, expect low single digit weeks per module | Refurb could be staged to take one module off at a time. Net impact on production dependent on # modules installed |  | Stack replacement, typ ~10% improvement in spec power at stack end of life |  |  |  | <1min | <1min | <1min | minimal | minimal | minimal
Electrolysers - Proton Exchange Membrane | str: Storage; str: Renewable Hydrogen; date: 2025; MW float: 500; years float: 20; years float: 20; years float: 5; years float: 4; weeks float: 52; % float: 10%; % float: 15; % float: 60s for 0-100%; % float: 60s for 0-100%; % float: 2600; % float: 1300000000; % float: 1365000000; % float: 520000000 |  | 65000000 | 780000000 |  |  |  | 263000 | 5000 | -157500 | 110500 |  |  |  |  | 65000 |  | Included in fixed O&M (excludes power, water)
Electrolysers - Alkaline | str: Storage; str: Renewable Hydrogen; date: 2025; MW float: 500; years float: 20; years float: 20; years float: 5; years float: 4; weeks float: 52; % float: 10%; % float: 15; % float: 20% per minute; % float: 20% per minute; % float: 2000; % float: 1000000000; % float: 1050000000; % float: 370000000 |  | 50000000 | 630000000 |  |  |  | 246000 | 5000 | -77500 | 173500 |  |  |  |  | 40000 |  | Included in fixed O&M (excludes power, water)

## SMR_&_Liquefaction_Plant
Technology | Description | Plant capacity | Water consumption | Capex rate: kW | Capex rate: kg | Capex | Development cost | Construction cost | Opex - power cost | Opex - operation and maintenance cost | Hydrogen source | Co2 emissions | Gas consumption | Electric power consumption | Opex incl natural gas cost | Storage temperature | Boil off losses /day
|  | T-H2/d | kg/kg H2 | $/kW-H2 | $/kg H2/yr | $ | % | % | $/year | $/kg H2 |  | kg-CO2/kg-H2 | GJ/d | kWh/kg-H2 | $/year | degC | Losses/day (%)
str | str | int | float | float | float | float | float | float | float | float | str | float | float | float | float | float | float
SMR | Hydrogen generation by Steam Methane Reforming - smaller | 100 | 6.3 | 2216 |  | 307802400 |  |  |  |  | NG | 10
| Hydrogen generation by Steam Methane Reforming - large | 800 | 6.3 | 1106 |  | 1228987200 |  |  |  |  | NG | 10
SMR with CCS | Hydrogen generation by SMR with Carbon Capture and Storage - smaller | 100 | 6.3 | 2882 |  | 400309800 |  |  |  |  | NG | 4.8
| Hydrogen generation by SMR with Carbon Capture and Storage - large | 800 | 6.3 | 1372 |  | 1524566400 |  |  |  |  | NG | 0.9
Liquefaction Plant & LH2 Storage | Hydrogen Liquefaction by cooling to cryogenic temperatures | 27 |  |  | 21.2301 | 188300000 |  |  | Excluded | 6.1972 | NG/electrolysis | Could be 0 theoretically |  | 11 |  | -253 | 0.1%
Gaseous H2 storage | Hydrogen compression and gaseous storage of compressed hydrogen in vessels | 20 |  |  |  | 35000007.4 |  |  | Excluded | 52.5 | NG/electrolysis | Could be 0 theoretically |  | 5 |  | Ambient | 0

## Ammonia_Facility
Technology | Description | Daily ammonia production (tpd) | Energy consumption | Hydrogen consumption | Water consumption | Annual ammonia output | Stream days | Capex | Opex
|  | tpd | MWh/t(ammonia) | kg (H2)/t(NH3) | m3/t(NH3) | tpa |  | $M | $M/year
str | str | float | float | float | float | float | int | float | float
Ammonia Facility | Haber-Bosch process, with air separation unit for nitrogen supply, cooling tower, and steam turbine generator for waste heat recovery | 2800 | 0.42 at design rates - highly load dependent | 178 | Primarily for cooling; highly dependent on cooling tech | 1000000 | 258 days p.a. ave excl planned shutdowns | 530 | 7.9

## Water_Treatment
Technology | Description | Source water | Plant capacity | Demineralised water produced | Potable water produced | Wastewater - membrane backwash and cleaning | Wastewater - brine production | Recovery ratio | Power consumption: with energy recovery | Power consumption: without energy recovery | Capex rate | Capex | Development cost | Construction cost | Opex - chemical cost | Opex - labour cost | Opex - power cost | Opex - operation and maintenance cost
|  |  | m3/d | m3/d | m3/d | m3/d | m3/d | % | kWh/m3 feed water | kWh/m3 feed water | $/ML/year feed water | $ | % | % | $/year | $/year | $/year | $/year
str | str | str | int | int | int | int | int | float | int | int | float | float | float | float | float | float | float | float
Demineralisation plant | Using potable water to produce highly purified water for hydrogen production for a 10 MW electrolyser | Potable water |  | 40 |  |  | 6.5 | 86 | 2.6 |  | 1000-2000 | 400,000-800,000 |  | 240,000-480,000 | < 1000 | 15,000-25,000 | 3,000-6,000 | 8,000-15,000
Desalination plant (large scale) | Full-scale desalination for 100,000 ML/year plant to produce potable water with a recovery ratio of 0.4 | Seawater | 273972.6027 |  | 109589.0411 | 0 | 164383.5616 | 40 | 3.75 | 10.5 | 22250 | 2225000000 | 20 | 80 | 8900000 | 8900000 | 22200000 | 13000000

## Hydrogen_Storage
Technology | Description | Cavern volume | Maximum storage capacity | Mean depth | Working capacity | Gas cycling requirements | Operating pressure | Operating temperature | Energy consumption | Capex, engineering | Capex, below ground | Capex, leaching and brine disposal | Capex, above ground | Opex
|  | m3 | tonne | m | m3 | cycles/year | bar | deg C | MWh/tonne | $M | $M | $M | $M | $M/year
str | str | int | int | int | int | int | int | float | float | float | float | float | float | float
Hydrogen storage (geological) | Salt cavern that reflects operating conditions of existing projects in the UK and USA | 300000 | 2200 | 1000 | 210000 | 10 | 100 | 35 | 1.2 | 8.5 | 46.5 | 8 | 26 | 1.6

## Biogas Digestors
General Details | [8 empty] | Technical Parameter | [46 empty] | Economic Parameter
Technology | Generation type | Fuel type | First year assumed commercially viable for construction | Assumed unit size | Plant net power output | Seasonal ratings: summer peak (Not Required) | Seasonal ratings: summer typical | Seasonal ratings: not summer | Technical life | Economic life | Lead time for development | Lead time | Construction time | Min stable generation | Auxiliary load | Auxiliary load for generators operating in synchronous condenser mode | Full forced outage rate | Frequency of full forced outage per annum | Full outage mean time to repair | Partial forced outage rate | Frequency of partial forced outages | Partial outage derating factor | Partial outage mean time to repair | Equivalent forced outage rate | Maintenance frequency | Average planned maintenance | Minimum load required for synchronous condensers | Ramp up rate | Ramp down rate | Heat rate at minimum operation | Heat rate at maximum operation | Combustion emissions | Efficiency | CHP efficiency | Hydrogen production | Hydrogen consumption | Hydrogen gas turbines | Hydrogen compressors | Hydrogen transport | Hydrogen storages | Energy consumption | Water consumption | Plant output | Gas compressors | Gas storages (Fixed) | Storage Maximum Charging/Pumping load | Storage cycle efficiency | Storage: charge efficiency | Storage: discharge efficiency | Storage: allowable max state of charge | Storage: allowable min state of charge | Storage: maximum number of cycles | Storage: depth of discharge | Unit size (nominal) | Number of units | Total capex: net | Total capex: gross | Total capex: storage depth | Total capex | Total capex with land costs | Equipment costs | Fuel connection costs (Fixed) | Fuel connection costs (Variable) | Cost of land and development | Installation costs | Carbon capture equipment and installation costs | Carbon storage costs | Carbon transportation costs | Disposal costs | Recycling cost | Fixed operating cost | Extended warranties | Variable operating cost
|  |  |  | NmÂ³/h | MW | MW | MW | MW | years | years | years | years | weeks | % | % | % | % |  | hour | % |  | % | hour | % | events per year | days/year | MW | MW/h | MW/h | GJ/MWh | GJ/MWh | kg CO2-e/GJ of fuel | % | % | kg/h | kg/h |  |  |  |  | MWh/t(NH3) | m3/t(NH3) | NmÂ³/year |  | $/GJ/day | MW | % | % | % | % | % |  |  | MW |  | $/kW | $/kW | $/kWh | $ | $ | $ | $ | $/km | $ | $ |  | $/t CO2 | $/tCO2/km |  |  | $/MW Net/year | $/MW Net/year | $/MWh Net
Data type | str | str | date | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float |  | float | float | float | float | float | float | float | float | float | float
Biogas digestors | str: Anaerobic digestion of organic feedstocks; str: Agricultural residues, energy crops, food waste, manures, sewage, MSW; date: 2025; float: 900; float: 2; float: 2; float: 2; float: 30; float: 25; float: 2; float: 1; float: 52; float: 20%; float: 10%; float: 15; float: 7560000; float: 17720; float: 35440000; float: 75440000; float: 14177200 |  | 40000000 | 21265800 | [5 empty] | 354430 |  | 531645
LFG | str: Landfill gas well collection system; str: Organics in (organics in general household waste); date: 2025; float: 900; float: 2; float: Up to 50 years; float: 15; float: 2 + 1-2 years for steady production; float: 0.5; float: 26; float: 15; float: 7313360; float: 5100; float: 10200000; float: 25200000; float: 4080000 |  | 15000000 | 6120000 | [5 empty] | 102000 |  | 255000

## Biodiesel Production
General Details | [8 empty] | Technical Parameter | [46 empty] | Economic Parameter
Technology | Generation type | Fuel type | First year assumed commercially viable for construction | Assumed unit size | Plant net power output | Seasonal ratings: summer peak (Not Required) | Seasonal ratings: summer typical | Seasonal ratings: not summer | Technical life | Economic life | Lead time for development | Lead time | Construction time | Min stable generation | Auxiliary load | Auxiliary load for generators operating in synchronous condenser mode | Full forced outage rate | Frequency of full forced outage per annum | Full outage mean time to repair | Partial forced outage rate | Frequency of partial forced outages | Partial outage derating factor | Partial outage mean time to repair | Equivalent forced outage rate | Maintenance frequency | Average planned maintenance | Minimum load required for synchronous condensers | Ramp up rate | Ramp down rate | Heat rate at minimum operation | Heat rate at maximum operation | Combustion emissions | Efficiency | CHP efficiency | Hydrogen production | Hydrogen consumption | Hydrogen gas turbines | Hydrogen compressors | Hydrogen transport | Hydrogen storages | Energy consumption | Water consumption | Plant output | Gas compressors | Gas storages (Fixed) | Storage Maximum Charging/Pumping load | Storage cycle efficiency | Storage: charge efficiency | Storage: discharge efficiency | Storage: allowable max state of charge | Storage: allowable min state of charge | Storage: maximum number of cycles | Storage: depth of discharge | Unit size (nominal) | Number of units | Total capex: net | Total capex: gross | Total capex: storage depth | Total capex | Total capex with land costs | Equipment costs | Fuel connection costs (Fixed) | Fuel connection costs (Variable) | Cost of land and development | Installation costs | Carbon capture equipment and installation costs | Carbon storage costs | Carbon transportation costs | Disposal costs | Recycling cost | Fixed operating cost | Extended warranties | Variable operating cost
|  |  |  | ML/year | ML/year | ML/year | ML/year | ML/year | years | years | years | years | weeks | % | % | % | % |  | hour | % |  | % | hour | % | events per year | days/year | MW | MW/h | MW/h | GJ/MWh | GJ/MWh | kg CO2-e/GJ of fuel | % | % | kg/h | kg/h |  |  |  |  | MWh/t(NH3) | m3/t(NH3) | tpd |  | $/GJ/day | MW | % | % | % | % | % |  |  | MW |  | $/kW | $/kW | $/kWh | $ | $ | $ | $ | $/km | $ | $ |  | $/t CO2 | $/tCO2/km |  |  | $/ML/year | $/MW Net/year | $/ML/year
Data type | str | str | date | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float |  | float | float | float | float | float | float | float | float | float | float
Biodiesel production | str: Renewable Biofuel Production; str: Vegetable Oils from soybean, sunflower or safflower, Used Cooking Oil (UCO), Tallow, etc; date: 2025; float: 50; float: 50; float: 50; float: 50; float: 30; float: 20; float: 2; float: 2; float: 52; float: 20%; float: 5%; float: 65; float: 75000000; float: 82500000; float: 30000000 |  | 7500000 | 45000000 | [5 empty] | 45000 |  | 1248000

## Biomass Generation
General Details | [12 empty] | Technical Parameter | [46 empty] | Economic Parameter
Technology | Generation type | Fuel type | First year assumed commercially viable for construction | Assumed unit size (Electrical) | Assumed unit size (thermal) | Plant net power output (Electrical) | Plant net power output (thermal) | Seasonal ratings: summer peak (Not Required) | Seasonal ratings: summer typical (Electrical) | Seasonal ratings: summer typical (thermal) | Seasonal ratings: not summer (Electrical) | Seasonal ratings: not summer (thermal) | Technical life | Economic life | Lead time for development | Lead time | Construction time | Min stable generation | Auxiliary load | Auxiliary load for generators operating in synchronous condenser mode | Full forced outage rate | Frequency of full forced outage per annum | Full outage mean time to repair | Partial forced outage rate | Frequency of partial forced outages | Partial outage derating factor | Partial outage mean time to repair | Equivalent forced outage rate | Maintenance frequency | Average planned maintenance | Minimum load required for synchronous condensers | Ramp up rate | Ramp down rate | Heat rate at minimum operation | Heat rate at maximum operation | Combustion emissions | Efficiency | CHP efficiency | Hydrogen production | Hydrogen consumption | Hydrogen gas turbines | Hydrogen compressors | Hydrogen transport | Hydrogen storages | Energy consumption | Water consumption | Plant output | Gas compressors | Gas storages (Fixed) | Storage Maximum Charging/Pumping load | Storage cycle efficiency | Storage: charge efficiency | Storage: discharge efficiency | Storage: allowable max state of charge | Storage: allowable min state of charge | Storage: maximum number of cycles | Storage: depth of discharge | Unit size (nominal) | Number of units | Total capex: net (Electrical) | Total capex: net (Electrical plus thermal0) | Total capex: gross | Total capex: storage depth | Total capex | Total capex with land costs | Equipment costs | Fuel connection costs (Fixed) | Fuel connection costs (Variable) | Cost of land and development | Installation costs | Carbon capture equipment and installation costs | Carbon storage costs | Carbon transportation costs | Disposal costs | Recycling cost | Fixed operating cost | Extended warranties | Variable operating cost
|  |  |  | MW | MW | MW | MW | MW | MW | MW | MW | MW | years | years | years | years | weeks | % | % | % | % |  | hour | % |  | % | hour | % | events per year | days/year | MW | MW/h | MW/h | GJ/MWh | GJ/MWh | kg CO2-e/GJ of fuel | % | % | kg/h | kg/h |  |  |  |  | MWh/t(NH3) | m3/t(NH3) | tpd |  | $/GJ/day | MW | % | % | % | % | % |  |  | MW |  | $/kW | $/kW | $/kW | $/kWh | $ | $ | $ | $ | $/km | $ | $ |  | $/t CO2 | $/tCO2/km |  |  | $/MW Net/year | $/MW Net/year | $/MWh Net
Data type | str | str | date | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | float | int | float | float | int | float | float | float | float | float | float | float | float |  | float | float | float | float | float | float | float | float | float | float
Biomass Generation - Electricity and steam | str: Thermal (renewable); str: Woodchip; date: 2025; MW float: 30; MW float: 44.2; MW float: 27.8; MW float: 44.2; MW float: 27.4; MW float: 44.2; MW float: 28; MW float: 44.2; years float: 30; years float: 25; years float: 3; years float: 1.75; weeks float: 65; % float: 40%; % float: 7.3%; % float: 4%; % float: 22.8; % float: 72; % float: 72; % float: 18.092; % float: 16.255; % float: 22.15%; % float: 57.4%; % float: 8271; % float: 3191; % float: 229938910; % float: 250633411.9; % float: 137963710 |  | 20694501.9 | 91975200 | [5 empty] | 186130 |  | 10.9