## Instructions
Instructions: This NCESS Submission form relates to a proposed fast frequency response service (see AEMO's call for submissions and NCESS Service Specification dated 15 August 2022). Respondents are requested to complete the following tabs in this spreadsheet: NCESS Submission Response - Please complete all green cells. Italicised text provides guidance regarding the expected content of responses. NCESS Service Specification - The NCESS Service Specification tab is based on the NCESS Service Specification. - Please complete all green cells. • The "Complies (Yes/No)" column indicates whether the respondent can meet the specified paragraph of the NCESS Service Specification. • The "Comments" column allows a respondent to provide additional commercial or information in support of its NCESS Submission. • The "Supporting Documents" column is to list any supporting documents provided in support of the NCESS Submission.
Responses must be submitted to AEMO by 5:00pm AWST on Monday, 12th September 2022 by Vendorpanel.

## NCESS Submission Response
Item | Request | Response
1 | The name and type of facility or equipment, and whether it is registered or intending to register under the WEM Rules [clause 3.11B.7(a) of the WEM Rules]
2 | The name of the Market Participant, or service provider, as applicable, in respect to the facility or equipment [clause 3.11B.7(b) of the WEM Rules]
3 | The quantity of service the facility or equipment will provide for the NCESS [clause 3.11B.7(c) of the WEM Rules] | Please refer to the NCESS Service Specification generally and paragraph 2.4 specifically
4 | The timing and duration of the service availability for the NCESS [clause 3.11B.7(d) of the WEM Rules] | Please refer to the NCESS Service Specification generally and paragraph 3.1.1 (Contract Term) specifically
5 | The location of the facility or equipment on the network [clause 3.11B.7(e) of the WEM Rules] | Please refer to the NCESS Service Specification generally and paragraph 2.3 specifically
6 | Any operational requirements or limitations that must be respected for use of the facility or equipment for the NCESS [clause 3.11B.7(f) of the WEM Rules] | Please refer to the NCESS Service Specification generally and paragraph 2.6 specifically
7 | Whether the facility or equipment participates, or will participate, in Central Dispatch or is accredited or will be accredited under these Market Rules to provide an Essential System Service [clause 3.11B.7(h) of the WEM Rules]
8 | The proposed availability payment which must be equal to or less than the incremental fixed costs, if any, that, where applicable, are not already covered by any Capacity Credit payments, which would be incurred to make the capability available for the NCESS [clause 3.11B.7(i) of the WEM Rules] | Please specify $/Trading Interval Please refer to the NCESS Service Specification generally and paragraph 3.1.1 (Availability Payment) specifcially Important: please note clause 5.3.1 of the WEM Rules, and clarify any assumptions made with respect to the treatment of Capacity Credit payments as part of the NCESS Submission.
9 | Any other payment that the facility or equipment requires to provide the NCESS [clause 3.11B.7(i) of the WEM Rules] | Please specify $/Trading Interval Please refer to the NCESS Service Specification generally and paragraph 3.1.1 (Enablement Payment) specifically Important: please note clause 5.3.1 of the WEM Rules, and clarify any assumptions made with respect to the treatment of Capacity Credit payments as part of the NCESS Submission.
Note: The proposed contract term (commencing no later than 1 February 2023 and ending on 30 September 2023) means clauses 3.11B.7(g) and 3.11B.7(gA) of the WEM Rules are not applicable.

## NCESS Service Specification
Paragraph | Content | Complies (Yes/No) | Comments | Supporting Documents
2 | NCESS Service Specification (Technical)
2.1. | Service requirements
2.1.1. | This NCESS Service Specification is for a fast frequency response service, measured in MW of response capability, that enables a facility or equipment to adjust injection or withdrawal to raise the SWIS Frequency. |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.2. | Expected technical capability of facility or equipment that may be able to provide service
2.2.1. | The expected technical capability of a facility or equipment that may be able to provide the FFR Service is that it satisfies all of the following requirements: |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.2.1.(a) | the Performance Requirements for Contingency Reserve Raise specified in the FCESS Accreditation Procedure; |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.2.1(b) | the requirements specified in the WEM Procedure: Communications and Control Systems, as applicable to Contingency Reserve Raise, including the requirements to install and maintain a suitable High Resolution Time Synchronised Data Recorder and to maintain SCADA data; |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.2.1(c)(i) | the speed of response for the facility or equipment (which must be determined in a manner that is consistent with the process for determining a Facility Speed Factor under paragraph 7.2 of the FCESS Accreditation Procedure) must be less than the equivalent of a Facility Speed Factor of 0.2 seconds (equivalent to full response in under 1 second to a step frequency change); |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.2.1(c)(ii) | (subject to any instruction from AEMO to the NCESS FFR provider under the NCESS Contract to delay enablement) the FFR Service must be capable of being re-enabled for the contract quantity within 15 minutes after the SWIS Frequency Recovers6 following a Contingency Event. |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.3. | Likely network location where service to be provided
2.3.1. | The FFR service may be provided at any location in the SWIS, excluding the following areas: - locations east of Merredin terminal - within the Cunderdin and Narrogin South 220 kV network - locations north of Northern terminal |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.4. | Maximum quantity of service required
2.4.1. | The maximum quantity of the FFR Service required (for all NCESS Contracts) is 100 MW. |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.4.2. | The minimum quantity of the FFR Service required (for each NCESS Contract) is 25 MW |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.4.3. | An NCESS Submission may specify any quantity of the FFR Service up to a maximum quantity. The maximum quantity must be determined using a process that is consistent with the process for determining a maximum quantity of Contingency Reserve Raise specified in paragraph 7.1 of the FCESS Accreditation Procedure, at temperatures up to 45°C. |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.5. | Timing and duration of service
2.5.1. | Subject to the NCESS Contract, during the Availability Period, the NCESS provider must make the FFR Service available and (when required to do so by AEMO) must enable the FFR Service. |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.5.2. | The Availability Period is:
2.5.2(a) | between 08:00 and 16:00 on each Trading Day from 1 October 2022 to 31 May 2023 (summer and shoulder seasons); |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.5.2(b) | between 10:00 and 14:00 on each Trading Day from 1 June 2023 to 30 September 2023 (winter season). |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification
2.6. | Operational requirements and limitations
2.6.1. | AEMO may require the NCESS provider to enable the FFR Service for any quantity up to the contract quantity by notifying the NCESS provider up to 3 hours in advance of the enablement period. The notice will specify the Trading Intervals in the enablement period and the enablement quantity. |  |  | Sufficient Supporting information must be provided to demonstrate compliance with the NCESS Service Specification